## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.2129 | 2.2129 | 0 | 0 | 1.5331 | 1.5331 | 0.58761 | -0.44071 | 1.1752 | -0.88142 | -67.8829 | 112.1171 | 0.85704 | 0.64278 | -4.4479 | -4.4479
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87306 | 0.87306 | -4.7758 | -4.7758
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479
Line2_1_4 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.016505 | 0.017405 | -0.10151 | 0.10331 | 94.7872 | -85.2128 | 0.85704 | 0.87306 | -4.4479 | -4.7758
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479
Line4_2_6 | 2.2129 | 2.2129 | 0 | 0 | 1.5331 | 1.5331 | 0.44071 | -0.29381 | 0.88142 | -0.58761 | -67.8829 | 112.1171 | 0.64278 | 0.42852 | -4.4479 | -4.4479
Line5_6_7 | 2.2129 | 2.2129 | 0 | 0 | 1.5331 | 1.5331 | 0.29381 | -0.1469 | 0.58761 | -0.29381 | -67.8829 | 112.1171 | 0.42852 | 0.21426 | -4.4479 | -4.4479
Line6_7_8 | 2.2129 | 2.2129 | 0 | 4.0824 | 1.5331 | 1.5331 | 0.1469 | -1e-07 | 0.29381 | -1e-07 | -67.8829 | 112.1171 | 0.21426 | 0 | -4.4479 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7708e-22 | 0 | 4.5115e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7708e-22 | 0 | 4.5115e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85704 | 0.85704 | -4.4479 | -4.4479

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.2966 | 2.2966 | 0 | 0 | 1.5911 | 1.5911 | 0.63291 | -0.47468 | 1.2658 | -0.94936 | -68.05 | 111.95 | 0.88946 | 0.66709 | -4.615 | -4.615
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90549 | 0.90549 | -4.9282 | -4.9282
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615
Line2_1_4 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.017436 | 0.018336 | -0.1053 | 0.1071 | 94.7869 | -85.2131 | 0.88946 | 0.90549 | -4.615 | -4.9282
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615
Line4_2_6 | 2.2966 | 2.2966 | 0 | 0 | 1.5911 | 1.5911 | 0.47468 | -0.31645 | 0.94936 | -0.63291 | -68.05 | 111.95 | 0.66709 | 0.44473 | -4.615 | -4.615
Line5_6_7 | 2.2966 | 2.2966 | 0 | 0 | 1.5911 | 1.5911 | 0.31645 | -0.15823 | 0.63291 | -0.31645 | -68.05 | 111.95 | 0.44473 | 0.22236 | -4.615 | -4.615
Line6_7_8 | 2.2966 | 2.2966 | 0 | 4.2462 | 1.5911 | 1.5911 | 0.15823 | -1e-07 | 0.31645 | -1e-07 | -68.05 | 111.95 | 0.22236 | 0 | -4.615 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0801e-21 | 0 | -4.6522e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0801e-21 | 0 | -4.6522e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88946 | 0.88946 | -4.615 | -4.615

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.034364 | 0.034364 | 0 | 0 | 0.023808 | 0.023808 | 0.017855 | -0.017819 | 0.017997 | -0.017926 | -45.346 | 134.654 | 1.0648 | 1.0616 | -0.11952 | -0.17563
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0804 | 1.0804 | -0.44776 | -0.44776
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952
Line2_1_4 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.010929 | 0.011829 | -0.12731 | 0.12911 | 94.7872 | -85.2128 | 1.0648 | 1.0804 | -0.11952 | -0.44776
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952
Line4_2_6 | 0.034364 | 0.034364 | 0 | 0 | 0.023808 | 0.023808 | 0.017819 | -0.017784 | 0.017926 | -0.017855 | -45.346 | 134.654 | 1.0616 | 1.0585 | -0.17563 | -0.23207
Line5_6_7 | 0.034364 | 0.034364 | 0 | 0 | 0.023808 | 0.023808 | 0.017784 | -0.017749 | 0.017855 | -0.017784 | -45.346 | 134.654 | 1.0585 | 1.0553 | -0.23207 | -0.28886
Line6_7_8 | 0.034364 | 0.034364 | 0 | 0.063395 | 0.023808 | 0.023808 | 0.017749 | -0.017713 | 0.017784 | -0.017713 | -45.346 | 134.654 | 1.0553 | 1.0522 | -0.28886 | -0.34598
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5377e-11 | 0 | 7.3383e-11 | 0 | 0 | 0 | 1.0522 | 1.0522 | -0.34598 | -0.34598
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5377e-11 | 0 | 7.3383e-11 | 0 | 0 | 0 | 1.0522 | 1.0522 | -0.34598 | -0.34598
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0648 | 1.0648 | -0.11952 | -0.11952

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.035996 | 0.035996 | 0 | 0 | 0.024939 | 0.024939 | 0.019591 | -0.019552 | 0.019746 | -0.019669 | -45.3516 | 134.6484 | 1.1154 | 1.1121 | -0.12515 | -0.18126
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.131 | 1.131 | -0.43864 | -0.43864
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515
Line2_1_4 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011461 | 0.012361 | -0.13335 | 0.13515 | 94.7869 | -85.2131 | 1.1154 | 1.131 | -0.12515 | -0.43864
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515
Line4_2_6 | 0.035996 | 0.035996 | 0 | 0 | 0.024939 | 0.024939 | 0.019552 | -0.019513 | 0.019669 | -0.019591 | -45.3516 | 134.6484 | 1.1121 | 1.1088 | -0.18126 | -0.23771
Line5_6_7 | 0.035996 | 0.035996 | 0 | 0 | 0.024939 | 0.024939 | 0.019513 | -0.019474 | 0.019591 | -0.019513 | -45.3516 | 134.6484 | 1.1088 | 1.1054 | -0.23771 | -0.29449
Line6_7_8 | 0.035996 | 0.035996 | 0 | 0.066554 | 0.024939 | 0.024939 | 0.019474 | -0.019435 | 0.019513 | -0.019435 | -45.3516 | 134.6484 | 1.1054 | 1.1021 | -0.29449 | -0.35161
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6208e-11 | 0 | 8.184e-11 | 0 | 0 | 0 | 1.1021 | 1.1021 | -0.35161 | -0.35161
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6208e-11 | 0 | 8.184e-11 | 0 | 0 | 0 | 1.1021 | 1.1021 | -0.35161 | -0.35161
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 1.1154 | -0.12515 | -0.12515

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.65034 | -0.48775 | 0.67743 | -0.50807 | -52.8727 | 127.1273 | 0.80677 | 0.60508 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036
Line4_2_6 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.48775 | -0.32517 | 0.50807 | -0.33872 | -52.8727 | 127.1273 | 0.60508 | 0.40338 | -6.7036 | -6.7036
Line5_6_7 | 1.6801 | 1.6801 | 0 | 0 | 1.164 | 1.164 | 0.32517 | -0.16258 | 0.33872 | -0.16936 | -52.8727 | 127.1273 | 0.40338 | 0.20169 | -6.7036 | -6.7036
Line6_7_8 | 1.6801 | 1.6801 | 0 | 2.6638 | 1.164 | 1.164 | 0.16258 | -1e-07 | 0.16936 | -1e-07 | -52.8727 | 127.1273 | 0.20169 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7987e-22 | 0 | 9.0104e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7987e-22 | 0 | 9.0104e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80677 | 0.80677 | -6.7036 | -6.7036

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.58368 | -0.43776 | 0.608 | -0.456 | -52.8727 | 127.1273 | 0.76431 | 0.57323 | -6.7036 | -6.7036
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036
Line4_2_6 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.43776 | -0.29184 | 0.456 | -0.304 | -52.8727 | 127.1273 | 0.57323 | 0.38215 | -6.7036 | -6.7036
Line5_6_7 | 1.5916 | 1.5916 | 0 | 0 | 1.1027 | 1.1027 | 0.29184 | -0.14592 | 0.304 | -0.152 | -52.8727 | 127.1273 | 0.38215 | 0.19108 | -6.7036 | -6.7036
Line6_7_8 | 1.5916 | 1.5916 | 0 | 2.5236 | 1.1027 | 1.1027 | 0.14592 | -1e-07 | 0.152 | -1e-07 | -52.8727 | 127.1273 | 0.19108 | 0 | -6.7036 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1001e-22 | 0 | 8.0913e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1001e-22 | 0 | 8.0913e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76431 | 0.76431 | -6.7036 | -6.7036

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.01414 | -0.014086 | 0.014149 | -0.014093 | -45.1423 | 134.8577 | 0.94756 | 0.9439 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428
Line4_2_6 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014086 | -0.014033 | 0.014093 | -0.014037 | -45.1423 | 134.8577 | 0.9439 | 0.94024 | -0.12874 | -0.13323
Line5_6_7 | 0.030469 | 0.030469 | 0 | 0 | 0.02111 | 0.02111 | 0.014033 | -0.013979 | 0.014037 | -0.013981 | -45.1423 | 134.8577 | 0.94024 | 0.93659 | -0.13323 | -0.13776
Line6_7_8 | 0.030469 | 0.030469 | 0 | 0.04831 | 0.02111 | 0.02111 | 0.013979 | -0.013926 | 0.013981 | -0.013926 | -45.1423 | 134.8577 | 0.93659 | 0.93293 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7514e-10 | 0 | 2.4218e-11 | 0 | 0 | 0 | 0.93293 | 0.93293 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.12428 | -0.12428

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.01269 | -0.012642 | 0.012698 | -0.012648 | -45.1423 | 134.8577 | 0.89769 | 0.89422 | -0.12428 | -0.12874
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428
Line4_2_6 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012642 | -0.012594 | 0.012648 | -0.012598 | -45.1423 | 134.8577 | 0.89422 | 0.89076 | -0.12874 | -0.13323
Line5_6_7 | 0.028866 | 0.028866 | 0 | 0 | 0.019999 | 0.019999 | 0.012594 | -0.012546 | 0.012598 | -0.012548 | -45.1423 | 134.8577 | 0.89076 | 0.88729 | -0.13323 | -0.13776
Line6_7_8 | 0.028866 | 0.028866 | 0 | 0.045767 | 0.019999 | 0.019999 | 0.012546 | -0.012498 | 0.012548 | -0.012498 | -45.1423 | 134.8577 | 0.88729 | 0.88383 | -0.13776 | -0.14233
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5719e-10 | 0 | 2.1736e-11 | 0 | 0 | 0 | 0.88383 | 0.88383 | -0.14233 | -0.14233
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.12428 | -0.12428

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.9164 | 1.9164 | 0 | 1.9164 | 1.9164 | 0 | 0.44257 | 0.44257 | 0 | 0.44257 | 0.44257 | 4.1016e-10 | 0.36574 | -0.071931 | -4.1016e-10 | -0.32901 | 0.10866 | 1.9396e-16 | 0.20487 | 0.38274 | -2.1366e-16 | -0.13142 | -0.30929 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.80052 | 0.74072 | -4.9682e-07 | -128.6271 | 122.7608 | -5.0455e-07 | -136.1092 | 131.4739
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1016e-10 | -1.8945e-09 | -3.2684e-09 | -4.1016e-10 | 1.8945e-09 | 3.2684e-09 | 1.9383e-16 | 3.2821e-09 | -9.7909e-10 | -2.5303e-16 | -3.2821e-09 | 9.7909e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -5.1616e-07 | -128.6271 | 122.7608 | -5.2389e-07 | -128.6271 | 122.7608
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.418e-10 | -1.5787e-09 | -2.7236e-09 | -3.418e-10 | 1.5787e-09 | 2.7236e-09 | 1.5489e-16 | 2.7351e-09 | -8.1591e-10 | -1.5485e-16 | -2.7351e-09 | 8.1591e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -5.2389e-07 | -128.6271 | 122.7608 | -5.3033e-07 | -128.6271 | 122.7608
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0508e-10 | -9.4723e-10 | -1.6342e-09 | -2.0508e-10 | 9.4723e-10 | 1.6342e-09 | 1.1661e-16 | 1.6411e-09 | -4.8954e-10 | -1.166e-16 | -1.6411e-09 | 4.8954e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -5.3033e-07 | -128.6271 | 122.7608 | -5.342e-07 | -128.6271 | 122.7608
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8359e-11 | -3.1574e-10 | -5.4473e-10 | -6.8359e-11 | 3.1574e-10 | 5.4473e-10 | 3.8871e-17 | 5.4702e-10 | -1.6318e-10 | -3.887e-17 | -5.4702e-10 | 1.6318e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -5.3033e-07 | -128.6271 | 122.7608 | -5.3162e-07 | -128.6271 | 122.7608
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3672e-10 | -6.3149e-10 | -1.0895e-09 | -1.3672e-10 | 6.3149e-10 | 1.0895e-09 | 5.7982e-17 | 1.094e-09 | -3.2636e-10 | -1.1723e-16 | -1.094e-09 | 3.2636e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -5.342e-07 | -128.6271 | 122.7608 | -5.3678e-07 | -128.6271 | 122.7608
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8359e-11 | -3.1574e-10 | -5.4473e-10 | -6.8359e-11 | 3.1574e-10 | 5.4473e-10 | -6.4043e-19 | 5.4702e-10 | -1.6318e-10 | -3.8862e-17 | -5.4702e-10 | 1.6318e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -5.3678e-07 | -128.6271 | 122.7608 | -5.3807e-07 | -128.6271 | 122.7608
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3134e-10 | -2.6123e-10 | -5.0521e-10 | -1.3134e-10 | 2.6124e-10 | 5.0521e-10 | 2.3955e-11 | 5.7098e-10 | -1.3923e-10 | -2.3955e-11 | -5.7098e-10 | 1.3923e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0831 | 0.96355 | 0.89523 | 1.0831 | 0.96355 | 0.89523 | -0.32916 | -128.854 | 122.3151 | -0.32916 | -128.854 | 122.3151
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8359e-11 | -3.1574e-10 | -5.4473e-10 | -6.8359e-11 | 3.1574e-10 | 5.4473e-10 | 1.9156e-17 | 5.4702e-10 | -1.6318e-10 | -3.8907e-17 | -5.4702e-10 | 1.6318e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -4.994e-07 | -128.6271 | 122.7608 | -5.0069e-07 | -128.6271 | 122.7608
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4687e-10 | -2.526e-09 | -4.3578e-09 | -5.4687e-10 | 2.526e-09 | 4.3578e-09 | 3.7055e-16 | 4.3762e-09 | -1.3055e-09 | -3.507e-16 | -4.3762e-09 | 1.3055e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -4.9682e-07 | -128.6271 | 122.7608 | -5.0713e-07 | -128.6271 | 122.7608
Line2_1_4 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0035634 | -0.0087898 | -0.0012446 | 0.0038634 | 0.0090898 | 0.0015446 | -0.04255 | -0.036855 | -0.035176 | 0.04315 | 0.037455 | 0.035776 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0675 | 0.94721 | 0.87995 | 1.0831 | 0.96355 | 0.89523 | -4.9682e-07 | -128.6271 | 122.7608 | -0.32916 | -128.854 | 122.3151
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3672e-10 | -6.3149e-10 | -1.0895e-09 | -1.3672e-10 | 6.3149e-10 | 1.0895e-09 | 7.7823e-17 | 1.094e-09 | -3.2636e-10 | -7.7817e-17 | -1.094e-09 | 3.2636e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -4.9682e-07 | -128.6271 | 122.7608 | -4.994e-07 | -128.6271 | 122.7608
Line4_2_6 | 0 | 1.9164 | 1.9164 | 0 | 1.9164 | 1.9164 | 0 | 0.44257 | 0.44257 | 0 | 0.44257 | 0.44257 | 3.418e-10 | 0.32901 | -0.10866 | -3.418e-10 | -0.29229 | 0.14538 | 1.9451e-16 | 0.13142 | 0.30929 | -1.9447e-16 | -0.057968 | -0.23584 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.0675 | 0.80052 | 0.74072 | 1.0675 | 0.67329 | 0.626 | -5.0455e-07 | -136.1092 | 131.4739 | -5.11e-07 | -146.6652 | 143.7688
Line5_6_7 | 0 | 1.9164 | 1.9164 | 0 | 1.9164 | 1.9164 | 0 | 0.44257 | 0.44257 | 0 | 0.44257 | 0.44257 | 2.7344e-10 | 0.29229 | -0.14538 | -2.7344e-10 | -0.25556 | 0.18211 | 1.5558e-16 | 0.057968 | 0.23584 | -7.6545e-17 | 0.015484 | -0.16239 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.0675 | 0.67329 | 0.626 | 1.0675 | 0.5785 | 0.55131 | -5.11e-07 | -146.6652 | 143.7688 | -5.1616e-07 | -161.35 | 160.3935
Line6_7_8 | 0 | 1.9164 | 1.9164 | 0 | 1.9164 | 1.9164 | 0 | 0.44257 | 0.44257 | 0 | 0.44257 | 0.44257 | 2.0508e-10 | 0.25556 | -0.18211 | -2.0508e-10 | -0.21883 | 0.21883 | -1.8475e-18 | -0.015484 | 0.16239 | 1.8613e-18 | 0.088936 | -0.088936 | 0 | -157.8829 | 22.1171 | 0 | 22.1171 | -157.8829 | 1.0675 | 0.5785 | 0.55131 | 1.0675 | 0.53373 | 0.53373 | -5.1616e-07 | -161.35 | 160.3935 | -5.2002e-07 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8359e-11 | 1.709e-11 | 1.709e-11 | -6.8359e-11 | -1.709e-11 | -1.709e-11 | 1.1789e-16 | 1.7796e-09 | -1.7796e-09 | -3.8882e-17 | -1.7796e-09 | 1.7796e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.53373 | 0.53373 | 1.0675 | 0.53373 | 0.53373 | -5.2002e-07 | 180 | 180 | -5.2131e-07 | 180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.836e-11 | 1.709e-11 | 1.7089e-11 | -6.836e-11 | -1.709e-11 | -1.709e-11 | -4.0125e-17 | 1.7796e-09 | -1.7796e-09 | 7.963e-17 | -1.7796e-09 | 1.7796e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.53373 | 0.53373 | 1.0675 | 0.53373 | 0.53373 | -5.2002e-07 | 180 | 180 | -5.2131e-07 | 180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7852e-10 | -2.2102e-09 | -3.8131e-09 | -4.7852e-10 | 2.2102e-09 | 3.8131e-09 | 2.9205e-16 | 3.8292e-09 | -1.1423e-09 | -3.1172e-16 | -3.8292e-09 | 1.1423e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 0.94721 | 0.87995 | 1.0675 | 0.94721 | 0.87995 | -5.0713e-07 | -128.6271 | 122.7608 | -5.1616e-07 | -128.6271 | 122.7608

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.9889 | 1.9889 | 0 | 1.9889 | 1.9889 | 0 | 0.45931 | 0.45931 | 0 | 0.45931 | 0.45931 | 4.4999e-10 | 0.39643 | -0.079979 | -4.4999e-10 | -0.35688 | 0.11954 | 1.6129e-16 | 0.22045 | 0.41245 | -1.6123e-16 | -0.14134 | -0.33334 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.83569 | 0.77099 | -5.4077e-07 | -128.9719 | 122.9242 | -5.485e-07 | -136.444 | 131.6779
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4999e-10 | -2.1502e-09 | -3.7e-09 | -4.4999e-10 | 2.1502e-09 | 3.7e-09 | 2.4391e-16 | 3.7271e-09 | -1.1292e-09 | -2.6454e-16 | -3.7271e-09 | 1.1292e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.6009e-07 | -128.9719 | 122.9242 | -5.6783e-07 | -128.9719 | 122.9242
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7499e-10 | -1.7919e-09 | -3.0833e-09 | -3.7499e-10 | 1.7919e-09 | 3.0833e-09 | 2.0321e-16 | 3.1059e-09 | -9.4104e-10 | -2.0317e-16 | -3.1059e-09 | 9.4104e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.6783e-07 | -128.9719 | 122.9242 | -5.7427e-07 | -128.9719 | 122.9242
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25e-10 | -1.0751e-09 | -1.85e-09 | -2.25e-10 | 1.0751e-09 | 1.85e-09 | 1.6329e-16 | 1.8635e-09 | -5.6462e-10 | -1.6327e-16 | -1.8635e-09 | 5.6462e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.7427e-07 | -128.9719 | 122.9242 | -5.7813e-07 | -128.9719 | 122.9242
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4998e-11 | -3.5837e-10 | -6.1666e-10 | -7.4998e-11 | 3.5837e-10 | 6.1666e-10 | 4.0633e-17 | 6.2118e-10 | -1.8821e-10 | -4.0632e-17 | -6.2118e-10 | 1.8821e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.7427e-07 | -128.9719 | 122.9242 | -5.7556e-07 | -128.9719 | 122.9242
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5e-10 | -7.1675e-10 | -1.2333e-09 | -1.5e-10 | 7.1675e-10 | 1.2333e-09 | 8.1257e-17 | 1.2424e-09 | -3.7641e-10 | -8.125e-17 | -1.2424e-09 | 3.7641e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.7813e-07 | -128.9719 | 122.9242 | -5.8071e-07 | -128.9719 | 122.9242
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4998e-11 | -3.5837e-10 | -6.1666e-10 | -7.4998e-11 | 3.5837e-10 | 6.1666e-10 | -7.6013e-19 | 6.2118e-10 | -1.8821e-10 | 7.6182e-19 | -6.2118e-10 | 1.8821e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.8071e-07 | -128.9719 | 122.9242 | -5.82e-07 | -128.9719 | 122.9242
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4093e-10 | -3.0172e-10 | -5.7625e-10 | -1.4093e-10 | 3.0172e-10 | 5.7625e-10 | 2.5096e-11 | 6.4627e-10 | -1.6311e-10 | -2.5096e-11 | -6.4627e-10 | 1.6311e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1339 | 1.0039 | 0.92997 | 1.1339 | 1.0039 | 0.92997 | -0.31441 | -129.184 | 122.4924 | -0.31441 | -129.184 | 122.4924
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4998e-11 | -3.5837e-10 | -6.1666e-10 | -7.4998e-11 | 3.5837e-10 | 6.1666e-10 | -7.1122e-19 | 6.2118e-10 | -1.8821e-10 | 2.1405e-17 | -6.2118e-10 | 1.8821e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.4334e-07 | -128.9719 | 122.9242 | -5.4463e-07 | -128.9719 | 122.9242
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9999e-10 | -2.867e-09 | -4.9333e-09 | -5.9999e-10 | 2.867e-09 | 4.9333e-09 | 4.0819e-16 | 4.9694e-09 | -1.5057e-09 | -4.2877e-16 | -4.9694e-09 | 1.5057e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.4077e-07 | -128.9719 | 122.9242 | -5.5107e-07 | -128.9719 | 122.9242
Line2_1_4 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0037328 | -0.0093952 | -0.0011893 | 0.0040328 | 0.0096952 | 0.0014893 | -0.044576 | -0.038369 | -0.036569 | 0.045176 | 0.038969 | 0.037169 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1183 | 0.98757 | 0.9147 | 1.1339 | 1.0039 | 0.92997 | -5.4077e-07 | -128.9719 | 122.9242 | -0.31441 | -129.184 | 122.4924
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5e-10 | -7.1675e-10 | -1.2333e-09 | -1.5e-10 | 7.1675e-10 | 1.2333e-09 | 3.9969e-17 | 1.2424e-09 | -3.7641e-10 | -6.0655e-17 | -1.2424e-09 | 3.7641e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.4077e-07 | -128.9719 | 122.9242 | -5.4334e-07 | -128.9719 | 122.9242
Line4_2_6 | 0 | 1.9889 | 1.9889 | 0 | 1.9889 | 1.9889 | 0 | 0.45931 | 0.45931 | 0 | 0.45931 | 0.45931 | 3.7499e-10 | 0.35688 | -0.11954 | -3.7499e-10 | -0.31732 | 0.15909 | 1.2057e-16 | 0.14134 | 0.33334 | -7.9138e-17 | -0.062226 | -0.25423 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1183 | 0.83569 | 0.77099 | 1.1183 | 0.70401 | 0.65294 | -5.485e-07 | -136.444 | 131.6779 | -5.5494e-07 | -146.955 | 143.988
Line5_6_7 | 0 | 1.9889 | 1.9889 | 0 | 1.9889 | 1.9889 | 0 | 0.45931 | 0.45931 | 0 | 0.45931 | 0.45931 | 2.9999e-10 | 0.31732 | -0.15909 | -2.9999e-10 | -0.27776 | 0.19865 | -2.9056e-18 | 0.062226 | 0.25423 | -3.8452e-17 | 0.016887 | -0.17511 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1183 | 0.70401 | 0.65294 | 1.1183 | 0.60585 | 0.57654 | -5.5494e-07 | -146.955 | 143.988 | -5.6009e-07 | -161.529 | 160.5532
Line6_7_8 | 0 | 1.9889 | 1.9889 | 0 | 1.9889 | 1.9889 | 0 | 0.45931 | 0.45931 | 0 | 0.45931 | 0.45931 | 2.25e-10 | 0.27776 | -0.19865 | -2.25e-10 | -0.23821 | 0.23821 | 3.9186e-17 | -0.016887 | 0.17511 | -8.0556e-17 | 0.096 | -0.096 | 0 | -158.05 | 21.95 | 0 | 21.95 | -158.05 | 1.1183 | 0.60585 | 0.57654 | 1.1183 | 0.55915 | 0.55915 | -5.6009e-07 | -161.529 | 160.5532 | -5.6396e-07 | 180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4999e-11 | 1.875e-11 | 1.8749e-11 | -7.4999e-11 | -1.875e-11 | -1.875e-11 | -7.3821e-19 | 1.9531e-09 | -1.9531e-09 | 7.3989e-19 | -1.9531e-09 | 1.9531e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.55915 | 0.55915 | 1.1183 | 0.55915 | 0.55915 | -5.6396e-07 | 180 | 180 | -5.6525e-07 | 180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4998e-11 | 1.875e-11 | 1.875e-11 | -7.4998e-11 | -1.875e-11 | -1.875e-11 | 8.2032e-17 | 1.9531e-09 | -1.9531e-09 | -1.2342e-16 | -1.9531e-09 | 1.9531e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.55915 | 0.55915 | 1.1183 | 0.55915 | 0.55915 | -5.6396e-07 | 180 | 180 | -5.6525e-07 | 180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2499e-10 | -2.5086e-09 | -4.3166e-09 | -5.2499e-10 | 2.5086e-09 | 4.3166e-09 | 3.0534e-16 | 4.3483e-09 | -1.3174e-09 | -3.2595e-16 | -4.3483e-09 | 1.3175e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 0.98757 | 0.9147 | 1.1183 | 0.98757 | 0.9147 | -5.5107e-07 | -128.9719 | 122.9242 | -5.6009e-07 | -128.9719 | 122.9242

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.058677 | 0.058677 | 0 | 0.058677 | 0.058677 | 0 | 0.013551 | 0.013551 | 0 | 0.013551 | 0.013551 | 4.1016e-10 | 0.01392 | 0.0035705 | -4.1016e-10 | -0.013886 | -0.0035361 | 2.781e-17 | 0.00383 | 0.013936 | -4.3803e-17 | -0.0037612 | -0.013867 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0616 | 1.0561 | 4.6331e-09 | -120.2981 | 119.9471 | -3.1008e-09 | -120.5262 | 120.0122
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1016e-10 | 3.6154e-10 | 2.7165e-10 | -4.1016e-10 | -3.6154e-10 | -2.7165e-10 | -3.2202e-17 | 1.2805e-10 | 2.263e-11 | 7.5676e-18 | -1.2805e-10 | -2.263e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | -1.4702e-08 | -120.2981 | 119.9471 | -2.2435e-08 | -120.2981 | 119.9471
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.418e-10 | 3.0128e-10 | 2.2638e-10 | -3.418e-10 | -3.0128e-10 | -2.2638e-10 | -2.9762e-17 | 1.0671e-10 | 1.8858e-11 | 1.4986e-17 | -1.0671e-10 | -1.8858e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | -2.2435e-08 | -120.2981 | 119.9471 | -2.888e-08 | -120.2981 | 119.9471
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0508e-10 | 1.8077e-10 | 1.3583e-10 | -2.0508e-10 | -1.8077e-10 | -1.3583e-10 | 1.3476e-17 | 6.4023e-11 | 1.1315e-11 | -1.2228e-17 | -6.4023e-11 | -1.1315e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | -2.888e-08 | -120.2981 | 119.9471 | -3.2747e-08 | -120.2981 | 119.9471
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8359e-11 | 6.0256e-11 | 4.5275e-11 | -6.8359e-11 | -6.0256e-11 | -4.5275e-11 | 7.3726e-18 | 2.1341e-11 | 3.7717e-12 | -1.7247e-17 | -2.1341e-11 | -3.7717e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | -2.888e-08 | -120.2981 | 119.9471 | -3.0169e-08 | -120.2981 | 119.9471
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3672e-10 | 1.2051e-10 | 9.0551e-11 | -1.3672e-10 | -1.2051e-10 | -9.0551e-11 | -2.1065e-17 | 4.2682e-11 | 7.5434e-12 | 9.9603e-18 | -4.2682e-11 | -7.5434e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | -3.2747e-08 | -120.2981 | 119.9471 | -3.5325e-08 | -120.2981 | 119.9471
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8359e-11 | 6.0257e-11 | 4.5275e-11 | -6.8359e-11 | -6.0257e-11 | -4.5275e-11 | -3.4608e-17 | 2.1341e-11 | 3.7717e-12 | 1.2389e-17 | -2.1341e-11 | -3.7717e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | -3.5325e-08 | -120.2981 | 119.9471 | -3.6614e-08 | -120.2981 | 119.9471
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3134e-10 | 1.2326e-10 | 1.0764e-10 | -1.3134e-10 | -1.2326e-10 | -1.0764e-10 | 2.3955e-11 | 4.5296e-11 | 2.7726e-11 | -2.3955e-11 | -4.5296e-11 | -2.7726e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0831 | 1.081 | 1.0772 | 1.0831 | 1.081 | 1.0772 | -0.32916 | -120.6236 | 119.617 | -0.32916 | -120.6236 | 119.617
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8359e-11 | 6.0257e-11 | 4.5275e-11 | -6.8359e-11 | -6.0257e-11 | -4.5275e-11 | -3.7033e-17 | 2.1341e-11 | 3.7717e-12 | 2.4689e-17 | -2.1341e-11 | -3.7717e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | 2.0551e-09 | -120.2981 | 119.9471 | 7.6617e-10 | -120.2981 | 119.9471
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4687e-10 | 4.8205e-10 | 3.622e-10 | -5.4687e-10 | -4.8205e-10 | -3.622e-10 | -2.3411e-17 | 1.7073e-10 | 3.0173e-11 | 7.4612e-18 | -1.7073e-10 | -3.0173e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | 4.6331e-09 | -120.2981 | 119.9471 | -5.6787e-09 | -120.2981 | 119.9471
Line2_1_4 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0035634 | -0.0037775 | -0.003583 | 0.0038634 | 0.0040775 | 0.003883 | -0.04255 | -0.042449 | -0.042314 | 0.04315 | 0.043049 | 0.042914 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.0675 | 1.0654 | 1.0616 | 1.0831 | 1.081 | 1.0772 | 4.6331e-09 | -120.2981 | 119.9471 | -0.32916 | -120.6236 | 119.617
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3672e-10 | 1.2051e-10 | 9.0551e-11 | -1.3672e-10 | -1.2051e-10 | -9.0551e-11 | -1.8507e-17 | 4.2682e-11 | 7.5434e-12 | 2.4641e-18 | -4.2682e-11 | -7.5434e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | 4.6331e-09 | -120.2981 | 119.9471 | 2.0551e-09 | -120.2981 | 119.9471
Line4_2_6 | 0 | 0.058677 | 0.058677 | 0 | 0.058677 | 0.058677 | 0 | 0.013551 | 0.013551 | 0 | 0.013551 | 0.013551 | 3.418e-10 | 0.013886 | 0.0035361 | -3.418e-10 | -0.013851 | -0.0035017 | 1.6647e-17 | 0.0037612 | 0.013867 | -2.8182e-17 | -0.0036923 | -0.013798 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.0675 | 1.0616 | 1.0561 | 1.0675 | 1.0578 | 1.0505 | -3.1008e-09 | -120.5262 | 120.0122 | -9.5456e-09 | -120.7558 | 120.078
Line5_6_7 | 0 | 0.058677 | 0.058677 | 0 | 0.058677 | 0.058677 | 0 | 0.013551 | 0.013551 | 0 | 0.013551 | 0.013551 | 2.7344e-10 | 0.013851 | 0.0035017 | -2.7344e-10 | -0.013817 | -0.0034673 | 3.9666e-18 | 0.0036923 | 0.013798 | -2.3385e-17 | -0.0036235 | -0.013729 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.0675 | 1.0578 | 1.0505 | 1.0675 | 1.0541 | 1.045 | -9.5456e-09 | -120.7558 | 120.078 | -1.4702e-08 | -120.9872 | 120.1445
Line6_7_8 | 0 | 0.058677 | 0.058677 | 0 | 0.058677 | 0.058677 | 0 | 0.013551 | 0.013551 | 0 | 0.013551 | 0.013551 | 2.0508e-10 | 0.013817 | 0.0034673 | -2.0508e-10 | -0.013782 | -0.0034328 | 6.1199e-18 | 0.0036235 | 0.013729 | -1.8451e-17 | -0.0035546 | -0.013661 | 0 | -135.6822 | 44.3178 | 0 | 44.3178 | -135.6822 | 1.0675 | 1.0541 | 1.045 | 1.0675 | 1.0504 | 1.0394 | -1.4702e-08 | -120.9872 | 120.1445 | -1.8568e-08 | -121.2201 | 120.2117
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8359e-11 | 2.2843e-12 | -4.0262e-11 | -6.8359e-11 | -2.2843e-12 | 4.0262e-11 | -1.854e-17 | 8.6108e-11 | -1.4788e-11 | 3.7272e-18 | -8.6108e-11 | 1.4788e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0504 | 1.0394 | 1.0675 | 1.0504 | 1.0394 | -1.8568e-08 | -121.2201 | 120.2117 | -1.9857e-08 | -121.2201 | 120.2117
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8359e-11 | 2.2843e-12 | -4.0262e-11 | -6.8359e-11 | -2.2843e-12 | 4.0262e-11 | -2.7181e-17 | 8.6108e-11 | -1.4788e-11 | 1.2369e-17 | -8.6108e-11 | 1.4788e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0504 | 1.0394 | 1.0675 | 1.0504 | 1.0394 | -1.8568e-08 | -121.2201 | 120.2117 | -1.9857e-08 | -121.2201 | 120.2117
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7851e-10 | 4.218e-10 | 3.1693e-10 | -4.7851e-10 | -4.218e-10 | -3.1693e-10 | -2.1034e-17 | 1.4939e-10 | 2.6402e-11 | 7.5298e-18 | -1.4939e-10 | -2.6402e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0675 | 1.0654 | 1.0616 | 1.0675 | 1.0654 | 1.0616 | -5.6787e-09 | -120.2981 | 119.9471 | -1.4702e-08 | -120.2981 | 119.9471

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.061457 | 0.061457 | 0 | 0.061457 | 0.061457 | 0 | 0.014193 | 0.014193 | 0 | 0.014193 | 0.014193 | 4.4999e-10 | 0.015272 | 0.0039144 | -4.4999e-10 | -0.015235 | -0.0038767 | 2.0715e-17 | 0.0042013 | 0.015288 | -2.906e-17 | -0.0041258 | -0.015212 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.1121 | 1.1061 | 2.8334e-09 | -120.3121 | 119.9447 | -4.8978e-09 | -120.5402 | 120.0098
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4999e-10 | 3.9414e-10 | 2.9087e-10 | -4.4999e-10 | -3.9414e-10 | -2.9087e-10 | -3.1168e-17 | 1.4713e-10 | 2.5975e-11 | 3.5109e-17 | -1.4713e-10 | -2.5975e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | -1.6495e-08 | -120.3121 | 119.9447 | -2.4226e-08 | -120.3121 | 119.9447
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7499e-10 | 3.2845e-10 | 2.424e-10 | -3.7499e-10 | -3.2845e-10 | -2.424e-10 | -3.3784e-17 | 1.2261e-10 | 2.1646e-11 | 1.0547e-17 | -1.2261e-10 | -2.1646e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | -2.4226e-08 | -120.3121 | 119.9447 | -3.0669e-08 | -120.3121 | 119.9447
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25e-10 | 1.9707e-10 | 1.4544e-10 | -2.25e-10 | -1.9707e-10 | -1.4544e-10 | -1.0467e-17 | 7.3564e-11 | 1.2988e-11 | 5.3087e-18 | -7.3564e-11 | -1.2988e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | -3.0669e-08 | -120.3121 | 119.9447 | -3.4534e-08 | -120.3121 | 119.9447
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4998e-11 | 6.569e-11 | 4.8479e-11 | -7.4998e-11 | -6.569e-11 | -4.8479e-11 | 9.0128e-18 | 2.4521e-11 | 4.3292e-12 | -1.6771e-17 | -2.4521e-11 | -4.3292e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | -3.0669e-08 | -120.3121 | 119.9447 | -3.1957e-08 | -120.3121 | 119.9447
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5e-10 | 1.3138e-10 | 9.6958e-11 | -1.5e-10 | -1.3138e-10 | -9.6958e-11 | -1.949e-17 | 4.9043e-11 | 8.6584e-12 | 1.8203e-17 | -4.9043e-11 | -8.6584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | -3.4534e-08 | -120.3121 | 119.9447 | -3.7111e-08 | -120.3121 | 119.9447
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4998e-11 | 6.569e-11 | 4.8479e-11 | -7.4998e-11 | -6.569e-11 | -4.8479e-11 | -1.5568e-17 | 2.4521e-11 | 4.3292e-12 | 2.6368e-18 | -2.4521e-11 | -4.3292e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | -3.7111e-08 | -120.3121 | 119.9447 | -3.84e-08 | -120.3121 | 119.9447
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4093e-10 | 1.3164e-10 | 1.1373e-10 | -1.4093e-10 | -1.3164e-10 | -1.1373e-10 | 2.5096e-11 | 4.9617e-11 | 2.9425e-11 | -2.5096e-11 | -4.9617e-11 | -2.9425e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1339 | 1.1317 | 1.1275 | 1.1339 | 1.1317 | 1.1275 | -0.31441 | -120.6228 | 119.6293 | -0.31441 | -120.6228 | 119.6293
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4998e-11 | 6.569e-11 | 4.8479e-11 | -7.4998e-11 | -6.569e-11 | -4.8479e-11 | -2.0692e-17 | 2.4521e-11 | 4.3292e-12 | 3.8812e-18 | -2.4521e-11 | -4.3292e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | 2.5635e-10 | -120.3121 | 119.9447 | -1.0322e-09 | -120.3121 | 119.9447
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9999e-10 | 5.2552e-10 | 3.8783e-10 | -5.9999e-10 | -5.2552e-10 | -3.8783e-10 | -1.4196e-17 | 1.9617e-10 | 3.4634e-11 | 6.5447e-18 | -1.9617e-10 | -3.4634e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | 2.8334e-09 | -120.3121 | 119.9447 | -7.4749e-09 | -120.3121 | 119.9447
Line2_1_4 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0037329 | -0.0039676 | -0.0037543 | 0.0040329 | 0.0042676 | 0.0040543 | -0.044576 | -0.044465 | -0.044317 | 0.045176 | 0.045065 | 0.044917 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1183 | 1.116 | 1.1119 | 1.1339 | 1.1317 | 1.1275 | 2.8334e-09 | -120.3121 | 119.9447 | -0.31441 | -120.6228 | 119.6293
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5e-10 | 1.3138e-10 | 9.6958e-11 | -1.5e-10 | -1.3138e-10 | -9.6958e-11 | -3.6205e-17 | 4.9043e-11 | 8.6584e-12 | 1.6812e-17 | -4.9043e-11 | -8.6584e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | 2.8334e-09 | -120.3121 | 119.9447 | 2.5635e-10 | -120.3121 | 119.9447
Line4_2_6 | 0 | 0.061457 | 0.061457 | 0 | 0.061457 | 0.061457 | 0 | 0.014193 | 0.014193 | 0 | 0.014193 | 0.014193 | 3.7499e-10 | 0.015235 | 0.0038767 | -3.7499e-10 | -0.015197 | -0.0038389 | 3.6861e-18 | 0.0041258 | 0.015212 | -6.0689e-18 | -0.0040502 | -0.015137 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1183 | 1.1121 | 1.1061 | 1.1183 | 1.1081 | 1.1003 | -4.8978e-09 | -120.5402 | 120.0098 | -1.134e-08 | -120.7698 | 120.0757
Line5_6_7 | 0 | 0.061457 | 0.061457 | 0 | 0.061457 | 0.061457 | 0 | 0.014193 | 0.014193 | 0 | 0.014193 | 0.014193 | 2.9999e-10 | 0.015197 | 0.0038389 | -2.9999e-10 | -0.015159 | -0.0038011 | -3.3361e-17 | 0.0040502 | 0.015137 | 1.3989e-17 | -0.0039747 | -0.015061 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1183 | 1.1081 | 1.1003 | 1.1183 | 1.1042 | 1.0944 | -1.134e-08 | -120.7698 | 120.0757 | -1.6495e-08 | -121.0011 | 120.1422
Line6_7_8 | 0 | 0.061457 | 0.061457 | 0 | 0.061457 | 0.061457 | 0 | 0.014193 | 0.014193 | 0 | 0.014193 | 0.014193 | 2.25e-10 | 0.015159 | 0.0038011 | -2.25e-10 | -0.015121 | -0.0037634 | -1.5584e-17 | 0.0039747 | 0.015061 | -2.5066e-18 | -0.0038991 | -0.014986 | 0 | -135.6932 | 44.3068 | 0 | 44.3068 | -135.6932 | 1.1183 | 1.1042 | 1.0944 | 1.1183 | 1.1003 | 1.0886 | -1.6495e-08 | -121.0011 | 120.1422 | -2.036e-08 | -121.2341 | 120.2095
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4998e-11 | 2.1136e-12 | -4.5324e-11 | -7.4998e-11 | -2.1136e-12 | 4.5324e-11 | 2.5599e-18 | 9.5574e-11 | -1.6054e-11 | -2.5582e-18 | -9.5574e-11 | 1.6054e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.1003 | 1.0886 | 1.1183 | 1.1003 | 1.0886 | -2.036e-08 | -121.2341 | 120.2095 | -2.1649e-08 | -121.2341 | 120.2095
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4999e-11 | 2.1136e-12 | -4.5324e-11 | -7.4999e-11 | -2.1136e-12 | 4.5324e-11 | 1.2666e-18 | 9.5574e-11 | -1.6054e-11 | 2.8338e-20 | -9.5574e-11 | 1.6054e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.1003 | 1.0886 | 1.1183 | 1.1003 | 1.0886 | -2.036e-08 | -121.2341 | 120.2095 | -2.1649e-08 | -121.2341 | 120.2095
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2499e-10 | 4.5983e-10 | 3.3935e-10 | -5.2499e-10 | -4.5983e-10 | -3.3935e-10 | -1.0415e-17 | 1.7165e-10 | 3.0304e-11 | 7.9108e-18 | -1.7165e-10 | -3.0304e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1183 | 1.116 | 1.1119 | 1.1183 | 1.116 | 1.1119 | -7.4749e-09 | -120.3121 | 119.9447 | -1.6495e-08 | -120.3121 | 119.9447

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | 2.1094e-16 | 0.28984 | 0.03533 | -1.9336e-16 | -0.24919 | 0.005316 | 1.0547e-16 | 0.073022 | 0.26569 | -8.7893e-17 | -0.030682 | -0.22336 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.74721 | 0.66491 | 9.3717e-14 | -128.7319 | 119.553 | 9.952e-14 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7579e-17 | -9.6789e-10 | -2.6725e-09 | -8.7893e-18 | 9.6789e-10 | 2.6725e-09 | 3.5157e-17 | 2.8224e-09 | 1.3007e-10 | -3.5157e-17 | -2.8224e-09 | -1.3007e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 9.7318e-14 | -128.7319 | 119.553 | 9.9585e-14 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3184e-17 | -8.0657e-10 | -2.2271e-09 | 1.3184e-17 | 8.0657e-10 | 2.2271e-09 | 8.7893e-17 | 2.352e-09 | 1.0839e-10 | -7.0314e-17 | -2.352e-09 | -1.0839e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 9.9585e-14 | -128.7319 | 119.553 | 1.0167e-13 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3946e-18 | -4.8394e-10 | -1.3362e-09 | 4.3946e-18 | 4.8394e-10 | 1.3362e-09 | 1.7579e-17 | 1.4112e-09 | 6.5035e-11 | -1.7579e-17 | -1.4112e-09 | -6.5035e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.0167e-13 | -128.7319 | 119.553 | 1.0265e-13 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3946e-18 | -1.6131e-10 | -4.4541e-10 | -4.3946e-18 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -3.5157e-17 | -4.7039e-10 | -2.1678e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.0167e-13 | -128.7319 | 119.553 | 1.016e-13 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -3.2263e-10 | -8.9083e-10 | 1.7579e-17 | 3.2263e-10 | 8.9083e-10 | 1.7579e-17 | 9.4079e-10 | 4.3357e-11 | -1.7579e-17 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.0265e-13 | -128.7319 | 119.553 | 1.0346e-13 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-18 | -1.6131e-10 | -4.4541e-10 | -4.3946e-18 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -1.7579e-17 | -4.7039e-10 | -2.1678e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 1.0346e-13 | -128.7319 | 119.553 | 1.0369e-13 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1973e-17 | -1.6131e-10 | -4.4541e-10 | 1.3184e-17 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -1.7579e-17 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 9.4404e-14 | -128.7319 | 119.553 | 9.464e-14 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1973e-17 | -1.6131e-10 | -4.4541e-10 | 1.3184e-17 | 1.6131e-10 | 4.4541e-10 | 1.7579e-17 | 4.7039e-10 | 2.1678e-11 | -1.7579e-17 | -4.7039e-10 | -2.1679e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 9.4404e-14 | -128.7319 | 119.553 | 9.464e-14 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5157e-17 | -1.2905e-09 | -3.5633e-09 | -3.5157e-17 | 1.2905e-09 | 3.5633e-09 | 7.0314e-17 | 3.7632e-09 | 1.7343e-10 | -5.2736e-17 | -3.7632e-09 | -1.7343e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 9.3717e-14 | -128.7319 | 119.553 | 9.5057e-14 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -3.2263e-10 | -8.9083e-10 | 8.7893e-18 | 3.2263e-10 | 8.9083e-10 | 3.5157e-17 | 9.4079e-10 | 4.3357e-11 | 1.4482e-32 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 9.3717e-14 | -128.7319 | 119.553 | 9.4404e-14 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -3.2263e-10 | -8.9083e-10 | 8.7893e-18 | 3.2263e-10 | 8.9083e-10 | 3.5157e-17 | 9.4079e-10 | 4.3357e-11 | 1.4482e-32 | -9.4079e-10 | -4.3357e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 9.3717e-14 | -128.7319 | 119.553 | 9.4404e-14 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | 1.0547e-16 | 0.24919 | -0.005316 | -1.0547e-16 | -0.20855 | 0.045962 | 2.1094e-16 | 0.030682 | 0.22336 | -2.1094e-16 | 0.011658 | -0.18102 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.74721 | 0.66491 | 0.95 | 0.62161 | 0.55581 | 9.952e-14 | -135.8534 | 128.4907 | 1.066e-13 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | 2.8126e-16 | 0.20855 | -0.045962 | -3.1641e-16 | -0.1679 | 0.086608 | 1.4063e-16 | -0.011658 | 0.18102 | -7.0314e-17 | 0.053997 | -0.13868 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.62161 | 0.55581 | 0.95 | 0.52489 | 0.48658 | 1.066e-13 | -146.0722 | 141.3743 | 1.1127e-13 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.455 | 1.455 | 0 | 1.455 | 1.455 | 0 | 0.33601 | 0.33601 | 0 | 0.33601 | 0.33601 | 2.1094e-16 | 0.1679 | -0.086608 | -1.4063e-16 | -0.12725 | 0.12725 | 7.0314e-17 | -0.053997 | 0.13868 | -7.0314e-17 | 0.096337 | -0.096337 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.95 | 0.52489 | 0.48658 | 0.95 | 0.475 | 0.475 | 1.1127e-13 | -160.7007 | 159.1134 | 1.1107e-13 | -180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7261e-31 | 7.0314e-17 | -1.4063e-16 | -7.0314e-17 | -1.022e-16 | 1.439e-16 | 1.4063e-16 | 1.4329e-09 | -1.4329e-09 | -2.1094e-16 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 1.1107e-13 | -180 | 180 | 1.0998e-13 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.0314e-17 | -2.9138e-23 | 1.4063e-16 | 4.092e-31 | 3.2761e-18 | -1.3735e-16 | 2.1094e-16 | 1.4329e-09 | -1.4329e-09 | -2.1094e-16 | -1.4329e-09 | 1.4329e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.475 | 0.475 | 0.95 | 0.475 | 0.475 | 1.1107e-13 | -180 | 180 | 1.1115e-13 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3946e-18 | -1.1292e-09 | -3.1179e-09 | 4.3946e-18 | 1.1292e-09 | 3.1179e-09 | 5.2736e-17 | 3.2928e-09 | 1.5175e-10 | -5.2736e-17 | -3.2928e-09 | -1.5175e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.88953 | 0.79769 | 0.95 | 0.88953 | 0.79769 | 9.5057e-14 | -128.7319 | 119.553 | 9.7318e-14 | -128.7319 | 119.553

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | 9.992e-17 | 0.26013 | 0.031709 | -1.1657e-16 | -0.22365 | 0.0047711 | 9.992e-17 | 0.065537 | 0.23846 | -9.992e-17 | -0.027537 | -0.20046 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.70788 | 0.62991 | 9.4662e-14 | -128.7319 | 119.553 | 1.0104e-13 | -135.8534 | 128.4907
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1424e-31 | -8.6869e-10 | -2.3986e-09 | 8.7659e-32 | 8.6869e-10 | 2.3986e-09 | 6.6613e-17 | 2.5331e-09 | 1.1674e-10 | -4.996e-17 | -2.5331e-09 | -1.1674e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 9.8263e-14 | -128.7319 | 119.553 | 1.0053e-13 | -128.7319 | 119.553
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0817e-17 | -7.2391e-10 | -1.9988e-09 | 2.0817e-17 | 7.2391e-10 | 1.9988e-09 | 4.996e-17 | 2.1109e-09 | 9.7283e-11 | -6.6613e-17 | -2.1109e-09 | -9.7283e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.0053e-13 | -128.7319 | 119.553 | 1.0262e-13 | -128.7319 | 119.553
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-18 | -4.3434e-10 | -1.1993e-09 | -1.249e-17 | 4.3434e-10 | 1.1993e-09 | 1.6653e-17 | 1.2665e-09 | 5.837e-11 | -2.2584e-32 | -1.2665e-09 | -5.837e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.0262e-13 | -128.7319 | 119.553 | 1.036e-13 | -128.7319 | 119.553
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0817e-17 | -1.4478e-10 | -3.9976e-10 | -2.0817e-17 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | -3.7258e-32 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.0262e-13 | -128.7319 | 119.553 | 1.0255e-13 | -128.7319 | 119.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6653e-17 | -2.8956e-10 | -7.9952e-10 | 8.3267e-18 | 2.8956e-10 | 7.9952e-10 | 3.3307e-17 | 8.4436e-10 | 3.8913e-11 | -3.3307e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.036e-13 | -128.7319 | 119.553 | 1.044e-13 | -128.7319 | 119.553
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -1.4478e-10 | -3.9976e-10 | 1.6653e-17 | 1.4478e-10 | 3.9976e-10 | -1.6653e-17 | 4.2218e-10 | 1.9457e-11 | 3.0414e-32 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 1.044e-13 | -128.7319 | 119.553 | 1.0464e-13 | -128.7319 | 119.553
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -1.4478e-10 | -3.9976e-10 | 8.3267e-18 | 1.4478e-10 | 3.9976e-10 | -1.3857e-32 | 4.2218e-10 | 1.9457e-11 | 1.3891e-32 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 9.5349e-14 | -128.7319 | 119.553 | 9.5585e-14 | -128.7319 | 119.553
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -1.4478e-10 | -3.9976e-10 | 8.3267e-18 | 1.4478e-10 | 3.9976e-10 | -1.3857e-32 | 4.2218e-10 | 1.9457e-11 | 1.3891e-32 | -4.2218e-10 | -1.9457e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 9.5349e-14 | -128.7319 | 119.553 | 9.5585e-14 | -128.7319 | 119.553
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-18 | -1.1582e-09 | -3.1981e-09 | 4.1633e-18 | 1.1582e-09 | 3.1981e-09 | 3.3307e-17 | 3.3775e-09 | 1.5565e-10 | -3.3307e-17 | -3.3775e-09 | -1.5565e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 9.4662e-14 | -128.7319 | 119.553 | 9.6002e-14 | -128.7319 | 119.553
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9143e-17 | -2.8956e-10 | -7.9952e-10 | 2.9143e-17 | 2.8956e-10 | 7.9952e-10 | 3.3307e-17 | 8.4436e-10 | 3.8913e-11 | -3.3307e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 9.4662e-14 | -128.7319 | 119.553 | 9.5349e-14 | -128.7319 | 119.553
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9143e-17 | -2.8956e-10 | -7.9952e-10 | 2.9143e-17 | 2.8956e-10 | 7.9952e-10 | 3.3307e-17 | 8.4436e-10 | 3.8913e-11 | -3.3307e-17 | -8.4436e-10 | -3.8913e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 9.4662e-14 | -128.7319 | 119.553 | 9.5349e-14 | -128.7319 | 119.553
Line4_2_6 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | 6.6613e-17 | 0.22365 | -0.0047711 | -6.6613e-17 | -0.18717 | 0.041251 | 1.9984e-16 | 0.027537 | 0.20046 | -1.9984e-16 | 0.010463 | -0.16246 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.70788 | 0.62991 | 0.9 | 0.5889 | 0.52656 | 1.0104e-13 | -135.8534 | 128.4907 | 1.0869e-13 | -146.0722 | 141.3743
Line5_6_7 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | 1.3323e-16 | 0.18717 | -0.041251 | -1.6653e-16 | -0.15069 | 0.077731 | 1.3323e-16 | -0.010463 | 0.16246 | -1.6653e-16 | 0.048463 | -0.12446 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.5889 | 0.52656 | 0.9 | 0.49726 | 0.46097 | 1.0869e-13 | -146.0722 | 141.3743 | 1.139e-13 | -160.7007 | 159.1134
Line6_7_8 | 0 | 1.3784 | 1.3784 | 0 | 1.3784 | 1.3784 | 0 | 0.31833 | 0.31833 | 0 | 0.31833 | 0.31833 | 6.6613e-17 | 0.15069 | -0.077731 | -6.6613e-17 | -0.11421 | 0.11421 | 1.3323e-16 | -0.048463 | 0.12446 | -1.3323e-16 | 0.086463 | -0.086463 | 0 | -142.8727 | 37.1273 | 0 | 37.1273 | -142.8727 | 0.9 | 0.49726 | 0.46097 | 0.9 | 0.45 | 0.45 | 1.139e-13 | -160.7007 | 159.1134 | 1.1424e-13 | -180 | 180
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6564e-31 | 1.3323e-16 | -4.6641e-23 | 2.6311e-31 | -1.3029e-16 | 2.9403e-18 | 1.3323e-16 | 1.286e-09 | -1.286e-09 | -1.3323e-16 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 1.1424e-13 | -180 | 180 | 1.1315e-13 | -180 | 180
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.57e-23 | -4.6641e-23 | -6.6613e-17 | 3.6247e-17 | 1.3617e-16 | 0 | 1.286e-09 | -1.286e-09 | -1.3365e-31 | -1.286e-09 | 1.286e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.45 | 0.45 | 0.9 | 0.45 | 0.45 | 1.1424e-13 | -180 | 180 | 1.1495e-13 | -180 | 180
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3307e-17 | -1.0135e-09 | -2.7983e-09 | -2.498e-17 | 1.0135e-09 | 2.7983e-09 | 6.6613e-17 | 2.9553e-09 | 1.362e-10 | -6.6613e-17 | -2.9553e-09 | -1.362e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.84271 | 0.7557 | 0.9 | 0.84271 | 0.7557 | 9.6002e-14 | -128.7319 | 119.553 | 9.8263e-14 | -128.7319 | 119.553

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 7.6906e-18 | 0.010966 | 0.0028847 | -6.5919e-18 | -0.010915 | -0.0028331 | 3.296e-18 | 0.0029326 | 0.010936 | -4.3946e-18 | -0.0028788 | -0.010882 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94283 | 0.93921 | 2.948e-15 | -120.3084 | 119.9432 | 3.1826e-15 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5533e-19 | -3.8309e-11 | -1.1119e-10 | -4.8066e-19 | 3.8309e-11 | 1.1119e-10 | 1.648e-18 | 1.0665e-10 | 1.9584e-11 | -1.0987e-18 | -1.0665e-10 | -1.9584e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.0611e-15 | -120.3084 | 119.9432 | 3.135e-15 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.06e-19 | -3.1925e-11 | -9.2658e-11 | 2.06e-19 | 3.1925e-11 | 9.2658e-11 | 3.296e-18 | 8.8872e-11 | 1.632e-11 | -3.8453e-18 | -8.8872e-11 | -1.632e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.135e-15 | -120.3084 | 119.9432 | 3.2054e-15 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8666e-20 | -1.9155e-11 | -5.5595e-11 | 6.8666e-20 | 1.9155e-11 | 5.5595e-11 | 5.4933e-19 | 5.3323e-11 | 9.7921e-12 | 3.8854e-36 | -5.3323e-11 | -9.7921e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.2054e-15 | -120.3084 | 119.9432 | 3.242e-15 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8066e-19 | -6.3849e-12 | -1.8532e-11 | -2.06e-19 | 6.3849e-12 | 1.8532e-11 | 1.0987e-18 | 1.7774e-11 | 3.264e-12 | -1.0987e-18 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.2054e-15 | -120.3084 | 119.9432 | 3.2043e-15 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8066e-19 | -1.277e-11 | -3.7063e-11 | 7.5533e-19 | 1.277e-11 | 3.7063e-11 | 5.4933e-19 | 3.5549e-11 | 6.5281e-12 | -1.648e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.242e-15 | -120.3084 | 119.9432 | 3.2742e-15 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0987e-18 | -6.3849e-12 | -1.8532e-11 | 1.0987e-18 | 6.3849e-12 | 1.8532e-11 | -6.2784e-35 | 1.7774e-11 | 3.264e-12 | 6.3016e-35 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 3.2742e-15 | -120.3084 | 119.9432 | 3.2863e-15 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3849e-12 | -1.8532e-11 | 2.7466e-19 | 6.3849e-12 | 1.8532e-11 | 0 | 1.7774e-11 | 3.264e-12 | 5.4933e-19 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 2.9748e-15 | -120.3084 | 119.9432 | 2.9869e-15 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3849e-12 | -1.8532e-11 | 2.7466e-19 | 6.3849e-12 | 1.8532e-11 | 0 | 1.7774e-11 | 3.264e-12 | 5.4933e-19 | -1.7774e-11 | -3.264e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 2.9748e-15 | -120.3084 | 119.9432 | 2.9869e-15 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1673e-18 | -5.1079e-11 | -1.4825e-10 | -1.1673e-18 | 5.1079e-11 | 1.4825e-10 | 2.7466e-18 | 1.422e-10 | 2.6112e-11 | -2.7466e-18 | -1.422e-10 | -2.6112e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 2.948e-15 | -120.3084 | 119.9432 | 2.9884e-15 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3733e-19 | -1.277e-11 | -3.7063e-11 | 1.3733e-19 | 1.277e-11 | 3.7063e-11 | 1.0987e-18 | 3.5549e-11 | 6.5281e-12 | -1.648e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 2.948e-15 | -120.3084 | 119.9432 | 2.9748e-15 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3733e-19 | -1.277e-11 | -3.7063e-11 | 1.3733e-19 | 1.277e-11 | 3.7063e-11 | 1.0987e-18 | 3.5549e-11 | 6.5281e-12 | -1.648e-18 | -3.5549e-11 | -6.5281e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 2.948e-15 | -120.3084 | 119.9432 | 2.9748e-15 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 6.5919e-18 | 0.010915 | 0.0028331 | -6.5919e-18 | -0.010863 | -0.0027815 | 6.5919e-18 | 0.0028788 | 0.010882 | -5.4933e-18 | -0.0028251 | -0.010828 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.94283 | 0.93921 | 0.95 | 0.93752 | 0.93379 | 3.1826e-15 | -120.5043 | 120.1275 | 3.465e-15 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 9.8879e-18 | 0.010863 | 0.0027815 | -5.4933e-18 | -0.010812 | -0.0027299 | 1.0987e-17 | 0.0028251 | 0.010828 | -1.0987e-17 | -0.0027713 | -0.010775 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93752 | 0.93379 | 0.95 | 0.93223 | 0.92837 | 3.465e-15 | -120.7024 | 120.3141 | 3.6538e-15 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.051843 | 0.051843 | 0 | 0.051843 | 0.051843 | 0 | 0.011973 | 0.011973 | 0 | 0.011973 | 0.011973 | 2.1973e-18 | 0.010812 | 0.0027299 | -2.1973e-18 | -0.01076 | -0.0026783 | 8.7893e-18 | 0.0027713 | 0.010775 | -1.0987e-17 | -0.0027175 | -0.010721 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.95 | 0.93223 | 0.92837 | 0.95 | 0.92694 | 0.92297 | 3.6538e-15 | -120.9028 | 120.5028 | 3.6705e-15 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1973e-18 | -7.7759e-11 | -9.1252e-11 | 2.1973e-18 | 7.7759e-11 | 9.1252e-11 | 1.4076e-34 | 6.2294e-11 | -3.8923e-11 | -2.1973e-18 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 3.6705e-15 | -121.1055 | 120.6937 | 3.637e-15 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-18 | -7.7759e-11 | -9.1252e-11 | 0 | 7.7759e-11 | 9.1252e-11 | -2.1973e-18 | 6.2294e-11 | -3.8923e-11 | 0 | -6.2294e-11 | 3.8923e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.92694 | 0.92297 | 0.95 | 0.92694 | 0.92297 | 3.6705e-15 | -121.1055 | 120.6937 | 3.6899e-15 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4933e-19 | -4.4694e-11 | -1.2972e-10 | -5.4933e-19 | 4.4694e-11 | 1.2972e-10 | 2.7466e-18 | 1.2442e-10 | 2.2848e-11 | -2.1973e-18 | -1.2442e-10 | -2.2848e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94815 | 0.94465 | 0.95 | 0.94815 | 0.94465 | 2.9884e-15 | -120.3084 | 119.9432 | 3.0611e-15 | -120.3084 | 119.9432

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 5.7246e-18 | 0.0098425 | 0.002589 | -5.7246e-18 | -0.0097961 | -0.0025427 | 3.1225e-18 | 0.002632 | 0.009815 | -3.1225e-18 | -0.0025837 | -0.0097667 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89321 | 0.88978 | 2.9636e-15 | -120.3084 | 119.9432 | 3.2108e-15 | -120.5043 | 120.1275
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2526e-19 | -3.4383e-11 | -9.9793e-11 | -5.8547e-19 | 3.4383e-11 | 9.9793e-11 | 3.1225e-18 | 9.5716e-11 | 1.7577e-11 | -3.6429e-18 | -9.5716e-11 | -1.7577e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 3.0768e-15 | -120.3084 | 119.9432 | 3.1507e-15 | -120.3084 | 119.9432
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5536e-19 | -2.8652e-11 | -8.3161e-11 | 4.5536e-19 | 2.8652e-11 | 8.3161e-11 | 2.6021e-18 | 7.9764e-11 | 1.4648e-11 | -2.6021e-18 | -7.9764e-11 | -1.4648e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 3.1507e-15 | -120.3084 | 119.9432 | 3.2211e-15 | -120.3084 | 119.9432
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-19 | -1.7191e-11 | -4.9896e-11 | -3.9031e-19 | 1.7191e-11 | 4.9896e-11 | 1.0408e-18 | 4.7858e-11 | 8.7885e-12 | -1.5613e-18 | -4.7858e-11 | -8.7885e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 3.2211e-15 | -120.3084 | 119.9432 | 3.2576e-15 | -120.3084 | 119.9432
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9031e-19 | -5.7305e-12 | -1.6632e-11 | 3.9031e-19 | 5.7305e-12 | 1.6632e-11 | -2.1943e-35 | 1.5953e-11 | 2.9295e-12 | -1.0408e-18 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 3.2211e-15 | -120.3084 | 119.9432 | 3.22e-15 | -120.3084 | 119.9432
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.1073e-19 | -1.1461e-11 | -3.3264e-11 | 9.1073e-19 | 1.1461e-11 | 3.3264e-11 | 1.5613e-18 | 3.1905e-11 | 5.859e-12 | -1.0408e-18 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 3.2576e-15 | -120.3084 | 119.9432 | 3.2899e-15 | -120.3084 | 119.9432
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9516e-19 | -5.7305e-12 | -1.6632e-11 | 1.9516e-19 | 5.7305e-12 | 1.6632e-11 | -1.1206e-35 | 1.5953e-11 | 2.9295e-12 | 1.1247e-35 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 3.2899e-15 | -120.3084 | 119.9432 | 3.302e-15 | -120.3084 | 119.9432
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2526e-19 | -5.7305e-12 | -1.6632e-11 | -3.2526e-19 | 5.7305e-12 | 1.6632e-11 | 5.2042e-19 | 1.5953e-11 | 2.9295e-12 | -5.2042e-19 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.9904e-15 | -120.3084 | 119.9432 | 3.0025e-15 | -120.3084 | 119.9432
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2526e-19 | -5.7305e-12 | -1.6632e-11 | -3.2526e-19 | 5.7305e-12 | 1.6632e-11 | 5.2042e-19 | 1.5953e-11 | 2.9295e-12 | -5.2042e-19 | -1.5953e-11 | -2.9295e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.9904e-15 | -120.3084 | 119.9432 | 3.0025e-15 | -120.3084 | 119.9432
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4962e-18 | -4.5844e-11 | -1.3306e-10 | -1.4962e-18 | 4.5844e-11 | 1.3306e-10 | 2.6021e-18 | 1.2762e-10 | 2.3436e-11 | -2.0817e-18 | -1.2762e-10 | -2.3436e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.9636e-15 | -120.3084 | 119.9432 | 3.0041e-15 | -120.3084 | 119.9432
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-19 | -1.1461e-11 | -3.3264e-11 | 6.5052e-19 | 1.1461e-11 | 3.3264e-11 | 1.0408e-18 | 3.1905e-11 | 5.859e-12 | -5.2042e-19 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.9636e-15 | -120.3084 | 119.9432 | 2.9904e-15 | -120.3084 | 119.9432
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-19 | -1.1461e-11 | -3.3264e-11 | 6.5052e-19 | 1.1461e-11 | 3.3264e-11 | 1.0408e-18 | 3.1905e-11 | 5.859e-12 | -5.2042e-19 | -3.1905e-11 | -5.859e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 2.9636e-15 | -120.3084 | 119.9432 | 2.9904e-15 | -120.3084 | 119.9432
Line4_2_6 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 4.1633e-18 | 0.0097961 | 0.0025427 | -4.1633e-18 | -0.0097498 | -0.0024964 | 7.2858e-18 | 0.0025837 | 0.0097667 | -7.2858e-18 | -0.0025355 | -0.0097185 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.89321 | 0.88978 | 0.9 | 0.88818 | 0.88464 | 3.2108e-15 | -120.5043 | 120.1275 | 3.5056e-15 | -120.7024 | 120.3141
Line5_6_7 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 1.0408e-17 | 0.0097498 | 0.0024964 | -1.0408e-17 | -0.0097035 | -0.0024501 | 4.1633e-18 | 0.0025355 | 0.0097185 | -4.1633e-18 | -0.0024873 | -0.0096702 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88818 | 0.88464 | 0.9 | 0.88316 | 0.87951 | 3.5056e-15 | -120.7024 | 120.3141 | 3.7072e-15 | -120.9028 | 120.5028
Line6_7_8 | 0 | 0.049114 | 0.049114 | 0 | 0.049114 | 0.049114 | 0 | 0.011342 | 0.011342 | 0 | 0.011342 | 0.011342 | 2.0817e-18 | 0.0097035 | 0.0024501 | -2.0817e-18 | -0.0096572 | -0.0024038 | 8.3267e-18 | 0.0024873 | 0.0096702 | -1.0408e-17 | -0.002439 | -0.009622 | 0 | -135.2796 | 44.7204 | 0 | 44.7204 | -135.2796 | 0.9 | 0.88316 | 0.87951 | 0.9 | 0.87816 | 0.87439 | 3.7072e-15 | -120.9028 | 120.5028 | 3.7364e-15 | -121.1055 | 120.6937
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.9789e-11 | -8.1899e-11 | -2.0817e-18 | 6.9789e-11 | 8.1899e-11 | 0 | 5.5909e-11 | -3.4934e-11 | -2.0817e-18 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 3.7364e-15 | -121.1055 | 120.6937 | 3.7029e-15 | -121.1055 | 120.6937
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.715e-34 | -6.9789e-11 | -8.1899e-11 | -4.1633e-18 | 6.9789e-11 | 8.1899e-11 | -4.1633e-18 | 5.5909e-11 | -3.4934e-11 | 2.0817e-18 | -5.5909e-11 | 3.4934e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.87816 | 0.87439 | 0.9 | 0.87816 | 0.87439 | 3.7364e-15 | -121.1055 | 120.6937 | 3.7499e-15 | -121.1055 | 120.6937
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-19 | -4.0113e-11 | -1.1643e-10 | -3.9031e-19 | 4.0113e-11 | 1.1643e-10 | 1.5613e-18 | 1.1167e-10 | 2.0507e-11 | -2.0817e-18 | -1.1167e-10 | -2.0507e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89825 | 0.89493 | 0.9 | 0.89825 | 0.89493 | 3.0041e-15 | -120.3084 | 119.9432 | 3.0768e-15 | -120.3084 | 119.9432

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.6512 | 0 | 0 | 2.6512 | 0 | 0 | 0.61227 | 0 | 0 | 0.61227 | 0 | 0 | 0.2343 | 7.0947e-08 | -7.5194e-08 | -0.17572 | -6.6304e-08 | 6.9695e-08 | 0.4686 | -3.9983e-08 | -3.793e-08 | -0.35145 | 3.4045e-08 | 3.2186e-08 | -67.2801 | 0 | 0 | 112.7199 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.64176 | 1.0086 | 1.0482 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -116.5252 | 115.448
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2648e-09 | 1.88e-08 | -2.1199e-08 | 1.6563e-09 | -1.5577e-08 | 1.7584e-08 | 2.0199e-08 | -1.26e-08 | -8.6458e-09 | -1.7054e-08 | 1.0588e-08 | 7.0213e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.054e-09 | 1.5667e-08 | -1.7666e-08 | 1.4455e-09 | -1.2444e-08 | 1.4051e-08 | 1.6833e-08 | -1.05e-08 | -7.2048e-09 | -1.3687e-08 | 8.4878e-09 | 5.5804e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3243e-10 | 9.4002e-09 | -1.0599e-08 | 1.0239e-09 | -6.1767e-09 | 6.9845e-09 | 1.01e-08 | -6.3002e-09 | -4.3229e-09 | -6.954e-09 | 4.2877e-09 | 2.6985e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1081e-10 | 3.1334e-09 | -3.5331e-09 | 6.0227e-10 | 9.0023e-11 | -8.1761e-11 | 3.3665e-09 | -2.1001e-09 | -1.441e-09 | -2.2092e-10 | 8.749e-11 | -1.8348e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.2162e-10 | 6.2668e-09 | -7.0662e-09 | 8.1308e-10 | -3.0434e-09 | 3.4513e-09 | 6.733e-09 | -4.2002e-09 | -2.8819e-09 | -3.5874e-09 | 2.1876e-09 | 1.2575e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1081e-10 | 3.1334e-09 | -3.5331e-09 | 6.0227e-10 | 9.0024e-11 | -8.1762e-11 | 3.3665e-09 | -2.1001e-09 | -1.441e-09 | -2.2092e-10 | 8.749e-11 | -1.8348e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4333e-10 | 3.2262e-09 | -3.5297e-09 | 5.6107e-10 | 3.2862e-11 | -1.4707e-10 | 3.4468e-09 | -2.127e-09 | -1.4224e-09 | -2.4487e-10 | 6.3535e-11 | -2.0743e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87165 | 1.0413 | 1.0857 | 0.87165 | 1.0413 | 1.0857 | -4.1845 | -119.0919 | 117.1554 | -4.1845 | -119.0919 | 117.1554
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1081e-10 | 3.1334e-09 | -3.5331e-09 | 6.0227e-10 | 9.0024e-11 | -8.1761e-11 | 3.3665e-09 | -2.1001e-09 | -1.441e-09 | -2.2092e-10 | 8.749e-11 | -1.8348e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6865e-09 | 2.5067e-08 | -2.8265e-08 | 2.0779e-09 | -2.1844e-08 | 2.465e-08 | 2.6932e-08 | -1.6801e-08 | -1.1528e-08 | -2.3787e-08 | 1.4788e-08 | 9.9033e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468
Line2_1_4 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0051373 | -0.0025177 | -0.0054673 | 0.0054373 | 0.0028177 | 0.0057673 | -0.033839 | -0.040955 | -0.042441 | 0.034439 | 0.041555 | 0.043041 | 94.7873 | -25.2128 | -145.2128 | -85.2127 | 154.7872 | 34.7872 | 0.85568 | 1.0258 | 1.0698 | 0.87165 | 1.0413 | 1.0857 | -3.8451 | -118.7306 | 117.4468 | -4.1845 | -119.0919 | 117.1554
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.2162e-10 | 6.2668e-09 | -7.0662e-09 | 8.1308e-10 | -3.0434e-09 | 3.4513e-09 | 6.733e-09 | -4.2002e-09 | -2.8819e-09 | -3.5874e-09 | 2.1876e-09 | 1.2575e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468
Line4_2_6 | 2.6512 | 0 | 0 | 2.6512 | 0 | 0 | 0.61227 | 0 | 0 | 0.61227 | 0 | 0 | 0.17572 | 6.645e-08 | -6.9701e-08 | -0.11715 | -5.8421e-08 | 6.0975e-08 | 0.35145 | -3.381e-08 | -3.2506e-08 | -0.2343 | 2.7097e-08 | 2.5539e-08 | -67.2801 | 0 | 0 | 112.7199 | 0 | 0 | 0.64176 | 1.0086 | 1.0482 | 0.42784 | 0.99284 | 1.028 | -3.8451 | -116.5252 | 115.448 | -3.8451 | -114.2465 | 113.3678
Line5_6_7 | 2.6512 | 0 | 0 | 2.6512 | 0 | 0 | 0.61227 | 0 | 0 | 0.61227 | 0 | 0 | 0.11715 | 5.861e-08 | -6.0919e-08 | -0.058575 | -4.7188e-08 | 4.8974e-08 | 0.2343 | -2.6714e-08 | -2.5996e-08 | -0.11715 | 1.9687e-08 | 1.8265e-08 | -67.28 | 0 | 0 | 112.72 | 0 | 0 | 0.42784 | 0.99284 | 1.028 | 0.21392 | 0.97875 | 1.0091 | -3.8451 | -114.2465 | 113.3678 | -3.8451 | -111.8984 | 111.207
Line6_7_8 | 2.6512 | 0 | 0 | 2.6512 | 0 | 0 | 0.61227 | 0 | 0 | 0.61227 | 0 | 0 | 0.058575 | 4.7406e-08 | -4.8868e-08 | 7.4987e-17 | -3.2585e-08 | 3.371e-08 | 0.11715 | -1.9156e-08 | -1.8859e-08 | 4.448e-14 | 1.2274e-08 | 1.0824e-08 | -67.28 | 0 | 0 | 112.72 | 0 | 0 | 0.21392 | 0.97875 | 1.0091 | 0 | 0.96634 | 0.99176 | -3.8451 | -111.8984 | 111.207 | 0 | -109.4859 | 108.9672
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1167e-22 | 1.6409e-08 | -1.6784e-08 | -3.8916e-18 | 2.3395e-10 | 1.4123e-10 | -1.0787e-21 | -5.7976e-09 | -5.7775e-09 | 8.5217e-18 | 6.789e-10 | -7.307e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96634 | 0.99176 | 0 | 0.96634 | 0.99176 | 0 | -109.4859 | 108.9672 | 0 | -109.4859 | 108.9672
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1167e-22 | 1.6409e-08 | -1.6784e-08 | -3.8916e-18 | 2.3395e-10 | 1.4123e-10 | -1.0787e-21 | -5.7976e-09 | -5.7775e-09 | 8.5217e-18 | 6.789e-10 | -7.307e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96634 | 0.99176 | 0 | 0.96634 | 0.99176 | 0 | -109.4859 | 108.9672 | 0 | -109.4859 | 108.9672
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4757e-09 | 2.1934e-08 | -2.4732e-08 | 1.8671e-09 | -1.871e-08 | 2.1117e-08 | 2.3566e-08 | -1.4701e-08 | -1.0087e-08 | -2.042e-08 | 1.2688e-08 | 8.4623e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85568 | 1.0258 | 1.0698 | 0.85568 | 1.0258 | 1.0698 | -3.8451 | -118.7306 | 117.4468 | -3.8451 | -118.7306 | 117.4468

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.7514 | 0 | 0 | 2.7514 | 0 | 0 | 0.6354 | 0 | 0 | 0.6354 | 0 | 0 | 0.25233 | 7.813e-08 | -8.283e-08 | -0.18925 | -7.2917e-08 | 7.6662e-08 | 0.50467 | -4.3788e-08 | -4.1757e-08 | -0.3785 | 3.7244e-08 | 3.5417e-08 | -67.4243 | 0 | 0 | 112.5757 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.666 | 1.0553 | 1.0983 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -116.4851 | 115.3731
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4395e-09 | 2.1416e-08 | -2.4153e-08 | 1.8812e-09 | -1.7742e-08 | 2.0038e-08 | 2.2789e-08 | -1.4257e-08 | -9.8693e-09 | -1.924e-08 | 1.1981e-08 | 8.0155e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1996e-09 | 1.7846e-08 | -2.0128e-08 | 1.6413e-09 | -1.4172e-08 | 1.6012e-08 | 1.8991e-08 | -1.1881e-08 | -8.2244e-09 | -1.5442e-08 | 9.6049e-09 | 6.3706e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1976e-10 | 1.0708e-08 | -1.2077e-08 | 1.1614e-09 | -7.0339e-09 | 7.961e-09 | 1.1395e-08 | -7.1287e-09 | -4.9346e-09 | -7.8457e-09 | 4.8525e-09 | 3.0809e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3992e-10 | 3.5693e-09 | -4.0255e-09 | 6.8159e-10 | 1.0468e-10 | -9.0097e-11 | 3.7982e-09 | -2.3762e-09 | -1.6449e-09 | -2.4918e-10 | 1.0002e-10 | -2.0886e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7984e-10 | 7.1386e-09 | -8.0511e-09 | 9.2151e-10 | -3.4646e-09 | 3.9354e-09 | 7.5965e-09 | -4.7524e-09 | -3.2898e-09 | -4.0474e-09 | 2.4762e-09 | 1.436e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3992e-10 | 3.5693e-09 | -4.0255e-09 | 6.8159e-10 | 1.0468e-10 | -9.0097e-11 | 3.7982e-09 | -2.3762e-09 | -1.6449e-09 | -2.4918e-10 | 1.0002e-10 | -2.0886e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6929e-10 | 3.6677e-09 | -4.0244e-09 | 6.3938e-10 | 4.5076e-11 | -1.5854e-10 | 3.8846e-09 | -2.4064e-09 | -1.6258e-09 | -2.7427e-10 | 7.4923e-11 | -2.3395e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90398 | 1.0885 | 1.1366 | 0.90398 | 1.0885 | 1.1366 | -4.3141 | -119.0222 | 117.0747 | -4.3141 | -119.0222 | 117.0747
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3992e-10 | 3.5693e-09 | -4.0255e-09 | 6.8159e-10 | 1.0468e-10 | -9.0097e-11 | 3.7982e-09 | -2.3762e-09 | -1.6449e-09 | -2.4918e-10 | 1.0002e-10 | -2.0886e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9194e-09 | 2.8554e-08 | -3.2204e-08 | 2.361e-09 | -2.488e-08 | 2.8089e-08 | 3.0386e-08 | -1.901e-08 | -1.3159e-08 | -2.6837e-08 | 1.6734e-08 | 1.1305e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518
Line2_1_4 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0054196 | -0.0025926 | -0.0058012 | 0.0057196 | 0.0028926 | 0.0061012 | -0.035104 | -0.042846 | -0.044453 | 0.035704 | 0.043446 | 0.045053 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 0.888 | 1.0731 | 1.1207 | 0.90398 | 1.0885 | 1.1366 | -3.9894 | -118.6758 | 117.3518 | -4.3141 | -119.0222 | 117.0747
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7984e-10 | 7.1386e-09 | -8.0511e-09 | 9.2151e-10 | -3.4646e-09 | 3.9354e-09 | 7.5965e-09 | -4.7524e-09 | -3.2897e-09 | -4.0474e-09 | 2.4762e-09 | 1.436e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518
Line4_2_6 | 2.7514 | 0 | 0 | 2.7514 | 0 | 0 | 0.6354 | 0 | 0 | 0.6354 | 0 | 0 | 0.18925 | 7.3082e-08 | -7.667e-08 | -0.12617 | -6.4185e-08 | 6.6998e-08 | 0.3785 | -3.6983e-08 | -3.5774e-08 | -0.25233 | 2.9621e-08 | 2.8108e-08 | -67.4243 | 0 | 0 | 112.5757 | 0 | 0 | 0.666 | 1.0553 | 1.0983 | 0.444 | 1.0392 | 1.0772 | -3.9894 | -116.4851 | 115.3731 | -3.9894 | -114.2227 | 113.3145
Line5_6_7 | 2.7514 | 0 | 0 | 2.7514 | 0 | 0 | 0.6354 | 0 | 0 | 0.6354 | 0 | 0 | 0.12617 | 6.4395e-08 | -6.6938e-08 | -0.063084 | -5.1807e-08 | 5.3769e-08 | 0.25233 | -2.9199e-08 | -2.8614e-08 | -0.12617 | 2.1513e-08 | 2.0117e-08 | -67.4243 | 0 | 0 | 112.5757 | 0 | 0 | 0.444 | 1.0392 | 1.0772 | 0.222 | 1.0246 | 1.0576 | -3.9894 | -114.2227 | 113.3145 | -3.9894 | -111.8925 | 111.1767
Line6_7_8 | 2.7514 | 0 | 0 | 2.7514 | 0 | 0 | 0.6354 | 0 | 0 | 0.6354 | 0 | 0 | 0.063084 | 5.2049e-08 | -5.3655e-08 | 4.2275e-14 | -3.5763e-08 | 3.6998e-08 | 0.12617 | -2.093e-08 | -2.0772e-08 | -4.5385e-14 | 1.3416e-08 | 1.1941e-08 | -67.4243 | 0 | 0 | 112.5757 | 0 | 0 | 0.222 | 1.0246 | 1.0576 | 0 | 1.0119 | 1.0395 | -3.9894 | -111.8925 | 111.1767 | 0 | -109.4994 | 108.9611
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8722e-21 | 1.8011e-08 | -1.8422e-08 | -4.2674e-18 | 2.5861e-10 | 1.5302e-10 | 3.3136e-22 | -6.3361e-09 | -6.372e-09 | 9.3653e-18 | 7.4379e-10 | -8.0279e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0119 | 1.0395 | 0 | 1.0119 | 1.0395 | 0 | -109.4994 | 108.9611 | 0 | -109.4994 | 108.9611
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8722e-21 | 1.8011e-08 | -1.8422e-08 | -4.2674e-18 | 2.5861e-10 | 1.5302e-10 | 3.3136e-22 | -6.3361e-09 | -6.372e-09 | 9.3653e-18 | 7.4379e-10 | -8.0279e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0119 | 1.0395 | 0 | 1.0119 | 1.0395 | 0 | -109.4994 | 108.9611 | 0 | -109.4994 | 108.9611
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6794e-09 | 2.4985e-08 | -2.8179e-08 | 2.1211e-09 | -2.1311e-08 | 2.4063e-08 | 2.6588e-08 | -1.6634e-08 | -1.1514e-08 | -2.3039e-08 | 1.4357e-08 | 9.6604e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.888 | 1.0731 | 1.1207 | 0.888 | 1.0731 | 1.1207 | -3.9894 | -118.6758 | 117.3518 | -3.9894 | -118.6758 | 117.3518

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.034444 | 0 | 0 | 0.034444 | 0 | 0 | 0.0079544 | 0 | 0 | 0.0079544 | 0 | 0 | 0.0059714 | 1.0723e-09 | -6.7786e-10 | -0.0059615 | -1.0263e-09 | 6.0232e-10 | 0.0060109 | -8.729e-10 | -1.3683e-10 | -0.0059912 | 8.1154e-10 | 1.2719e-10 | -45.2822 | 0 | 0 | 134.7178 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0625 | 1.0664 | 1.0676 | -0.093122 | -119.9963 | 119.9695 | -0.14004 | -119.9763 | 119.9403
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.872e-10 | 5.7111e-10 | 1.0879e-10 | -4.6526e-10 | -5.4183e-10 | -1.6001e-10 | 3.1798e-10 | -2.5472e-10 | -1.2269e-11 | -2.7165e-10 | 2.1253e-10 | 8.0379e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.06e-10 | 4.7592e-10 | 9.0661e-11 | -3.8406e-10 | -4.4665e-10 | -1.4187e-10 | 2.6499e-10 | -2.1226e-10 | -1.0224e-11 | -2.1865e-10 | 1.7008e-10 | 5.9931e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.436e-10 | 2.8555e-10 | 5.4397e-11 | -2.2166e-10 | -2.5628e-10 | -1.0561e-10 | 1.5899e-10 | -1.2736e-10 | -6.1345e-12 | -1.1266e-10 | 8.5174e-11 | 1.9034e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.12e-11 | 9.5184e-11 | 1.8132e-11 | -5.9259e-11 | -6.5913e-11 | -6.9344e-11 | 5.2997e-11 | -4.2453e-11 | -2.0449e-12 | -6.6651e-12 | 2.6871e-13 | -2.1862e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.624e-10 | 1.9037e-10 | 3.6264e-11 | -1.4046e-10 | -1.611e-10 | -8.7476e-11 | 1.0599e-10 | -8.4905e-11 | -4.0897e-12 | -5.9662e-11 | 4.2721e-11 | -1.4143e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.12e-11 | 9.5184e-11 | 1.8132e-11 | -5.9259e-11 | -6.5913e-11 | -6.9344e-11 | 5.2997e-11 | -4.2453e-11 | -2.0448e-12 | -6.6651e-12 | 2.6873e-13 | -2.1863e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4459e-10 | 1.5828e-10 | 8.0399e-11 | -1.2206e-10 | -1.2882e-10 | -1.3238e-10 | 7.7502e-11 | -1.9284e-11 | 2.2146e-11 | -3.062e-11 | -2.3686e-11 | -2.6141e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0808 | 1.0824 | 1.0833 | 1.0808 | 1.0824 | 1.0833 | -0.42163 | -120.3257 | 119.6409 | -0.42163 | -120.3257 | 119.6409
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.12e-11 | 9.5184e-11 | 1.8132e-11 | -5.9259e-11 | -6.5913e-11 | -6.9344e-11 | 5.2997e-11 | -4.2453e-11 | -2.0448e-12 | -6.6651e-12 | 2.6875e-13 | -2.1863e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.496e-10 | 7.6147e-10 | 1.4506e-10 | -6.2766e-10 | -7.322e-10 | -1.9627e-10 | 4.2398e-10 | -3.3962e-10 | -1.6359e-11 | -3.7764e-10 | 2.9744e-10 | 1.2128e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695
Line2_1_4 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036248 | -0.0035586 | -0.0035869 | 0.0039248 | 0.0038586 | 0.0038869 | -0.042452 | -0.042525 | -0.042558 | 0.043052 | 0.043125 | 0.043158 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.0652 | 1.0668 | 1.0677 | 1.0808 | 1.0824 | 1.0833 | -0.093122 | -119.9963 | 119.9695 | -0.42163 | -120.3257 | 119.6409
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.624e-10 | 1.9037e-10 | 3.6264e-11 | -1.4046e-10 | -1.611e-10 | -8.7477e-11 | 1.0599e-10 | -8.4905e-11 | -4.0897e-12 | -5.9662e-11 | 4.2721e-11 | -1.4144e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695
Line4_2_6 | 0.034444 | 0 | 0 | 0.034444 | 0 | 0 | 0.0079544 | 0 | 0 | 0.0079544 | 0 | 0 | 0.0059615 | 9.6205e-10 | -6.7121e-10 | -0.0059516 | -8.8296e-10 | 5.4701e-10 | 0.0059912 | -8.0984e-10 | -1.3147e-10 | -0.0059714 | 7.1164e-10 | 1.1174e-10 | -45.2822 | 0 | 0 | 134.7178 | 0 | 0 | 1.0625 | 1.0664 | 1.0676 | 1.0599 | 1.066 | 1.0675 | -0.14004 | -119.9763 | 119.9403 | -0.1872 | -119.9564 | 119.9111
Line5_6_7 | 0.034444 | 0 | 0 | 0.034444 | 0 | 0 | 0.0079544 | 0 | 0 | 0.0079544 | 0 | 0 | 0.0059516 | 8.2033e-10 | -6.1545e-10 | -0.0059417 | -7.0812e-10 | 4.4258e-10 | 0.0059714 | -7.0851e-10 | -1.1812e-10 | -0.0059516 | 5.7353e-10 | 8.8381e-11 | -45.2822 | 0 | 0 | 134.7178 | 0 | 0 | 1.0599 | 1.066 | 1.0675 | 1.0573 | 1.0656 | 1.0674 | -0.1872 | -119.9564 | 119.9111 | -0.23459 | -119.9364 | 119.8819
Line6_7_8 | 0.034444 | 0 | 0 | 0.034444 | 0 | 0 | 0.0079544 | 0 | 0 | 0.0079544 | 0 | 0 | 0.0059417 | 6.4713e-10 | -5.1058e-10 | -0.0059319 | -5.0178e-10 | 2.8905e-10 | 0.0059516 | -5.6898e-10 | -9.6851e-11 | -0.0059319 | 3.973e-10 | 5.7182e-11 | -45.2822 | 0 | 0 | 134.7178 | 0 | 0 | 1.0573 | 1.0656 | 1.0674 | 1.0546 | 1.0652 | 1.0673 | -0.23459 | -119.9364 | 119.8819 | -0.28222 | -119.9165 | 119.8527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.019e-10 | 2.2122e-10 | -1.783e-10 | -1.7912e-11 | -5.935e-11 | -6.7555e-11 | 2.5215e-10 | -1.9566e-10 | -3.3873e-11 | -1.9999e-11 | 5.9794e-12 | -1.0564e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0546 | 1.0652 | 1.0673 | 1.0546 | 1.0652 | 1.0673 | -0.28222 | -119.9165 | 119.8527 | -0.28222 | -119.9165 | 119.8527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.019e-10 | 2.2122e-10 | -1.783e-10 | -1.7912e-11 | -5.935e-11 | -6.7555e-11 | 2.5215e-10 | -1.9566e-10 | -3.3873e-11 | -1.9999e-11 | 5.9794e-12 | -1.0564e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0546 | 1.0652 | 1.0673 | 1.0546 | 1.0652 | 1.0673 | -0.28222 | -119.9165 | 119.8527 | -0.28222 | -119.9165 | 119.8527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.684e-10 | 6.6629e-10 | 1.2693e-10 | -5.4646e-10 | -6.3702e-10 | -1.7814e-10 | 3.7098e-10 | -2.9717e-10 | -1.4314e-11 | -3.2465e-10 | 2.5498e-10 | 1.0083e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0652 | 1.0668 | 1.0677 | 1.0652 | 1.0668 | 1.0677 | -0.093122 | -119.9963 | 119.9695 | -0.093122 | -119.9963 | 119.9695

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.03608 | 0 | 0 | 0.03608 | 0 | 0 | 0.0083323 | 0 | 0 | 0.0083323 | 0 | 0 | 0.0065522 | 1.1851e-09 | -7.5974e-10 | -0.0065414 | -1.1331e-09 | 6.7416e-10 | 0.0065956 | -9.7113e-10 | -1.5087e-10 | -0.0065739 | 9.0159e-10 | 1.4006e-10 | -45.2866 | 0 | 0 | 134.7134 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.113 | 1.1172 | 1.1184 | -0.097518 | -119.9961 | 119.9681 | -0.14444 | -119.9762 | 119.9389
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3857e-10 | 6.3505e-10 | 1.0353e-10 | -5.1335e-10 | -6.014e-10 | -1.624e-10 | 3.6551e-10 | -2.928e-10 | -1.4133e-11 | -3.1226e-10 | 2.4431e-10 | 9.266e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4881e-10 | 5.2921e-10 | 8.6274e-11 | -4.2359e-10 | -4.9556e-10 | -1.4515e-10 | 3.046e-10 | -2.44e-10 | -1.1778e-11 | -2.5134e-10 | 1.9551e-10 | 6.9105e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6928e-10 | 3.1753e-10 | 5.1764e-11 | -2.4406e-10 | -2.8387e-10 | -1.1064e-10 | 1.8276e-10 | -1.464e-10 | -7.0667e-12 | -1.295e-10 | 9.791e-11 | 2.1994e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9762e-11 | 1.0584e-10 | 1.7255e-11 | -6.4541e-11 | -7.2187e-11 | -7.613e-11 | 6.0919e-11 | -4.8801e-11 | -2.3556e-12 | -7.6595e-12 | 3.0851e-13 | -2.5118e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7952e-10 | 2.1168e-10 | 3.4509e-11 | -1.543e-10 | -1.7803e-10 | -9.3385e-11 | 1.2184e-10 | -9.7601e-11 | -4.7111e-12 | -6.8579e-11 | 4.9109e-11 | -1.5619e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9762e-11 | 1.0584e-10 | 1.7255e-11 | -6.4541e-11 | -7.2187e-11 | -7.6131e-11 | 6.0919e-11 | -4.8801e-11 | -2.3556e-12 | -7.6595e-12 | 3.0853e-13 | -2.5118e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5614e-10 | 1.7189e-10 | 8.2401e-11 | -1.3027e-10 | -1.3804e-10 | -1.4212e-10 | 8.6619e-11 | -2.4568e-11 | 2.2999e-11 | -3.2755e-11 | -2.4787e-11 | -2.7608e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1314 | 1.1332 | 1.1342 | 1.1314 | 1.1332 | 1.1342 | -0.41128 | -120.3107 | 119.6542 | -0.41128 | -120.3107 | 119.6542
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9762e-11 | 1.0584e-10 | 1.7255e-11 | -6.4541e-11 | -7.2187e-11 | -7.6131e-11 | 6.0919e-11 | -4.8801e-11 | -2.3556e-12 | -7.6595e-12 | 3.0852e-13 | -2.5118e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1809e-10 | 8.4674e-10 | 1.3804e-10 | -6.9287e-10 | -8.1308e-10 | -1.9691e-10 | 4.8735e-10 | -3.9041e-10 | -1.8844e-11 | -4.3409e-10 | 3.4191e-10 | 1.3977e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681
Line2_1_4 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0038002 | -0.0037276 | -0.0037586 | 0.0041002 | 0.0040276 | 0.0040586 | -0.044469 | -0.044549 | -0.044584 | 0.045069 | 0.045149 | 0.045184 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1158 | 1.1176 | 1.1186 | 1.1314 | 1.1332 | 1.1342 | -0.097518 | -119.9961 | 119.9681 | -0.41128 | -120.3107 | 119.6542
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7952e-10 | 2.1168e-10 | 3.451e-11 | -1.543e-10 | -1.7803e-10 | -9.3385e-11 | 1.2184e-10 | -9.7601e-11 | -4.7111e-12 | -6.8579e-11 | 4.9109e-11 | -1.5618e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681
Line4_2_6 | 0.03608 | 0 | 0 | 0.03608 | 0 | 0 | 0.0083323 | 0 | 0 | 0.0083323 | 0 | 0 | 0.0065414 | 1.0627e-09 | -7.498e-10 | -0.0065305 | -9.7439e-10 | 6.1082e-10 | 0.0065739 | -8.9971e-10 | -1.4487e-10 | -0.0065522 | 7.8974e-10 | 1.2299e-10 | -45.2866 | 0 | 0 | 134.7134 | 0 | 0 | 1.113 | 1.1172 | 1.1184 | 1.1102 | 1.1167 | 1.1183 | -0.14444 | -119.9762 | 119.9389 | -0.19159 | -119.9562 | 119.9097
Line5_6_7 | 0.03608 | 0 | 0 | 0.03608 | 0 | 0 | 0.0083323 | 0 | 0 | 0.0083323 | 0 | 0 | 0.0065305 | 9.0581e-10 | -6.8596e-10 | -0.0065197 | -7.8113e-10 | 4.9358e-10 | 0.0065522 | -7.863e-10 | -1.301e-10 | -0.0065305 | 6.3598e-10 | 9.7231e-11 | -45.2866 | 0 | 0 | 134.7134 | 0 | 0 | 1.1102 | 1.1167 | 1.1183 | 1.1075 | 1.1163 | 1.1182 | -0.19159 | -119.9562 | 119.9097 | -0.23898 | -119.9363 | 119.8805
Line6_7_8 | 0.03608 | 0 | 0 | 0.03608 | 0 | 0 | 0.0083323 | 0 | 0 | 0.0083323 | 0 | 0 | 0.0065197 | 7.1434e-10 | -5.6823e-10 | -0.0065088 | -5.533e-10 | 3.2245e-10 | 0.0065305 | -6.3097e-10 | -1.0664e-10 | -0.0065088 | 4.4039e-10 | 6.2874e-11 | -45.2866 | 0 | 0 | 134.7134 | 0 | 0 | 1.1075 | 1.1163 | 1.1182 | 1.1047 | 1.1159 | 1.1181 | -0.23898 | -119.9363 | 119.8805 | -0.28661 | -119.9163 | 119.8513
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1248e-10 | 2.4416e-10 | -1.9831e-10 | -1.9178e-11 | -6.4987e-11 | -7.4166e-11 | 2.7942e-10 | -2.1691e-10 | -3.7289e-11 | -2.2289e-11 | 6.5759e-12 | -1.1705e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1047 | 1.1159 | 1.1181 | 1.1047 | 1.1159 | 1.1181 | -0.28661 | -119.9163 | 119.8513 | -0.28661 | -119.9163 | 119.8513
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1248e-10 | 2.4416e-10 | -1.9831e-10 | -1.9178e-11 | -6.4987e-11 | -7.4166e-11 | 2.7942e-10 | -2.1691e-10 | -3.7289e-11 | -2.2289e-11 | 6.5759e-12 | -1.1705e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1047 | 1.1159 | 1.1181 | 1.1047 | 1.1159 | 1.1181 | -0.28661 | -119.9163 | 119.8513 | -0.28661 | -119.9163 | 119.8513
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2833e-10 | 7.409e-10 | 1.2078e-10 | -6.0311e-10 | -7.0724e-10 | -1.7966e-10 | 4.2643e-10 | -3.416e-10 | -1.6489e-11 | -3.7317e-10 | 2.9311e-10 | 1.1622e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1158 | 1.1176 | 1.1186 | 1.1158 | 1.1176 | 1.1186 | -0.097518 | -119.9961 | 119.9681 | -0.097518 | -119.9961 | 119.9681

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.0086 | 0 | 0 | 2.0086 | 0 | 0 | 0.46386 | 0 | 0 | 0.46386 | 0 | 0 | 0.25819 | 5.4303e-08 | -6.0644e-08 | -0.19365 | -5.1463e-08 | 5.6174e-08 | 0.26895 | -3.3624e-08 | -2.8969e-08 | -0.20171 | 2.8447e-08 | 2.4987e-08 | -52.3774 | 0 | 0 | 127.6226 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.60282 | 0.89844 | 0.93937 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -117.0911 | 115.8212
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3098e-09 | 1.004e-08 | -1.6317e-08 | -2.3436e-09 | -8.2451e-09 | 1.3555e-08 | 1.4621e-08 | -1.1981e-08 | -2.0797e-09 | -1.2487e-08 | 1.0015e-08 | 1.6076e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7582e-09 | 8.3671e-09 | -1.3597e-08 | -1.792e-09 | -6.5717e-09 | 1.0836e-08 | 1.2184e-08 | -9.984e-09 | -1.7331e-09 | -1.005e-08 | 8.018e-09 | 1.261e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6549e-09 | 5.0202e-09 | -8.1584e-09 | -6.887e-10 | -3.2248e-09 | 5.3968e-09 | 7.3103e-09 | -5.9904e-09 | -1.0398e-09 | -5.1763e-09 | 4.0243e-09 | 5.6774e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5164e-10 | 1.6734e-09 | -2.7195e-09 | 4.1458e-10 | 1.2199e-10 | -4.214e-11 | 2.4368e-09 | -1.9968e-09 | -3.4661e-10 | -3.0277e-10 | 3.0727e-11 | -1.2548e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1033e-09 | 3.3468e-09 | -5.4389e-09 | -1.3706e-10 | -1.5514e-09 | 2.6773e-09 | 4.8735e-09 | -3.9936e-09 | -6.9323e-10 | -2.7395e-09 | 2.0275e-09 | 2.2113e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5164e-10 | 1.6734e-09 | -2.7195e-09 | 4.1458e-10 | 1.2199e-10 | -4.214e-11 | 2.4368e-09 | -1.9968e-09 | -3.4661e-10 | -3.0277e-10 | 3.0727e-11 | -1.2548e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5164e-10 | 1.6734e-09 | -2.7195e-09 | 4.1458e-10 | 1.2199e-10 | -4.214e-11 | 2.4368e-09 | -1.9968e-09 | -3.4661e-10 | -3.0277e-10 | 3.0727e-11 | -1.2548e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5164e-10 | 1.6734e-09 | -2.7195e-09 | 4.1458e-10 | 1.2199e-10 | -4.214e-11 | 2.4368e-09 | -1.9968e-09 | -3.4661e-10 | -3.0277e-10 | 3.0727e-11 | -1.2548e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4131e-09 | 1.3387e-08 | -2.1756e-08 | -3.4469e-09 | -1.1592e-08 | 1.8994e-08 | 1.9494e-08 | -1.5974e-08 | -2.7729e-09 | -1.736e-08 | 1.4008e-08 | 2.3008e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1033e-09 | 3.3468e-09 | -5.4389e-09 | -1.3706e-10 | -1.5514e-09 | 2.6773e-09 | 4.8735e-09 | -3.9936e-09 | -6.9322e-10 | -2.7395e-09 | 2.0275e-09 | 2.2113e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1033e-09 | 3.3468e-09 | -5.4389e-09 | -1.3706e-10 | -1.5514e-09 | 2.6773e-09 | 4.8735e-09 | -3.9936e-09 | -6.9322e-10 | -2.7395e-09 | 2.0275e-09 | 2.2113e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line4_2_6 | 2.0086 | 0 | 0 | 2.0086 | 0 | 0 | 0.46386 | 0 | 0 | 0.46386 | 0 | 0 | 0.19365 | 5.1628e-08 | -5.6146e-08 | -0.1291 | -4.5856e-08 | 4.91e-08 | 0.20171 | -2.8288e-08 | -2.5225e-08 | -0.13448 | 2.2512e-08 | 2.0045e-08 | -52.3774 | 0 | 0 | 127.6226 | 0 | 0 | 0.60282 | 0.89844 | 0.93937 | 0.40188 | 0.88491 | 0.91869 | -6.2082 | -117.0911 | 115.8212 | -6.2082 | -114.6593 | 113.6959
Line5_6_7 | 2.0086 | 0 | 0 | 2.0086 | 0 | 0 | 0.46386 | 0 | 0 | 0.46386 | 0 | 0 | 0.1291 | 4.6054e-08 | -4.9014e-08 | -0.064549 | -3.7344e-08 | 3.9399e-08 | 0.13448 | -2.2225e-08 | -2.0396e-08 | -0.067238 | 1.6257e-08 | 1.4424e-08 | -52.3774 | 0 | 0 | 127.6226 | 0 | 0 | 0.40188 | 0.88491 | 0.91869 | 0.20094 | 0.87303 | 0.89933 | -6.2082 | -114.6593 | 113.6959 | -6.2082 | -112.1566 | 111.4758
Line6_7_8 | 2.0086 | 0 | 0 | 2.0086 | 0 | 0 | 0.46386 | 0 | 0 | 0.46386 | 0 | 0 | 0.064549 | 3.7562e-08 | -3.9266e-08 | -1.9509e-14 | -2.5908e-08 | 2.7087e-08 | 0.067238 | -1.5842e-08 | -1.4888e-08 | 4.3125e-14 | 1.0086e-08 | 8.53e-09 | -52.3774 | 0 | 0 | 127.6226 | 0 | 0 | 0.20094 | 0.87303 | 0.89933 | 0 | 0.86285 | 0.88138 | -6.2082 | -112.1566 | 111.4758 | 0 | -109.5898 | 109.1618
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6486e-21 | 1.3067e-08 | -1.346e-08 | -1.1957e-18 | 2.2625e-10 | 1.6701e-10 | -4.1181e-22 | -4.7717e-09 | -4.5537e-09 | 9.3474e-18 | 5.4309e-10 | -5.7729e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86285 | 0.88138 | 0 | 0.86285 | 0.88138 | 0 | -109.5898 | 109.1618 | 0 | -109.5898 | 109.1618
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6486e-21 | 1.3067e-08 | -1.346e-08 | -1.1957e-18 | 2.2625e-10 | 1.6701e-10 | -4.1181e-22 | -4.7717e-09 | -4.5537e-09 | 9.3474e-18 | 5.4309e-10 | -5.7729e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86285 | 0.88138 | 0 | 0.86285 | 0.88138 | 0 | -109.5898 | 109.1618 | 0 | -109.5898 | 109.1618
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8614e-09 | 1.1714e-08 | -1.9036e-08 | -2.8952e-09 | -9.9185e-09 | 1.6275e-08 | 1.7057e-08 | -1.3978e-08 | -2.4263e-09 | -1.4923e-08 | 1.2012e-08 | 1.9542e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80376 | 0.91354 | 0.96129 | 0.80376 | 0.91354 | 0.96129 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.9028 | 0 | 0 | 1.9028 | 0 | 0 | 0.43944 | 0 | 0 | 0.43944 | 0 | 0 | 0.23173 | 4.8737e-08 | -5.4429e-08 | -0.1738 | -4.6188e-08 | 5.0416e-08 | 0.24139 | -3.0178e-08 | -2.6e-08 | -0.18104 | 2.5531e-08 | 2.2426e-08 | -52.3774 | 0 | 0 | 127.6226 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.57109 | 0.85115 | 0.88993 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -117.0911 | 115.8212
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9706e-09 | 9.0114e-09 | -1.4644e-08 | -2.1034e-09 | -7.4e-09 | 1.2166e-08 | 1.3122e-08 | -1.0753e-08 | -1.8665e-09 | -1.1207e-08 | 8.9883e-09 | 1.4428e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4755e-09 | 7.5095e-09 | -1.2204e-08 | -1.6083e-09 | -5.8981e-09 | 9.7251e-09 | 1.0935e-08 | -8.9607e-09 | -1.5554e-09 | -9.0198e-09 | 7.1962e-09 | 1.1317e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4853e-09 | 4.5057e-09 | -7.3222e-09 | -6.1811e-10 | -2.8943e-09 | 4.8437e-09 | 6.5611e-09 | -5.3764e-09 | -9.3326e-10 | -4.6458e-09 | 3.6119e-09 | 5.0955e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.951e-10 | 1.5019e-09 | -2.4407e-09 | 3.7208e-10 | 1.0948e-10 | -3.7821e-11 | 2.187e-09 | -1.7921e-09 | -3.1109e-10 | -2.7174e-10 | 2.7578e-11 | -1.1262e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9019e-10 | 3.0038e-09 | -4.8815e-09 | -1.2301e-10 | -1.3924e-09 | 2.4029e-09 | 4.374e-09 | -3.5843e-09 | -6.2218e-10 | -2.4588e-09 | 1.8197e-09 | 1.9846e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.951e-10 | 1.5019e-09 | -2.4407e-09 | 3.7208e-10 | 1.0948e-10 | -3.7821e-11 | 2.187e-09 | -1.7921e-09 | -3.1109e-10 | -2.7174e-10 | 2.7578e-11 | -1.1262e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.951e-10 | 1.5019e-09 | -2.4407e-09 | 3.7208e-10 | 1.0948e-10 | -3.7821e-11 | 2.187e-09 | -1.7921e-09 | -3.1109e-10 | -2.7174e-10 | 2.7578e-11 | -1.1262e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.951e-10 | 1.5019e-09 | -2.4407e-09 | 3.7208e-10 | 1.0948e-10 | -3.7821e-11 | 2.187e-09 | -1.7921e-09 | -3.1109e-10 | -2.7174e-10 | 2.7578e-11 | -1.1262e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9608e-09 | 1.2015e-08 | -1.9526e-08 | -3.0936e-09 | -1.0404e-08 | 1.7047e-08 | 1.7496e-08 | -1.4337e-08 | -2.4887e-09 | -1.5581e-08 | 1.2573e-08 | 2.065e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9019e-10 | 3.0038e-09 | -4.8815e-09 | -1.2301e-10 | -1.3924e-09 | 2.4029e-09 | 4.374e-09 | -3.5843e-09 | -6.2217e-10 | -2.4588e-09 | 1.8197e-09 | 1.9846e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9019e-10 | 3.0038e-09 | -4.8815e-09 | -1.2301e-10 | -1.3924e-09 | 2.4029e-09 | 4.374e-09 | -3.5843e-09 | -6.2217e-10 | -2.4588e-09 | 1.8197e-09 | 1.9846e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523
Line4_2_6 | 1.9028 | 0 | 0 | 1.9028 | 0 | 0 | 0.43944 | 0 | 0 | 0.43944 | 0 | 0 | 0.1738 | 4.6337e-08 | -5.0391e-08 | -0.11587 | -4.1156e-08 | 4.4068e-08 | 0.18104 | -2.5389e-08 | -2.264e-08 | -0.12069 | 2.0205e-08 | 1.799e-08 | -52.3774 | 0 | 0 | 127.6226 | 0 | 0 | 0.57109 | 0.85115 | 0.88993 | 0.38073 | 0.83834 | 0.87034 | -6.2082 | -117.0911 | 115.8212 | -6.2082 | -114.6593 | 113.6959
Line5_6_7 | 1.9028 | 0 | 0 | 1.9028 | 0 | 0 | 0.43944 | 0 | 0 | 0.43944 | 0 | 0 | 0.11587 | 4.1334e-08 | -4.399e-08 | -0.057933 | -3.3516e-08 | 3.5361e-08 | 0.12069 | -1.9947e-08 | -1.8306e-08 | -0.060347 | 1.4591e-08 | 1.2945e-08 | -52.3774 | 0 | 0 | 127.6226 | 0 | 0 | 0.38073 | 0.83834 | 0.87034 | 0.19036 | 0.82708 | 0.85199 | -6.2082 | -114.6593 | 113.6959 | -6.2082 | -112.1566 | 111.4758
Line6_7_8 | 1.9028 | 0 | 0 | 1.9028 | 0 | 0 | 0.43944 | 0 | 0 | 0.43944 | 0 | 0 | 0.057933 | 3.3712e-08 | -3.5242e-08 | -1.754e-14 | -2.3252e-08 | 2.4311e-08 | 0.060347 | -1.4218e-08 | -1.3362e-08 | 3.8712e-14 | 9.0526e-09 | 7.6558e-09 | -52.3774 | 0 | 0 | 127.6226 | 0 | 0 | 0.19036 | 0.82708 | 0.85199 | 0 | 0.81744 | 0.83499 | -6.2082 | -112.1566 | 111.4758 | 0 | -109.5898 | 109.1618
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4805e-21 | 1.1728e-08 | -1.2081e-08 | -1.0731e-18 | 2.0306e-10 | 1.4989e-10 | -3.6891e-22 | -4.2826e-09 | -4.0869e-09 | 8.3894e-18 | 4.8743e-10 | -5.1813e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81744 | 0.83499 | 0 | 0.81744 | 0.83499 | 0 | -109.5898 | 109.1618 | 0 | -109.5898 | 109.1618
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4805e-21 | 1.1728e-08 | -1.2081e-08 | -1.0731e-18 | 2.0306e-10 | 1.4989e-10 | -3.6891e-22 | -4.2826e-09 | -4.0869e-09 | 8.3894e-18 | 4.8743e-10 | -5.1813e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81744 | 0.83499 | 0 | 0.81744 | 0.83499 | 0 | -109.5898 | 109.1618 | 0 | -109.5898 | 109.1618
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4657e-09 | 1.0513e-08 | -1.7085e-08 | -2.5985e-09 | -8.9019e-09 | 1.4607e-08 | 1.5309e-08 | -1.2545e-08 | -2.1776e-09 | -1.3394e-08 | 1.078e-08 | 1.7539e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76145 | 0.86546 | 0.91069 | 0.76145 | 0.86546 | 0.91069 | -6.2082 | -119.4467 | 117.8523 | -6.2082 | -119.4467 | 117.8523

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.030559 | 0 | 0 | 0.030559 | 0 | 0 | 0.0070572 | 0 | 0 | 0.0070572 | 0 | 0 | 0.0047289 | 7.7837e-10 | -9.4746e-10 | -0.004714 | -7.3373e-10 | 8.8407e-10 | 0.0047314 | -6.4348e-10 | -3.5206e-10 | -0.0047159 | 5.9567e-10 | 3.3635e-10 | -45.1119 | 0 | 0 | 134.8881 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94483 | 0.94912 | 0.94993 | -0.096849 | -119.9962 | 119.9684 | -0.10058 | -119.9646 | 119.9362
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4658e-11 | 1.3153e-10 | -2.4721e-10 | -4.6554e-11 | -1.0763e-10 | 2.0521e-10 | 2.6108e-10 | -2.0927e-10 | -9.1262e-12 | -2.2315e-10 | 1.7461e-10 | 5.7825e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3882e-11 | 1.0961e-10 | -2.0601e-10 | -3.5778e-11 | -8.5708e-11 | 1.6401e-10 | 2.1757e-10 | -1.7439e-10 | -7.6052e-12 | -1.7964e-10 | 1.3973e-10 | 4.2615e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2329e-11 | 6.5763e-11 | -1.236e-10 | -1.4225e-11 | -4.1865e-11 | 8.1602e-11 | 1.3054e-10 | -1.0463e-10 | -4.5631e-12 | -9.2609e-11 | 6.9976e-11 | 1.2194e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0776e-11 | 2.1921e-11 | -4.1202e-11 | 7.3276e-12 | 1.977e-12 | -8.0057e-13 | 4.3514e-11 | -3.4878e-11 | -1.521e-12 | -5.5812e-12 | 2.1907e-13 | -1.8227e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1553e-11 | 4.3842e-11 | -8.2403e-11 | -3.4487e-12 | -1.9944e-11 | 4.0401e-11 | 8.7027e-11 | -6.9756e-11 | -3.0421e-12 | -4.9095e-11 | 3.5097e-11 | -3.0166e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0776e-11 | 2.1921e-11 | -4.1202e-11 | 7.3276e-12 | 1.977e-12 | -8.0057e-13 | 4.3514e-11 | -3.4878e-11 | -1.521e-12 | -5.5812e-12 | 2.1907e-13 | -1.8227e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0776e-11 | 2.1921e-11 | -4.1202e-11 | 7.3276e-12 | 1.977e-12 | -8.0057e-13 | 4.3514e-11 | -3.4878e-11 | -1.521e-12 | -5.5812e-12 | 2.1907e-13 | -1.8227e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0776e-11 | 2.1921e-11 | -4.1202e-11 | 7.3276e-12 | 1.977e-12 | -8.0057e-13 | 4.3514e-11 | -3.4878e-11 | -1.521e-12 | -5.5812e-12 | 2.1907e-13 | -1.8227e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6211e-11 | 1.7537e-10 | -3.2961e-10 | -6.8107e-11 | -1.5147e-10 | 2.8761e-10 | 3.4811e-10 | -2.7903e-10 | -1.2168e-11 | -3.1018e-10 | 2.4437e-10 | 8.8245e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1553e-11 | 4.3842e-11 | -8.2403e-11 | -3.4487e-12 | -1.9944e-11 | 4.0401e-11 | 8.7027e-11 | -6.9756e-11 | -3.042e-12 | -4.9095e-11 | 3.5097e-11 | -3.0168e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1553e-11 | 4.3842e-11 | -8.2403e-11 | -3.4487e-12 | -1.9944e-11 | 4.0401e-11 | 8.7027e-11 | -6.9756e-11 | -3.042e-12 | -4.9095e-11 | 3.5097e-11 | -3.0168e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line4_2_6 | 0.030559 | 0 | 0 | 0.030559 | 0 | 0 | 0.0070572 | 0 | 0 | 0.0070572 | 0 | 0 | 0.004714 | 7.368e-10 | -8.8385e-10 | -0.004699 | -6.5047e-10 | 7.7787e-10 | 0.0047159 | -5.9363e-10 | -3.4004e-10 | -0.0047003 | 5.2088e-10 | 3.0093e-10 | -45.1119 | 0 | 0 | 134.8881 | 0 | 0 | 0.94483 | 0.94912 | 0.94993 | 0.94178 | 0.9488 | 0.94964 | -0.10058 | -119.9646 | 119.9362 | -0.10434 | -119.9329 | 119.9039
Line5_6_7 | 0.030559 | 0 | 0 | 0.030559 | 0 | 0 | 0.0070572 | 0 | 0 | 0.0070572 | 0 | 0 | 0.004699 | 6.5463e-10 | -7.7662e-10 | -0.0046841 | -5.2661e-10 | 6.2806e-10 | 0.0047003 | -5.1701e-10 | -3.0649e-10 | -0.0046847 | 4.1941e-10 | 2.4409e-10 | -45.1119 | 0 | 0 | 134.8881 | 0 | 0 | 0.94178 | 0.9488 | 0.94964 | 0.93872 | 0.94849 | 0.94934 | -0.10434 | -119.9329 | 119.9039 | -0.10812 | -119.9013 | 119.8715
Line6_7_8 | 0.030559 | 0 | 0 | 0.030559 | 0 | 0 | 0.0070572 | 0 | 0 | 0.0070572 | 0 | 0 | 0.0046841 | 5.3187e-10 | -6.2579e-10 | -0.0046692 | -3.6216e-10 | 4.3466e-10 | 0.0046847 | -4.1372e-10 | -2.515e-10 | -0.0046692 | 2.9136e-10 | 1.6591e-10 | -45.1119 | 0 | 0 | 134.8881 | 0 | 0 | 0.93872 | 0.94849 | 0.94934 | 0.93566 | 0.94817 | 0.94905 | -0.10812 | -119.9013 | 119.8715 | -0.11193 | -119.8696 | 119.8392
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7384e-11 | 1.8425e-10 | -2.1568e-10 | 4.9176e-11 | 6.3439e-12 | 3.294e-12 | 2.3548e-10 | -1.4192e-10 | -8.7592e-11 | -6.3671e-12 | 7.5171e-12 | -9.2779e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93566 | 0.94817 | 0.94905 | 0.93566 | 0.94817 | 0.94905 | -0.11193 | -119.8696 | 119.8392 | -0.11193 | -119.8696 | 119.8392
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7384e-11 | 1.8425e-10 | -2.1568e-10 | 4.9176e-11 | 6.3439e-12 | 3.294e-12 | 2.3548e-10 | -1.4192e-10 | -8.7592e-11 | -6.3671e-12 | 7.5171e-12 | -9.2779e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93566 | 0.94817 | 0.94905 | 0.93566 | 0.94817 | 0.94905 | -0.11193 | -119.8696 | 119.8392 | -0.11193 | -119.8696 | 119.8392
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5434e-11 | 1.5345e-10 | -2.8841e-10 | -5.733e-11 | -1.2955e-10 | 2.4641e-10 | 3.046e-10 | -2.4415e-10 | -1.0647e-11 | -2.6666e-10 | 2.0949e-10 | 7.3035e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94789 | 0.94943 | 0.95023 | 0.94789 | 0.94943 | 0.95023 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.02895 | 0 | 0 | 0.02895 | 0 | 0 | 0.0066858 | 0 | 0 | 0.0066858 | 0 | 0 | 0.0042442 | 6.9859e-10 | -8.5036e-10 | -0.0042308 | -6.5852e-10 | 7.9346e-10 | 0.0042465 | -5.7752e-10 | -3.1598e-10 | -0.0042325 | 5.3462e-10 | 3.0188e-10 | -45.1119 | 0 | 0 | 134.8881 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.89511 | 0.89916 | 0.89994 | -0.096849 | -119.9962 | 119.9684 | -0.10058 | -119.9646 | 119.9362
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8031e-11 | 1.1805e-10 | -2.2187e-10 | -4.1783e-11 | -9.6598e-11 | 1.8417e-10 | 2.3432e-10 | -1.8782e-10 | -8.1908e-12 | -2.0028e-10 | 1.5671e-10 | 5.1898e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8359e-11 | 9.8372e-11 | -1.8489e-10 | -3.2111e-11 | -7.6923e-11 | 1.472e-10 | 1.9527e-10 | -1.5652e-10 | -6.8257e-12 | -1.6122e-10 | 1.2541e-10 | 3.8247e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9015e-11 | 5.9023e-11 | -1.1094e-10 | -1.2767e-11 | -3.7574e-11 | 7.3239e-11 | 1.1716e-10 | -9.391e-11 | -4.0954e-12 | -8.3117e-11 | 6.2803e-11 | 1.0944e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6718e-12 | 1.9674e-11 | -3.6979e-11 | 6.5766e-12 | 1.7744e-12 | -7.1851e-13 | 3.9054e-11 | -3.1303e-11 | -1.3651e-12 | -5.0092e-12 | 1.9662e-13 | -1.6359e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9344e-11 | 3.9349e-11 | -7.3957e-11 | -3.0952e-12 | -1.79e-11 | 3.626e-11 | 7.8108e-11 | -6.2607e-11 | -2.7303e-12 | -4.4063e-11 | 3.15e-11 | -2.7074e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6718e-12 | 1.9674e-11 | -3.6979e-11 | 6.5766e-12 | 1.7744e-12 | -7.1851e-13 | 3.9054e-11 | -3.1303e-11 | -1.3651e-12 | -5.0092e-12 | 1.9662e-13 | -1.6359e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6718e-12 | 1.9674e-11 | -3.6979e-11 | 6.5766e-12 | 1.7744e-12 | -7.1851e-13 | 3.9054e-11 | -3.1303e-11 | -1.3651e-12 | -5.0092e-12 | 1.9662e-13 | -1.6359e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6718e-12 | 1.9674e-11 | -3.6979e-11 | 6.5766e-12 | 1.7744e-12 | -7.1851e-13 | 3.9054e-11 | -3.1303e-11 | -1.3651e-12 | -5.0092e-12 | 1.9662e-13 | -1.6359e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7375e-11 | 1.5739e-10 | -2.9583e-10 | -6.1126e-11 | -1.3595e-10 | 2.5813e-10 | 3.1243e-10 | -2.5043e-10 | -1.0921e-11 | -2.7839e-10 | 2.1932e-10 | 7.9201e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9344e-11 | 3.9349e-11 | -7.3957e-11 | -3.0952e-12 | -1.79e-11 | 3.626e-11 | 7.8108e-11 | -6.2607e-11 | -2.7302e-12 | -4.4063e-11 | 3.15e-11 | -2.7076e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9344e-11 | 3.9349e-11 | -7.3957e-11 | -3.0952e-12 | -1.79e-11 | 3.626e-11 | 7.8108e-11 | -6.2607e-11 | -2.7302e-12 | -4.4063e-11 | 3.15e-11 | -2.7076e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684
Line4_2_6 | 0.02895 | 0 | 0 | 0.02895 | 0 | 0 | 0.0066858 | 0 | 0 | 0.0066858 | 0 | 0 | 0.0042308 | 6.6128e-10 | -7.9326e-10 | -0.0042174 | -5.838e-10 | 6.9815e-10 | 0.0042325 | -5.3278e-10 | -3.0518e-10 | -0.0042185 | 4.6749e-10 | 2.7009e-10 | -45.1119 | 0 | 0 | 134.8881 | 0 | 0 | 0.89511 | 0.89916 | 0.89994 | 0.89221 | 0.89886 | 0.89966 | -0.10058 | -119.9646 | 119.9362 | -0.10434 | -119.9329 | 119.9039
Line5_6_7 | 0.02895 | 0 | 0 | 0.02895 | 0 | 0 | 0.0066858 | 0 | 0 | 0.0066858 | 0 | 0 | 0.0042174 | 5.8754e-10 | -6.9702e-10 | -0.004204 | -4.7264e-10 | 5.6369e-10 | 0.0042185 | -4.6402e-10 | -2.7507e-10 | -0.0042046 | 3.7642e-10 | 2.1907e-10 | -45.1119 | 0 | 0 | 134.8881 | 0 | 0 | 0.89221 | 0.89886 | 0.89966 | 0.88931 | 0.89857 | 0.89938 | -0.10434 | -119.9329 | 119.9039 | -0.10812 | -119.9013 | 119.8715
Line6_7_8 | 0.02895 | 0 | 0 | 0.02895 | 0 | 0 | 0.0066858 | 0 | 0 | 0.0066858 | 0 | 0 | 0.004204 | 4.7736e-10 | -5.6165e-10 | -0.0041906 | -3.2504e-10 | 3.9011e-10 | 0.0042046 | -3.7131e-10 | -2.2573e-10 | -0.0041906 | 2.615e-10 | 1.489e-10 | -45.1119 | 0 | 0 | 134.8881 | 0 | 0 | 0.88931 | 0.89857 | 0.89938 | 0.88642 | 0.89827 | 0.8991 | -0.10812 | -119.9013 | 119.8715 | -0.11193 | -119.8696 | 119.8392
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4578e-11 | 1.6537e-10 | -1.9357e-10 | 4.4136e-11 | 5.6937e-12 | 2.9564e-12 | 2.1134e-10 | -1.2738e-10 | -7.8614e-11 | -5.7145e-12 | 6.7466e-12 | -8.327e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88642 | 0.89827 | 0.8991 | 0.88642 | 0.89827 | 0.8991 | -0.11193 | -119.8696 | 119.8392 | -0.11193 | -119.8696 | 119.8392
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4578e-11 | 1.6537e-10 | -1.9357e-10 | 4.4136e-11 | 5.6937e-12 | 2.9564e-12 | 2.1134e-10 | -1.2738e-10 | -7.8614e-11 | -5.7145e-12 | 6.7466e-12 | -8.327e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88642 | 0.89827 | 0.8991 | 0.88642 | 0.89827 | 0.8991 | -0.11193 | -119.8696 | 119.8392 | -0.11193 | -119.8696 | 119.8392
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7703e-11 | 1.3772e-10 | -2.5885e-10 | -5.1454e-11 | -1.1627e-10 | 2.2115e-10 | 2.7338e-10 | -2.1912e-10 | -9.556e-12 | -2.3933e-10 | 1.8802e-10 | 6.555e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.898 | 0.89946 | 0.90022 | 0.898 | 0.89946 | 0.90022 | -0.096849 | -119.9962 | 119.9684 | -0.096849 | -119.9962 | 119.9684

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 2.5633 | 2.4976 | 0 | 2.5633 | 2.4976 | 0 | 0.59196 | 0.57679 | 0 | 0.59196 | 0.57679 | -5.7524e-09 | 0.14085 | 0.29864 | 4.9349e-09 | -0.10564 | -0.22398 | -1.0015e-07 | 0.49278 | 0.38619 | 8.832e-08 | -0.36959 | -0.28964 | 0 | 161.9848 | 63.5318 | 0 | -18.0152 | -116.4683 | 1.0178 | 0.8658 | 0.84639 | 0.96447 | 0.64935 | 0.63479 | -1.7947 | -123.9666 | 115.8176 | -1.7311 | -123.9666 | 115.8176
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6303e-09 | -2.2338e-08 | 1.8058e-08 | 3.1435e-09 | 1.9191e-08 | -1.4425e-08 | -2.7317e-08 | 1.6193e-08 | 1.0086e-08 | 2.2642e-08 | -1.3725e-08 | -8.6429e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0253e-09 | -1.8615e-08 | 1.5049e-08 | 2.5385e-09 | 1.5468e-08 | -1.1416e-08 | -2.2764e-08 | 1.3494e-08 | 8.4053e-09 | 1.8089e-08 | -1.1026e-08 | -6.9619e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8152e-09 | -1.1169e-08 | 9.0292e-09 | 1.3284e-09 | 8.0226e-09 | -5.3962e-09 | -1.3659e-08 | 8.0966e-09 | 5.0432e-09 | 8.983e-09 | -5.6283e-09 | -3.5998e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0505e-10 | -3.7229e-09 | 3.0097e-09 | 1.1826e-10 | 5.7678e-10 | 6.2322e-10 | -4.5529e-09 | 2.6989e-09 | 1.6811e-09 | -1.2272e-10 | -2.3058e-10 | -2.3766e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2101e-09 | -7.4458e-09 | 6.0194e-09 | 7.2331e-10 | 4.2997e-09 | -2.3865e-09 | -9.1057e-09 | 5.3977e-09 | 3.3621e-09 | 4.4301e-09 | -2.9295e-09 | -1.9187e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0505e-10 | -3.7229e-09 | 3.0097e-09 | 1.1826e-10 | 5.7678e-10 | 6.2322e-10 | -4.5529e-09 | 2.6989e-09 | 1.6811e-09 | -1.2272e-10 | -2.3058e-10 | -2.3766e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8021e-10 | -3.7239e-09 | 3.1273e-09 | 5.9546e-11 | 5.3433e-10 | 5.8292e-10 | -4.5986e-09 | 2.787e-09 | 1.7105e-09 | -1.4668e-10 | -2.5454e-10 | -2.6161e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0336 | 0.88178 | 0.86239 | 1.0336 | 0.88178 | 0.86239 | -2.1124 | -124.2999 | 115.4808 | -2.1124 | -124.2999 | 115.4808
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0505e-10 | -3.7229e-09 | 3.0097e-09 | 1.1826e-10 | 5.7678e-10 | 6.2322e-10 | -4.5529e-09 | 2.6989e-09 | 1.6811e-09 | -1.2272e-10 | -2.3058e-10 | -2.3766e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8404e-09 | -2.9783e-08 | 2.4078e-08 | 4.3536e-09 | 2.6637e-08 | -2.0445e-08 | -3.6423e-08 | 2.1591e-08 | 1.3448e-08 | 3.1747e-08 | -1.9123e-08 | -1.2005e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176
Line2_1_4 | 0.17321 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0046666 | -0.0052706 | -0.0052784 | 0.0049666 | 0.0055706 | 0.0055784 | -0.040444 | -0.034229 | -0.033441 | 0.041044 | 0.034829 | 0.034041 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0178 | 0.8658 | 0.84639 | 1.0336 | 0.88178 | 0.86239 | -1.7947 | -123.9666 | 115.8176 | -2.1124 | -124.2999 | 115.4808
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2101e-09 | -7.4458e-09 | 6.0194e-09 | 7.2331e-10 | 4.2997e-09 | -2.3865e-09 | -9.1057e-09 | 5.3977e-09 | 3.3621e-09 | 4.4301e-09 | -2.9295e-09 | -1.9187e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176
Line4_2_6 | 0 | 2.5633 | 2.4976 | 0 | 2.5633 | 2.4976 | 0 | 0.59196 | 0.57679 | 0 | 0.59196 | 0.57679 | -4.6341e-09 | 0.10564 | 0.22398 | 3.9853e-09 | -0.070426 | -0.14932 | -8.8432e-08 | 0.36959 | 0.28964 | 7.3255e-08 | -0.24639 | -0.1931 | 0 | 161.9848 | 63.5317 | 0 | -18.0152 | -116.4683 | 0.96447 | 0.64935 | 0.63479 | 0.91114 | 0.4329 | 0.42319 | -1.7311 | -123.9666 | 115.8176 | -1.6601 | -123.9666 | 115.8176
Line5_6_7 | 0 | 2.5633 | 2.4976 | 0 | 2.5633 | 2.4976 | 0 | 0.59196 | 0.57679 | 0 | 0.59196 | 0.57679 | -3.5228e-09 | 0.070426 | 0.14932 | 3.053e-09 | -0.035213 | -0.074659 | -7.3357e-08 | 0.24639 | 0.1931 | 5.5545e-08 | -0.1232 | -0.096548 | 0 | 161.9848 | 63.5317 | 0 | -18.0152 | -116.4683 | 0.91114 | 0.4329 | 0.42319 | 0.85781 | 0.21645 | 0.2116 | -1.6601 | -123.9666 | 115.8176 | -1.5802 | -123.9666 | 115.8176
Line6_7_8 | 0 | 2.5633 | 2.4976 | 0 | 2.5633 | 2.4976 | 0 | 0.59196 | 0.57679 | 0 | 0.59196 | 0.57679 | -2.4498e-09 | 0.035213 | 0.074659 | 2.1695e-09 | 2.4354e-14 | 1.0938e-14 | -5.5636e-08 | 0.1232 | 0.096548 | 3.5905e-08 | 1.9254e-14 | 1.5675e-14 | 0 | 161.9849 | 63.5317 | 0 | -18.0151 | -116.4683 | 0.85781 | 0.21645 | 0.2116 | 0.80449 | 0 | 0 | -1.5802 | -123.9666 | 115.8176 | -1.4898 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.2317e-10 | 5.9302e-22 | -5.1643e-22 | 7.2317e-10 | 1.6782e-18 | -4.4938e-18 | -1.7993e-08 | -1.2228e-21 | -3.7659e-22 | -8.0525e-11 | 1.4592e-17 | 8.831e-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80449 | 0 | 0 | 0.80449 | 0 | 0 | -1.4898 | 0 | 0 | -1.4898 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.2317e-10 | 5.9302e-22 | -5.1643e-22 | 7.2317e-10 | 1.6782e-18 | -4.4938e-18 | -1.7993e-08 | -1.2228e-21 | -3.7659e-22 | -8.0525e-11 | 1.4592e-17 | 8.831e-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80449 | 0 | 0 | 0.80449 | 0 | 0 | -1.4898 | 0 | 0 | -1.4898 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.2354e-09 | -2.606e-08 | 2.1068e-08 | 3.7486e-09 | 2.2914e-08 | -1.7435e-08 | -3.187e-08 | 1.8892e-08 | 1.1767e-08 | 2.7194e-08 | -1.6424e-08 | -1.0324e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0178 | 0.8658 | 0.84639 | 1.0178 | 0.8658 | 0.84639 | -1.7947 | -123.9666 | 115.8176 | -1.7947 | -123.9666 | 115.8176

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 2.6613 | 2.5906 | 0 | 2.6613 | 2.5906 | 0 | 0.61461 | 0.59827 | 0 | 0.61461 | 0.59827 | -6.3573e-09 | 0.15193 | 0.3214 | 5.4439e-09 | -0.11394 | -0.24105 | -1.1009e-07 | 0.53117 | 0.41548 | 9.699e-08 | -0.39837 | -0.31161 | 0 | 161.8456 | 63.385 | 0 | -18.1544 | -116.615 | 1.0643 | 0.89889 | 0.87799 | 1.0089 | 0.67417 | 0.65849 | -1.8595 | -124.1162 | 115.661 | -1.7939 | -124.1162 | 115.661
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1175e-09 | -2.5215e-08 | 2.0361e-08 | 3.5684e-09 | 2.1666e-08 | -1.6263e-08 | -3.1057e-08 | 1.8291e-08 | 1.1354e-08 | 2.5742e-08 | -1.5503e-08 | -9.7295e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4313e-09 | -2.1012e-08 | 1.6968e-08 | 2.8821e-09 | 1.7463e-08 | -1.287e-08 | -2.5881e-08 | 1.5243e-08 | 9.4616e-09 | 2.0565e-08 | -1.2454e-08 | -7.8372e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0588e-09 | -1.2607e-08 | 1.0181e-08 | 1.5096e-09 | 9.0585e-09 | -6.0826e-09 | -1.5529e-08 | 9.1456e-09 | 5.677e-09 | 1.0213e-08 | -6.3573e-09 | -4.0526e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8625e-10 | -4.2025e-09 | 3.3936e-09 | 1.3711e-10 | 6.5349e-10 | 7.0457e-10 | -5.1762e-09 | 3.0485e-09 | 1.8923e-09 | -1.3929e-10 | -2.6024e-10 | -2.6792e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3725e-09 | -8.405e-09 | 6.7872e-09 | 8.2336e-10 | 4.856e-09 | -2.689e-09 | -1.0352e-08 | 6.097e-09 | 3.7847e-09 | 5.0369e-09 | -3.3088e-09 | -2.1602e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8625e-10 | -4.2025e-09 | 3.3936e-09 | 1.3711e-10 | 6.5349e-10 | 7.0457e-10 | -5.1762e-09 | 3.0485e-09 | 1.8923e-09 | -1.3929e-10 | -2.6024e-10 | -2.6792e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6164e-10 | -4.2062e-09 | 3.5188e-09 | 7.5828e-11 | 6.0993e-10 | 6.6334e-10 | -5.2269e-09 | 3.1433e-09 | 1.9236e-09 | -1.6439e-10 | -2.8533e-10 | -2.9301e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0801 | 0.91489 | 0.894 | 1.0801 | 0.91489 | 0.894 | -2.1626 | -124.4348 | 115.3389 | -2.1626 | -124.4348 | 115.3389
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.8625e-10 | -4.2025e-09 | 3.3936e-09 | 1.3711e-10 | 6.5349e-10 | 7.0457e-10 | -5.1762e-09 | 3.0485e-09 | 1.8923e-09 | -1.3929e-10 | -2.6024e-10 | -2.6792e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.49e-09 | -3.362e-08 | 2.7149e-08 | 4.9409e-09 | 3.0071e-08 | -2.305e-08 | -4.1409e-08 | 2.4388e-08 | 1.5139e-08 | 3.6094e-08 | -2.16e-08 | -1.3514e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661
Line2_1_4 | 0.17321 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0049273 | -0.0055647 | -0.0055701 | 0.0052273 | 0.0058646 | 0.0058701 | -0.042285 | -0.035522 | -0.034675 | 0.042885 | 0.036122 | 0.035275 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.0643 | 0.89889 | 0.87799 | 1.0801 | 0.91489 | 0.894 | -1.8595 | -124.1162 | 115.661 | -2.1626 | -124.4348 | 115.3389
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3725e-09 | -8.405e-09 | 6.7871e-09 | 8.2336e-10 | 4.856e-09 | -2.689e-09 | -1.0352e-08 | 6.097e-09 | 3.7846e-09 | 5.0369e-09 | -3.3088e-09 | -2.1602e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661
Line4_2_6 | 0 | 2.6613 | 2.5906 | 0 | 2.6613 | 2.5906 | 0 | 0.61461 | 0.59827 | 0 | 0.61461 | 0.59827 | -5.1091e-09 | 0.11394 | 0.24105 | 4.3856e-09 | -0.075963 | -0.1607 | -9.7117e-08 | 0.39837 | 0.31161 | 8.0401e-08 | -0.26558 | -0.20774 | 0 | 161.8456 | 63.385 | 0 | -18.1544 | -116.615 | 1.0089 | 0.67417 | 0.65849 | 0.95361 | 0.44945 | 0.43899 | -1.7939 | -124.1162 | 115.661 | -1.7208 | -124.1162 | 115.661
Line5_6_7 | 0 | 2.6613 | 2.5906 | 0 | 2.6613 | 2.5906 | 0 | 0.61461 | 0.59827 | 0 | 0.61461 | 0.59827 | -3.8754e-09 | 0.075963 | 0.1607 | 3.353e-09 | -0.037981 | -0.080349 | -8.0517e-08 | 0.26558 | 0.20774 | 6.0951e-08 | -0.13279 | -0.10387 | 0 | 161.8456 | 63.385 | 0 | -18.1544 | -116.615 | 0.95361 | 0.44945 | 0.43899 | 0.89827 | 0.22472 | 0.2195 | -1.7208 | -124.1162 | 115.661 | -1.6385 | -124.1162 | 115.661
Line6_7_8 | 0 | 2.6613 | 2.5906 | 0 | 2.6613 | 2.5906 | 0 | 0.61461 | 0.59827 | 0 | 0.61461 | 0.59827 | -2.69e-09 | 0.037981 | 0.080349 | 2.3798e-09 | 7.0234e-14 | 3.1679e-14 | -6.1055e-08 | 0.13279 | 0.10387 | 3.9409e-08 | -3.571e-14 | -4.9431e-14 | 0 | 161.8456 | 63.385 | 0 | -18.1544 | -116.615 | 0.89827 | 0.22472 | 0.2195 | 0.84294 | 0 | 0 | -1.6385 | -124.1162 | 115.661 | -1.5455 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9328e-10 | -2.2143e-21 | -4.6565e-22 | 7.9328e-10 | 1.8516e-18 | -4.9389e-18 | -1.9751e-08 | -2.686e-21 | 1.9281e-21 | -9.17e-11 | 1.6018e-17 | 1.0401e-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84294 | 0 | 0 | 0.84294 | 0 | 0 | -1.5455 | 0 | 0 | -1.5455 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9328e-10 | -2.2143e-21 | -4.6565e-22 | 7.9328e-10 | 1.8516e-18 | -4.9389e-18 | -1.9751e-08 | -2.686e-21 | 1.9281e-21 | -9.17e-11 | 1.6018e-17 | 1.0401e-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84294 | 0 | 0 | 0.84294 | 0 | 0 | -1.5455 | 0 | 0 | -1.5455 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8038e-09 | -2.9417e-08 | 2.3755e-08 | 4.2546e-09 | 2.5868e-08 | -1.9657e-08 | -3.6233e-08 | 2.134e-08 | 1.3246e-08 | 3.0918e-08 | -1.8551e-08 | -1.1622e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0643 | 0.89889 | 0.87799 | 1.0643 | 0.89889 | 0.87799 | -1.8595 | -124.1162 | 115.661 | -1.8595 | -124.1162 | 115.661

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.034437 | 0.034371 | 0 | 0.034437 | 0.034371 | 0 | 0.0079529 | 0.0079376 | 0 | 0.0079529 | 0.0079376 | -1.7543e-11 | 0.0059594 | 0.0059637 | -1.2122e-11 | -0.0059519 | -0.0059494 | -1.0122e-09 | 0.0060234 | 0.0059864 | 9.4151e-10 | -0.0059999 | -0.0059665 | 0 | -165.4292 | 74.8016 | 0 | 14.5708 | -105.1984 | 1.0671 | 1.0654 | 1.0646 | 1.0666 | 1.0627 | 1.0615 | -0.026827 | -120.1232 | 119.9107 | -0.036196 | -120.1991 | 119.8837
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6919e-10 | 1.8644e-10 | 6.4825e-10 | -2.9122e-10 | -2.156e-10 | -5.9706e-10 | -2.6761e-10 | 3.0686e-10 | 6.3047e-11 | 2.2108e-10 | -2.6454e-10 | -5.8928e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2433e-10 | 1.5537e-10 | 5.4021e-10 | -2.4636e-10 | -1.8452e-10 | -4.8902e-10 | -2.2301e-10 | 2.5572e-10 | 5.2539e-11 | 1.7648e-10 | -2.134e-10 | -4.842e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.346e-10 | 9.3219e-11 | 3.2412e-10 | -1.5663e-10 | -1.2238e-10 | -2.7294e-10 | -1.338e-10 | 1.5343e-10 | 3.1523e-11 | 8.7279e-11 | -1.1111e-10 | -2.7405e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4866e-11 | 3.1073e-11 | 1.0804e-10 | -6.6895e-11 | -6.0233e-11 | -5.6853e-11 | -4.4601e-11 | 5.1144e-11 | 1.0508e-11 | -1.9236e-12 | -8.8214e-12 | -6.3891e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9731e-11 | 6.2146e-11 | 2.1608e-10 | -1.1176e-10 | -9.1306e-11 | -1.6489e-10 | -8.9202e-11 | 1.0229e-10 | 2.1016e-11 | 4.2678e-11 | -5.9965e-11 | -1.6897e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4866e-11 | 3.1073e-11 | 1.0804e-10 | -6.6895e-11 | -6.0233e-11 | -5.6853e-11 | -4.4601e-11 | 5.1144e-11 | 1.0508e-11 | -1.9236e-12 | -8.8214e-12 | -6.3891e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0724e-10 | 9.3747e-11 | 1.7154e-10 | -1.2986e-10 | -1.2309e-10 | -1.1958e-10 | -2.1197e-11 | 7.5887e-11 | 3.4225e-11 | -2.5878e-11 | -3.2776e-11 | -3.0344e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0827 | 1.081 | 1.0802 | 1.0827 | 1.081 | 1.0802 | -0.35571 | -120.4512 | 119.5819 | -0.35571 | -120.4512 | 119.5819
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4866e-11 | 3.1073e-11 | 1.0804e-10 | -6.6895e-11 | -6.0233e-11 | -5.6853e-11 | -4.4601e-11 | 5.1144e-11 | 1.0508e-11 | -1.9236e-12 | -8.8214e-12 | -6.3891e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5893e-10 | 2.4858e-10 | 8.6433e-10 | -3.8095e-10 | -2.7774e-10 | -8.1314e-10 | -3.5681e-10 | 4.0915e-10 | 8.4062e-11 | 3.1028e-10 | -3.6683e-10 | -7.9943e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107
Line2_1_4 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0035821 | -0.0036479 | -0.0036199 | 0.0038821 | 0.0039479 | 0.0039199 | -0.042533 | -0.04246 | -0.042428 | 0.043133 | 0.04306 | 0.043028 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.0671 | 1.0654 | 1.0646 | 1.0827 | 1.081 | 1.0802 | -0.026827 | -120.1232 | 119.9107 | -0.35571 | -120.4512 | 119.5819
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9731e-11 | 6.2146e-11 | 2.1608e-10 | -1.1176e-10 | -9.1306e-11 | -1.6489e-10 | -8.9202e-11 | 1.0229e-10 | 2.1015e-11 | 4.2677e-11 | -5.9965e-11 | -1.6897e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107
Line4_2_6 | 0 | 0.034437 | 0.034371 | 0 | 0.034437 | 0.034371 | 0 | 0.0079529 | 0.0079376 | 0 | 0.0079529 | 0.0079376 | -5.2671e-11 | 0.0059519 | 0.0059494 | 7.3888e-12 | -0.0059445 | -0.0059352 | -9.4411e-10 | 0.0059999 | 0.0059665 | 8.2628e-10 | -0.0059765 | -0.0059466 | 0 | -165.4292 | 74.8016 | 0 | 14.5708 | -105.1984 | 1.0666 | 1.0627 | 1.0615 | 1.066 | 1.0599 | 1.0585 | -0.036196 | -120.1991 | 119.8837 | -0.045575 | -120.2754 | 119.8565
Line5_6_7 | 0 | 0.034437 | 0.034371 | 0 | 0.034437 | 0.034371 | 0 | 0.0079529 | 0.0079376 | 0 | 0.0079529 | 0.0079376 | -7.0082e-11 | 0.0059445 | 0.0059352 | 9.1837e-12 | -0.0059371 | -0.0059209 | -8.2955e-10 | 0.0059765 | 0.0059466 | 6.6462e-10 | -0.0059531 | -0.0059266 | 0 | -165.4292 | 74.8016 | 0 | 14.5708 | -105.1984 | 1.066 | 1.0599 | 1.0585 | 1.0655 | 1.0572 | 1.0554 | -0.045575 | -120.2754 | 119.8565 | -0.054963 | -120.3521 | 119.8291
Line6_7_8 | 0 | 0.034437 | 0.034371 | 0 | 0.034437 | 0.034371 | 0 | 0.0079529 | 0.0079376 | 0 | 0.0079529 | 0.0079376 | -6.9779e-11 | 0.0059371 | 0.0059209 | -6.7336e-12 | -0.0059296 | -0.0059067 | -6.6856e-10 | 0.0059531 | 0.0059266 | 4.566e-10 | -0.0059296 | -0.0059067 | 0 | -165.4292 | 74.8016 | 0 | 14.5708 | -105.1984 | 1.0655 | 1.0572 | 1.0554 | 1.065 | 1.0544 | 1.0524 | -0.054963 | -120.3521 | 119.8291 | -0.064361 | -120.4292 | 119.8016
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5883e-11 | -1.4149e-10 | 2.5229e-10 | -5.8501e-11 | -1.7205e-11 | -9.2105e-12 | -2.306e-10 | 2.2022e-10 | 5.7459e-11 | -4.6057e-12 | -3.0411e-11 | -1.4028e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.065 | 1.0544 | 1.0524 | 1.065 | 1.0544 | 1.0524 | -0.064361 | -120.4292 | 119.8016 | -0.064361 | -120.4292 | 119.8016
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5883e-11 | -1.4149e-10 | 2.5229e-10 | -5.8501e-11 | -1.7205e-11 | -9.2105e-12 | -2.306e-10 | 2.2022e-10 | 5.7459e-11 | -4.6057e-12 | -3.0411e-11 | -1.4028e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.065 | 1.0544 | 1.0524 | 1.065 | 1.0544 | 1.0524 | -0.064361 | -120.4292 | 119.8016 | -0.064361 | -120.4292 | 119.8016
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1406e-10 | 2.1751e-10 | 7.5629e-10 | -3.3609e-10 | -2.4667e-10 | -7.051e-10 | -3.1221e-10 | 3.5801e-10 | 7.3554e-11 | 2.6568e-10 | -3.1569e-10 | -6.9436e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0671 | 1.0654 | 1.0646 | 1.0671 | 1.0654 | 1.0646 | -0.026827 | -120.1232 | 119.9107 | -0.026827 | -120.1232 | 119.9107

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.036074 | 0.036002 | 0 | 0.036074 | 0.036002 | 0 | 0.0083308 | 0.0083144 | 0 | 0.0083308 | 0.0083144 | -2.6679e-11 | 0.0065392 | 0.0065434 | -7.0252e-12 | -0.006531 | -0.0065278 | -1.1247e-09 | 0.0066094 | 0.0065684 | 1.0448e-09 | -0.0065837 | -0.0065465 | 0 | -165.435 | 74.7974 | 0 | 14.565 | -105.2026 | 1.1179 | 1.116 | 1.1151 | 1.1173 | 1.1132 | 1.1119 | -0.028087 | -120.129 | 119.9065 | -0.037455 | -120.2049 | 119.8794
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8795e-10 | 1.9285e-10 | 7.2371e-10 | -3.1328e-10 | -2.2636e-10 | -6.6487e-10 | -3.0766e-10 | 3.5274e-10 | 7.2454e-11 | 2.5418e-10 | -3.0409e-10 | -6.7721e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3996e-10 | 1.607e-10 | 6.0309e-10 | -2.6529e-10 | -1.9422e-10 | -5.4425e-10 | -2.5639e-10 | 2.9395e-10 | 6.0379e-11 | 2.029e-10 | -2.453e-10 | -5.5645e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4398e-10 | 9.6423e-11 | 3.6186e-10 | -1.693e-10 | -1.2994e-10 | -3.0301e-10 | -1.5383e-10 | 1.7637e-10 | 3.6227e-11 | 1.0034e-10 | -1.2772e-10 | -3.1494e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7992e-11 | 3.2141e-11 | 1.2062e-10 | -7.3316e-11 | -6.5659e-11 | -6.1776e-11 | -5.1277e-11 | 5.879e-11 | 1.2076e-11 | -2.2103e-12 | -1.0137e-11 | -7.3424e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5985e-11 | 6.4282e-11 | 2.4124e-10 | -1.2131e-10 | -9.78e-11 | -1.824e-10 | -1.0255e-10 | 1.1758e-10 | 2.4151e-11 | 4.9067e-11 | -6.8927e-11 | -1.9418e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7992e-11 | 3.2141e-11 | 1.2062e-10 | -7.3316e-11 | -6.5659e-11 | -6.1776e-11 | -5.1277e-11 | 5.879e-11 | 1.2076e-11 | -2.2103e-12 | -1.0137e-11 | -7.3424e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1325e-10 | 9.7734e-11 | 1.8712e-10 | -1.3923e-10 | -1.3145e-10 | -1.2743e-10 | -2.6786e-11 | 8.4751e-11 | 3.6911e-11 | -2.7306e-11 | -3.5232e-11 | -3.2438e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1335 | 1.1316 | 1.1307 | 1.1335 | 1.1316 | 1.1307 | -0.34222 | -120.4423 | 119.5925 | -0.34222 | -120.4423 | 119.5925
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7992e-11 | 3.2141e-11 | 1.2062e-10 | -7.3316e-11 | -6.5659e-11 | -6.1776e-11 | -5.1277e-11 | 5.879e-11 | 1.2076e-11 | -2.2103e-12 | -1.0137e-11 | -7.3424e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8394e-10 | 2.5713e-10 | 9.6495e-10 | -4.0926e-10 | -2.9065e-10 | -9.0611e-10 | -4.1022e-10 | 4.7032e-10 | 9.6606e-11 | 3.5673e-10 | -4.2167e-10 | -9.1872e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065
Line2_1_4 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0037534 | -0.0038255 | -0.0037948 | 0.0040534 | 0.0041255 | 0.0040948 | -0.044558 | -0.044477 | -0.044443 | 0.045158 | 0.045077 | 0.045043 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1179 | 1.116 | 1.1151 | 1.1335 | 1.1316 | 1.1307 | -0.028087 | -120.129 | 119.9065 | -0.34222 | -120.4423 | 119.5925
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5985e-11 | 6.4282e-11 | 2.4124e-10 | -1.2131e-10 | -9.78e-11 | -1.824e-10 | -1.0255e-10 | 1.1758e-10 | 2.4151e-11 | 4.9067e-11 | -6.8927e-11 | -1.9418e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065
Line4_2_6 | 0 | 0.036074 | 0.036002 | 0 | 0.036074 | 0.036002 | 0 | 0.0083308 | 0.0083144 | 0 | 0.0083308 | 0.0083144 | -6.3985e-11 | 0.006531 | 0.0065278 | 1.3145e-11 | -0.0065229 | -0.0065122 | -1.0477e-09 | 0.0065837 | 0.0065465 | 9.1598e-10 | -0.006558 | -0.0065246 | 0 | -165.435 | 74.7974 | 0 | 14.565 | -105.2026 | 1.1173 | 1.1132 | 1.1119 | 1.1168 | 1.1103 | 1.1087 | -0.037455 | -120.2049 | 119.8794 | -0.046832 | -120.2812 | 119.8522
Line5_6_7 | 0 | 0.036074 | 0.036002 | 0 | 0.036074 | 0.036002 | 0 | 0.0083308 | 0.0083144 | 0 | 0.0083308 | 0.0083144 | -8.185e-11 | 0.0065229 | 0.0065122 | 1.3876e-11 | -0.0065147 | -0.0064965 | -9.1966e-10 | 0.006558 | 0.0065246 | 7.3624e-10 | -0.0065322 | -0.0065028 | 0 | -165.435 | 74.7974 | 0 | 14.565 | -105.2026 | 1.1168 | 1.1103 | 1.1087 | 1.1162 | 1.1074 | 1.1055 | -0.046832 | -120.2812 | 119.8522 | -0.056219 | -120.3579 | 119.8249
Line6_7_8 | 0 | 0.036074 | 0.036002 | 0 | 0.036074 | 0.036002 | 0 | 0.0083308 | 0.0083144 | 0 | 0.0083308 | 0.0083144 | -8.028e-11 | 0.0065147 | 0.0064965 | -4.8274e-12 | -0.0065065 | -0.0064809 | -7.4066e-10 | 0.0065322 | 0.0065028 | 5.0563e-10 | -0.0065065 | -0.0064809 | 0 | -165.435 | 74.7974 | 0 | 14.565 | -105.2026 | 1.1162 | 1.1074 | 1.1055 | 1.1157 | 1.1045 | 1.1023 | -0.056219 | -120.3579 | 119.8249 | -0.065614 | -120.435 | 119.7974
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9639e-11 | -1.5717e-10 | 2.7888e-10 | -6.4105e-11 | -1.8452e-11 | -9.5105e-12 | -2.5539e-10 | 2.443e-10 | 6.3579e-11 | -5.1532e-12 | -3.3824e-11 | -1.5721e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1157 | 1.1045 | 1.1023 | 1.1157 | 1.1045 | 1.1023 | -0.065614 | -120.435 | 119.7974 | -0.065614 | -120.435 | 119.7974
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9639e-11 | -1.5717e-10 | 2.7888e-10 | -6.4105e-11 | -1.8452e-11 | -9.5105e-12 | -2.5539e-10 | 2.443e-10 | 6.3579e-11 | -5.1532e-12 | -3.3824e-11 | -1.5721e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1157 | 1.1045 | 1.1023 | 1.1157 | 1.1045 | 1.1023 | -0.065614 | -120.435 | 119.7974 | -0.065614 | -120.435 | 119.7974
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3595e-10 | 2.2499e-10 | 8.4433e-10 | -3.6127e-10 | -2.585e-10 | -7.8549e-10 | -3.5894e-10 | 4.1153e-10 | 8.453e-11 | 3.0545e-10 | -3.6288e-10 | -7.9797e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.116 | 1.1151 | 1.1179 | 1.116 | 1.1151 | -0.028087 | -120.129 | 119.9065 | -0.028087 | -120.129 | 119.9065

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.9373 | 1.8965 | 0 | 1.9373 | 1.8965 | 0 | 0.44739 | 0.43799 | 0 | 0.44739 | 0.43799 | -7.2216e-09 | 0.19893 | 0.28577 | 5.5706e-09 | -0.1492 | -0.21433 | -7.952e-08 | 0.30413 | 0.20076 | 7.0471e-08 | -0.2281 | -0.15057 | 0 | 177.0251 | 78.2735 | 0 | -2.9749 | -101.7265 | 0.91889 | 0.8123 | 0.79739 | 0.86904 | 0.60922 | 0.59804 | -2.1342 | -126.1629 | 113.3627 | -1.9425 | -126.1629 | 113.3627
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.7796e-09 | -1.2476e-08 | 1.4712e-08 | 6.5856e-09 | 1.0791e-08 | -1.1832e-08 | -1.7927e-08 | 1.6293e-08 | 3.2785e-09 | 1.482e-08 | -1.3881e-08 | -3.0531e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.483e-09 | -1.0397e-08 | 1.226e-08 | 5.289e-09 | 8.7112e-09 | -9.3804e-09 | -1.4939e-08 | 1.3578e-08 | 2.7321e-09 | 1.1832e-08 | -1.1166e-08 | -2.5067e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8898e-09 | -6.2381e-09 | 7.356e-09 | 2.6958e-09 | 4.5525e-09 | -4.4764e-09 | -8.9634e-09 | 8.1466e-09 | 1.6393e-09 | 5.8564e-09 | -5.7348e-09 | -1.4139e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2966e-09 | -2.0794e-09 | 2.452e-09 | 1.0258e-10 | 3.9379e-10 | 4.2759e-10 | -2.9878e-09 | 2.7155e-09 | 5.4642e-10 | -1.192e-10 | -3.0376e-10 | -3.2104e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5932e-09 | -4.1587e-09 | 4.904e-09 | 1.3992e-09 | 2.4731e-09 | -2.0244e-09 | -5.9756e-09 | 5.431e-09 | 1.0928e-09 | 2.8686e-09 | -3.0193e-09 | -8.6746e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2966e-09 | -2.0794e-09 | 2.452e-09 | 1.0258e-10 | 3.9379e-10 | 4.2759e-10 | -2.9878e-09 | 2.7155e-09 | 5.4642e-10 | -1.192e-10 | -3.0376e-10 | -3.2104e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2966e-09 | -2.0794e-09 | 2.452e-09 | 1.0258e-10 | 3.9379e-10 | 4.2759e-10 | -2.9878e-09 | 2.7155e-09 | 5.4642e-10 | -1.192e-10 | -3.0376e-10 | -3.2104e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2966e-09 | -2.0794e-09 | 2.452e-09 | 1.0258e-10 | 3.9379e-10 | 4.2759e-10 | -2.9878e-09 | 2.7155e-09 | 5.4642e-10 | -1.192e-10 | -3.0376e-10 | -3.2104e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0373e-08 | -1.6635e-08 | 1.9616e-08 | 9.1788e-09 | 1.4949e-08 | -1.6736e-08 | -2.3902e-08 | 2.1724e-08 | 4.3714e-09 | 2.0795e-08 | -1.9312e-08 | -4.146e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5932e-09 | -4.1587e-09 | 4.904e-09 | 1.3992e-09 | 2.4731e-09 | -2.0244e-09 | -5.9756e-09 | 5.431e-09 | 1.0928e-09 | 2.8686e-09 | -3.0193e-09 | -8.6746e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5932e-09 | -4.1587e-09 | 4.904e-09 | 1.3992e-09 | 2.4731e-09 | -2.0244e-09 | -5.9756e-09 | 5.431e-09 | 1.0928e-09 | 2.8686e-09 | -3.0193e-09 | -8.6746e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line4_2_6 | 0 | 1.9373 | 1.8965 | 0 | 1.9373 | 1.8965 | 0 | 0.44739 | 0.43799 | 0 | 0.44739 | 0.43799 | -5.3143e-09 | 0.1492 | 0.21433 | 4.0508e-09 | -0.099465 | -0.14289 | -7.0573e-08 | 0.2281 | 0.15057 | 5.8635e-08 | -0.15207 | -0.10038 | 0 | 177.0251 | 78.2735 | 0 | -2.9749 | -101.7265 | 0.86904 | 0.60922 | 0.59804 | 0.81919 | 0.40615 | 0.39869 | -1.9425 | -126.1629 | 113.3627 | -1.7274 | -126.1629 | 113.3627
Line5_6_7 | 0 | 1.9373 | 1.8965 | 0 | 1.9373 | 1.8965 | 0 | 0.44739 | 0.43799 | 0 | 0.44739 | 0.43799 | -3.6592e-09 | 0.099465 | 0.14289 | 2.7923e-09 | -0.049732 | -0.071443 | -5.8721e-08 | 0.15207 | 0.10038 | 4.4522e-08 | -0.076034 | -0.050191 | 0 | 177.0251 | 78.2735 | 0 | -2.9749 | -101.7265 | 0.81919 | 0.40615 | 0.39869 | 0.76935 | 0.20307 | 0.19935 | -1.7274 | -126.1629 | 113.3627 | -1.4845 | -126.1629 | 113.3627
Line6_7_8 | 0 | 1.9373 | 1.8965 | 0 | 1.9373 | 1.8965 | 0 | 0.44739 | 0.43799 | 0 | 0.44739 | 0.43799 | -2.2836e-09 | 0.049732 | 0.071443 | 1.8224e-09 | -2.8296e-14 | -3.1093e-14 | -4.4591e-08 | 0.076034 | 0.050191 | 2.8757e-08 | 1.7131e-14 | 3.5188e-14 | 0 | 177.0251 | 78.2735 | 0 | -2.9749 | -101.7265 | 0.76935 | 0.20307 | 0.19935 | 0.71954 | 0 | 0 | -1.4845 | -126.1629 | 113.3627 | -1.2079 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0748e-10 | 8.2694e-22 | 1.1095e-21 | 6.0748e-10 | 5.9593e-18 | -4.2139e-18 | -1.4405e-08 | 1.5033e-21 | -1.4741e-21 | -5.2835e-11 | 1.3541e-17 | 1.4322e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71954 | 0 | 0 | 0.71954 | 0 | 0 | -1.2079 | 0 | 0 | -1.2079 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.0748e-10 | 8.2694e-22 | 1.1095e-21 | 6.0748e-10 | 5.9593e-18 | -4.2139e-18 | -1.4405e-08 | 1.5033e-21 | -1.4741e-21 | -5.2835e-11 | 1.3541e-17 | 1.4322e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71954 | 0 | 0 | 0.71954 | 0 | 0 | -1.2079 | 0 | 0 | -1.2079 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.0762e-09 | -1.4556e-08 | 1.7164e-08 | 7.8822e-09 | 1.287e-08 | -1.4284e-08 | -2.0915e-08 | 1.9009e-08 | 3.8249e-09 | 1.7808e-08 | -1.6597e-08 | -3.5996e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91889 | 0.8123 | 0.79739 | 0.91889 | 0.8123 | 0.79739 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 1.8353 | 1.7967 | 0 | 1.8353 | 1.7967 | 0 | 0.42384 | 0.41494 | 0 | 0.42384 | 0.41494 | -6.4814e-09 | 0.17854 | 0.25648 | 4.9996e-09 | -0.13391 | -0.19236 | -7.137e-08 | 0.27296 | 0.18019 | 6.3248e-08 | -0.20472 | -0.13514 | 0 | 177.0251 | 78.2735 | 0 | -2.9749 | -101.7265 | 0.87053 | 0.76954 | 0.75542 | 0.8233 | 0.57716 | 0.56656 | -2.1342 | -126.1629 | 113.3627 | -1.9425 | -126.1629 | 113.3627
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.9822e-09 | -1.1197e-08 | 1.3204e-08 | 5.9106e-09 | 9.6846e-09 | -1.062e-08 | -1.6089e-08 | 1.4623e-08 | 2.9425e-09 | 1.3301e-08 | -1.2459e-08 | -2.7402e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8185e-09 | -9.3312e-09 | 1.1003e-08 | 4.7469e-09 | 7.8184e-09 | -8.419e-09 | -1.3408e-08 | 1.2186e-08 | 2.4521e-09 | 1.0619e-08 | -1.0021e-08 | -2.2498e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4911e-09 | -5.5987e-09 | 6.6021e-09 | 2.4195e-09 | 4.0859e-09 | -4.0176e-09 | -8.0447e-09 | 7.3116e-09 | 1.4712e-09 | 5.2562e-09 | -5.147e-09 | -1.269e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1637e-09 | -1.8662e-09 | 2.2007e-09 | 9.2068e-11 | 3.5343e-10 | 3.8376e-10 | -2.6816e-09 | 2.4372e-09 | 4.9041e-10 | -1.0698e-10 | -2.7263e-10 | -2.8814e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3274e-09 | -3.7325e-09 | 4.4014e-09 | 1.2558e-09 | 2.2197e-09 | -1.8169e-09 | -5.3631e-09 | 4.8744e-09 | 9.8083e-10 | 2.5746e-09 | -2.7098e-09 | -7.7855e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1637e-09 | -1.8662e-09 | 2.2007e-09 | 9.2068e-11 | 3.5343e-10 | 3.8376e-10 | -2.6816e-09 | 2.4372e-09 | 4.9041e-10 | -1.0698e-10 | -2.7263e-10 | -2.8814e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1637e-09 | -1.8662e-09 | 2.2007e-09 | 9.2068e-11 | 3.5343e-10 | 3.8376e-10 | -2.6816e-09 | 2.4372e-09 | 4.9041e-10 | -1.0698e-10 | -2.7263e-10 | -2.8814e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1637e-09 | -1.8662e-09 | 2.2007e-09 | 9.2068e-11 | 3.5343e-10 | 3.8376e-10 | -2.6816e-09 | 2.4372e-09 | 4.9041e-10 | -1.0698e-10 | -2.7263e-10 | -2.8814e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.3096e-09 | -1.493e-08 | 1.7606e-08 | 8.238e-09 | 1.3417e-08 | -1.5021e-08 | -2.1453e-08 | 1.9498e-08 | 3.9233e-09 | 1.8664e-08 | -1.7333e-08 | -3.721e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3274e-09 | -3.7325e-09 | 4.4014e-09 | 1.2558e-09 | 2.2197e-09 | -1.8169e-09 | -5.3631e-09 | 4.8744e-09 | 9.8083e-10 | 2.5746e-09 | -2.7098e-09 | -7.7855e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.3274e-09 | -3.7325e-09 | 4.4014e-09 | 1.2558e-09 | 2.2197e-09 | -1.8169e-09 | -5.3631e-09 | 4.8744e-09 | 9.8083e-10 | 2.5746e-09 | -2.7098e-09 | -7.7855e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627
Line4_2_6 | 0 | 1.8353 | 1.7967 | 0 | 1.8353 | 1.7967 | 0 | 0.42384 | 0.41494 | 0 | 0.42384 | 0.41494 | -4.7697e-09 | 0.13391 | 0.19236 | 3.6356e-09 | -0.08927 | -0.12824 | -6.334e-08 | 0.20472 | 0.13514 | 5.2626e-08 | -0.13648 | -0.090094 | 0 | 177.0251 | 78.2735 | 0 | -2.9749 | -101.7265 | 0.8233 | 0.57716 | 0.56656 | 0.77607 | 0.38477 | 0.37771 | -1.9425 | -126.1629 | 113.3627 | -1.7274 | -126.1629 | 113.3627
Line5_6_7 | 0 | 1.8353 | 1.7967 | 0 | 1.8353 | 1.7967 | 0 | 0.42384 | 0.41494 | 0 | 0.42384 | 0.41494 | -3.2842e-09 | 0.08927 | 0.12824 | 2.5061e-09 | -0.044635 | -0.064121 | -5.2703e-08 | 0.13648 | 0.090094 | 3.9959e-08 | -0.068241 | -0.045047 | 0 | 177.0251 | 78.2735 | 0 | -2.9749 | -101.7265 | 0.77607 | 0.38477 | 0.37771 | 0.72886 | 0.19239 | 0.18885 | -1.7274 | -126.1629 | 113.3627 | -1.4845 | -126.1629 | 113.3627
Line6_7_8 | 0 | 1.8353 | 1.7967 | 0 | 1.8353 | 1.7967 | 0 | 0.42384 | 0.41494 | 0 | 0.42384 | 0.41494 | -2.0495e-09 | 0.044635 | 0.064121 | 1.6356e-09 | -2.5439e-14 | -2.7853e-14 | -4.0021e-08 | 0.068241 | 0.045047 | 2.581e-08 | 1.5311e-14 | 3.1505e-14 | 0 | 177.0251 | 78.2735 | 0 | -2.9749 | -101.7265 | 0.72886 | 0.19239 | 0.18885 | 0.68167 | 0 | 0 | -1.4845 | -126.1629 | 113.3627 | -1.2079 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4521e-10 | 7.3876e-22 | 9.939e-22 | 5.4521e-10 | 5.3485e-18 | -3.782e-18 | -1.2929e-08 | 1.3514e-21 | -1.3199e-21 | -4.742e-11 | 1.2153e-17 | 1.2855e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68167 | 0 | 0 | 0.68167 | 0 | 0 | -1.2079 | 0 | 0 | -1.2079 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4521e-10 | 7.3876e-22 | 9.939e-22 | 5.4521e-10 | 5.3485e-18 | -3.782e-18 | -1.2929e-08 | 1.3514e-21 | -1.3199e-21 | -4.742e-11 | 1.2153e-17 | 1.2855e-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68167 | 0 | 0 | 0.68167 | 0 | 0 | -1.2079 | 0 | 0 | -1.2079 | 0 | 0
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1459e-09 | -1.3064e-08 | 1.5405e-08 | 7.0743e-09 | 1.1551e-08 | -1.282e-08 | -1.8771e-08 | 1.706e-08 | 3.4329e-09 | 1.5982e-08 | -1.4896e-08 | -3.2306e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87053 | 0.76954 | 0.75542 | 0.87053 | 0.76954 | 0.75542 | -2.1342 | -126.1629 | 113.3627 | -2.1342 | -126.1629 | 113.3627

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.030528 | 0.0305 | 0 | 0.030528 | 0.0305 | 0 | 0.0070502 | 0.0070437 | 0 | 0.0070502 | 0.0070437 | -1.697e-10 | 0.0047147 | 0.0047275 | 1.5097e-10 | -0.004701 | -0.0047085 | -9.9881e-10 | 0.0047385 | 0.0047091 | 9.3569e-10 | -0.0047189 | -0.0046947 | 0 | -165.2726 | 75.0187 | 0 | 14.7274 | -104.9813 | 0.94966 | 0.94812 | 0.94733 | 0.94905 | 0.94477 | 0.94397 | -0.027868 | -120.1279 | 119.9069 | -0.028589 | -120.1637 | 119.9345
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1607e-10 | -1.822e-10 | 1.9641e-10 | 9.7909e-11 | 1.5837e-10 | -1.5441e-10 | -2.1911e-10 | 2.5292e-10 | 5.1832e-11 | 1.8098e-10 | -2.1814e-10 | -4.8556e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.6729e-11 | -1.5184e-10 | 1.6367e-10 | 7.8563e-11 | 1.28e-10 | -1.2167e-10 | -1.8259e-10 | 2.1076e-10 | 4.3193e-11 | 1.4446e-10 | -1.7598e-10 | -3.9917e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8037e-11 | -9.1101e-11 | 9.8205e-11 | 3.9872e-11 | 6.7264e-11 | -5.6203e-11 | -1.0955e-10 | 1.2646e-10 | 2.5916e-11 | 7.1427e-11 | -9.1678e-11 | -2.264e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9346e-11 | -3.0367e-11 | 3.2735e-11 | 1.1802e-12 | 6.5303e-12 | 9.2673e-12 | -3.6518e-11 | 4.2153e-11 | 8.6386e-12 | -1.609e-12 | -7.3724e-12 | -5.3628e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8691e-11 | -6.0734e-11 | 6.547e-11 | 2.0526e-11 | 3.6897e-11 | -2.3468e-11 | -7.3036e-11 | 8.4306e-11 | 1.7277e-11 | 3.4909e-11 | -4.9525e-11 | -1.4001e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9346e-11 | -3.0367e-11 | 3.2735e-11 | 1.1802e-12 | 6.5303e-12 | 9.2673e-12 | -3.6518e-11 | 4.2153e-11 | 8.6386e-12 | -1.609e-12 | -7.3724e-12 | -5.3628e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9346e-11 | -3.0367e-11 | 3.2735e-11 | 1.1802e-12 | 6.5303e-12 | 9.2673e-12 | -3.6518e-11 | 4.2153e-11 | 8.6386e-12 | -1.609e-12 | -7.3724e-12 | -5.3628e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9346e-11 | -3.0367e-11 | 3.2735e-11 | 1.1802e-12 | 6.5303e-12 | 9.2673e-12 | -3.6518e-11 | 4.2153e-11 | 8.6386e-12 | -1.609e-12 | -7.3724e-12 | -5.3628e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5477e-10 | -2.4294e-10 | 2.6188e-10 | 1.366e-10 | 2.191e-10 | -2.1988e-10 | -2.9215e-10 | 3.3722e-10 | 6.9109e-11 | 2.5402e-10 | -3.0244e-10 | -6.5833e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8691e-11 | -6.0734e-11 | 6.547e-11 | 2.0526e-11 | 3.6897e-11 | -2.3468e-11 | -7.3036e-11 | 8.4306e-11 | 1.7277e-11 | 3.4909e-11 | -4.9525e-11 | -1.4001e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.8691e-11 | -6.0734e-11 | 6.547e-11 | 2.0526e-11 | 3.6897e-11 | -2.3468e-11 | -7.3036e-11 | 8.4306e-11 | 1.7277e-11 | 3.4909e-11 | -4.9525e-11 | -1.4001e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line4_2_6 | 0 | 0.030528 | 0.0305 | 0 | 0.030528 | 0.0305 | 0 | 0.0070502 | 0.0070437 | 0 | 0.0070502 | 0.0070437 | -1.4766e-10 | 0.004701 | 0.0047085 | 1.2801e-10 | -0.0046873 | -0.0046894 | -9.3734e-10 | 0.0047189 | 0.0046947 | 8.2558e-10 | -0.0046992 | -0.0046802 | 0 | -165.2726 | 75.0187 | 0 | 14.7274 | -104.9813 | 0.94905 | 0.94477 | 0.94397 | 0.94843 | 0.94143 | 0.9406 | -0.028589 | -120.1637 | 119.9345 | -0.029311 | -120.1997 | 119.9624
Line5_6_7 | 0 | 0.030528 | 0.0305 | 0 | 0.030528 | 0.0305 | 0 | 0.0070502 | 0.0070437 | 0 | 0.0070502 | 0.0070437 | -1.2257e-10 | 0.0046873 | 0.0046894 | 1.0199e-10 | -0.0046736 | -0.0046704 | -8.2727e-10 | 0.0046992 | 0.0046802 | 6.6697e-10 | -0.0046796 | -0.0046657 | 0 | -165.2726 | 75.0187 | 0 | 14.7274 | -104.9813 | 0.94843 | 0.94143 | 0.9406 | 0.94782 | 0.93808 | 0.93724 | -0.029311 | -120.1997 | 119.9624 | -0.030033 | -120.236 | 119.9904
Line6_7_8 | 0 | 0.030528 | 0.0305 | 0 | 0.030528 | 0.0305 | 0 | 0.0070502 | 0.0070437 | 0 | 0.0070502 | 0.0070437 | -9.4422e-11 | 0.0046736 | 0.0046704 | 7.2924e-11 | -0.0046599 | -0.0046513 | -6.687e-10 | 0.0046796 | 0.0046657 | 4.5996e-10 | -0.0046599 | -0.0046513 | 0 | -165.2726 | 75.0187 | 0 | 14.7274 | -104.9813 | 0.94782 | 0.93808 | 0.93724 | 0.94721 | 0.93474 | 0.93387 | -0.030033 | -120.236 | 119.9904 | -0.030757 | -120.2726 | 120.0187
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1615e-11 | -2.3971e-10 | 1.5413e-10 | 9.6946e-12 | 5.2278e-11 | 5.5224e-11 | -2.3086e-10 | 1.498e-10 | 9.5086e-11 | -1.7712e-12 | -1.5489e-11 | 1.0589e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94721 | 0.93474 | 0.93387 | 0.94721 | 0.93474 | 0.93387 | -0.030757 | -120.2726 | 120.0187 | -0.030757 | -120.2726 | 120.0187
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1615e-11 | -2.3971e-10 | 1.5413e-10 | 9.6946e-12 | 5.2278e-11 | 5.5224e-11 | -2.3086e-10 | 1.498e-10 | 9.5086e-11 | -1.7712e-12 | -1.5489e-11 | 1.0589e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94721 | 0.93474 | 0.93387 | 0.94721 | 0.93474 | 0.93387 | -0.030757 | -120.2726 | 120.0187 | -0.030757 | -120.2726 | 120.0187
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3542e-10 | -2.1257e-10 | 2.2914e-10 | 1.1725e-10 | 1.8873e-10 | -1.8714e-10 | -2.5563e-10 | 2.9507e-10 | 6.047e-11 | 2.175e-10 | -2.6029e-10 | -5.7194e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.94812 | 0.94733 | 0.94966 | 0.94812 | 0.94733 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0.028922 | 0.028895 | 0 | 0.028922 | 0.028895 | 0 | 0.0066792 | 0.006673 | 0 | 0.0066792 | 0.006673 | -1.5231e-10 | 0.0042314 | 0.004243 | 1.355e-10 | -0.0042192 | -0.0042259 | -8.9644e-10 | 0.0042529 | 0.0042265 | 8.3979e-10 | -0.0042352 | -0.0042135 | 0 | -165.2726 | 75.0187 | 0 | 14.7274 | -104.9813 | 0.89968 | 0.89822 | 0.89747 | 0.8991 | 0.89505 | 0.89428 | -0.027868 | -120.1279 | 119.9069 | -0.028589 | -120.1637 | 119.9345
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0418e-10 | -1.6353e-10 | 1.7628e-10 | 8.7874e-11 | 1.4213e-10 | -1.3858e-10 | -1.9665e-10 | 2.27e-10 | 4.6519e-11 | 1.6243e-10 | -1.9578e-10 | -4.3579e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.6815e-11 | -1.3627e-10 | 1.469e-10 | 7.0511e-11 | 1.1488e-10 | -1.092e-10 | -1.6388e-10 | 1.8916e-10 | 3.8766e-11 | 1.2966e-10 | -1.5795e-10 | -3.5826e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2089e-11 | -8.1764e-11 | 8.814e-11 | 3.5785e-11 | 6.037e-11 | -5.0442e-11 | -9.8326e-11 | 1.135e-10 | 2.326e-11 | 6.4107e-11 | -8.2282e-11 | -2.032e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7363e-11 | -2.7255e-11 | 2.938e-11 | 1.0593e-12 | 5.861e-12 | 8.3175e-12 | -3.2775e-11 | 3.7833e-11 | 7.7532e-12 | -1.4441e-12 | -6.6168e-12 | -4.8132e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4726e-11 | -5.4509e-11 | 5.876e-11 | 1.8422e-11 | 3.3116e-11 | -2.1062e-11 | -6.5551e-11 | 7.5665e-11 | 1.5506e-11 | 3.1331e-11 | -4.4449e-11 | -1.2566e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7363e-11 | -2.7255e-11 | 2.938e-11 | 1.0593e-12 | 5.861e-12 | 8.3175e-12 | -3.2775e-11 | 3.7833e-11 | 7.7532e-12 | -1.4441e-12 | -6.6168e-12 | -4.8132e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7363e-11 | -2.7255e-11 | 2.938e-11 | 1.0593e-12 | 5.861e-12 | 8.3175e-12 | -3.2775e-11 | 3.7833e-11 | 7.7532e-12 | -1.4441e-12 | -6.6168e-12 | -4.8132e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7363e-11 | -2.7255e-11 | 2.938e-11 | 1.0593e-12 | 5.861e-12 | 8.3175e-12 | -3.2775e-11 | 3.7833e-11 | 7.7532e-12 | -1.4441e-12 | -6.6168e-12 | -4.8132e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.389e-10 | -2.1804e-10 | 2.3504e-10 | 1.226e-10 | 1.9664e-10 | -1.9734e-10 | -2.622e-10 | 3.0266e-10 | 6.2026e-11 | 2.2798e-10 | -2.7145e-10 | -5.9086e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line2_1_4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4726e-11 | -5.4509e-11 | 5.876e-11 | 1.8422e-11 | 3.3116e-11 | -2.1062e-11 | -6.5551e-11 | 7.5665e-11 | 1.5506e-11 | 3.1331e-11 | -4.4449e-11 | -1.2566e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4726e-11 | -5.4509e-11 | 5.876e-11 | 1.8422e-11 | 3.3116e-11 | -2.1062e-11 | -6.5551e-11 | 7.5665e-11 | 1.5506e-11 | 3.1331e-11 | -4.4449e-11 | -1.2566e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069
Line4_2_6 | 0 | 0.028922 | 0.028895 | 0 | 0.028922 | 0.028895 | 0 | 0.0066792 | 0.006673 | 0 | 0.0066792 | 0.006673 | -1.3253e-10 | 0.0042192 | 0.0042259 | 1.1489e-10 | -0.0042069 | -0.0042088 | -8.4127e-10 | 0.0042352 | 0.0042135 | 7.4096e-10 | -0.0042176 | -0.0042005 | 0 | -165.2726 | 75.0187 | 0 | 14.7274 | -104.9813 | 0.8991 | 0.89505 | 0.89428 | 0.89852 | 0.89188 | 0.8911 | -0.028589 | -120.1637 | 119.9345 | -0.029311 | -120.1997 | 119.9624
Line5_6_7 | 0 | 0.028922 | 0.028895 | 0 | 0.028922 | 0.028895 | 0 | 0.0066792 | 0.006673 | 0 | 0.0066792 | 0.006673 | -1.1001e-10 | 0.0042069 | 0.0042088 | 9.1539e-11 | -0.0041946 | -0.0041917 | -7.4248e-10 | 0.0042176 | 0.0042005 | 5.9861e-10 | -0.0041999 | -0.0041875 | 0 | -165.2726 | 75.0187 | 0 | 14.7274 | -104.9813 | 0.89852 | 0.89188 | 0.8911 | 0.89794 | 0.88871 | 0.88791 | -0.029311 | -120.1997 | 119.9624 | -0.030033 | -120.236 | 119.9904
Line6_7_8 | 0 | 0.028922 | 0.028895 | 0 | 0.028922 | 0.028895 | 0 | 0.0066792 | 0.006673 | 0 | 0.0066792 | 0.006673 | -8.4744e-11 | 0.0041946 | 0.0041917 | 6.545e-11 | -0.0041823 | -0.0041746 | -6.0016e-10 | 0.0041999 | 0.0041875 | 4.1282e-10 | -0.0041823 | -0.0041746 | 0 | -165.2726 | 75.0187 | 0 | 14.7274 | -104.9813 | 0.89794 | 0.88871 | 0.88791 | 0.89736 | 0.88554 | 0.88472 | -0.030033 | -120.236 | 119.9904 | -0.030757 | -120.2726 | 120.0187
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8374e-11 | -2.1514e-10 | 1.3833e-10 | 8.701e-12 | 4.692e-11 | 4.9564e-11 | -2.072e-10 | 1.3445e-10 | 8.534e-11 | -1.5896e-12 | -1.3901e-11 | 9.5039e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89736 | 0.88554 | 0.88472 | 0.89736 | 0.88554 | 0.88472 | -0.030757 | -120.2726 | 120.0187 | -0.030757 | -120.2726 | 120.0187
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.8374e-11 | -2.1514e-10 | 1.3833e-10 | 8.701e-12 | 4.692e-11 | 4.9564e-11 | -2.072e-10 | 1.3445e-10 | 8.534e-11 | -1.5896e-12 | -1.3901e-11 | 9.5039e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89736 | 0.88554 | 0.88472 | 0.89736 | 0.88554 | 0.88472 | -0.030757 | -120.2726 | 120.0187 | -0.030757 | -120.2726 | 120.0187
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2154e-10 | -1.9078e-10 | 2.0566e-10 | 1.0524e-10 | 1.6939e-10 | -1.6796e-10 | -2.2943e-10 | 2.6483e-10 | 5.4272e-11 | 1.9521e-10 | -2.3361e-10 | -5.1332e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.89822 | 0.89747 | 0.89968 | 0.89822 | 0.89747 | -0.027868 | -120.1279 | 119.9069 | -0.027868 | -120.1279 | 119.9069