## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.018715 | 0.019615 | -0.087124 | 0.088924 | 94.7872 | -85.2128 | 0.7426 | 0.75885 | -7.336 | -7.6518
Line10_11_12 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.020515 | 0.021415 | -0.090724 | 0.092524 | 94.7872 | -85.2128 | 0.77512 | 0.79142 | -7.9543 | -8.2444
Line11_12_13 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.021415 | 0.022315 | -0.092524 | 0.094324 | 94.7872 | -85.2128 | 0.79142 | 0.80773 | -8.2444 | -8.5228
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80773 | 0.80773 | -8.5228 | -8.5228
Line13_13_14 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.022315 | 0.023215 | -0.094324 | 0.096124 | 94.7872 | -85.2128 | 0.80773 | 0.82406 | -8.5228 | -8.7901
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80773 | 0.80773 | -8.5228 | -8.5228
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80773 | 0.80773 | -8.5228 | -8.5228
Line16_4_18 | 3.9212 | 3.9212 | 0 | 7.4206 | 2.7167 | 2.7167 | 0.46127 | -1e-07 | 0.92253 | -1e-07 | -70.8543 | 109.1457 | 0.37967 | 0 | -7.4193 | 0
Line17_5_19 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.019615 | 0.020515 | -0.088924 | 0.090724 | 94.7872 | -85.2128 | 0.75885 | 0.77512 | -7.6518 | -7.9543
Line1_1_3 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.018715 | 0.019615 | -0.087124 | 0.088924 | 94.7872 | -85.2128 | 0.7426 | 0.75885 | -7.336 | -7.6518
Line2_1_4 | 3.7483 | 3.7483 | 0 | 0 | 2.5969 | 2.5969 | 0.86506 | -0.44356 | 1.7236 | -0.88056 | -70.6837 | 109.3163 | 0.7426 | 0.37967 | -7.336 | -7.4193
Line3_1_5 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.018715 | 0.019615 | -0.087124 | 0.088924 | 94.7872 | -85.2128 | 0.7426 | 0.75885 | -7.336 | -7.6518
Line4_2_6 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.019615 | 0.020515 | -0.088924 | 0.090724 | 94.7872 | -85.2128 | 0.75885 | 0.77512 | -7.6518 | -7.9543
Line5_6_7 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.020515 | 0.021415 | -0.090724 | 0.092524 | 94.7872 | -85.2128 | 0.77512 | 0.79142 | -7.9543 | -8.2444
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79142 | 0.79142 | -8.2444 | -8.2444
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79142 | 0.79142 | -8.2444 | -8.2444
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79142 | 0.79142 | -8.2444 | -8.2444
Line9_3_11 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.019615 | 0.020515 | -0.088924 | 0.090724 | 94.7872 | -85.2128 | 0.75885 | 0.77512 | -7.6518 | -7.9543

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.019661 | 0.020561 | -0.089761 | 0.091561 | 94.7869 | -85.2131 | 0.76574 | 0.78201 | -7.5681 | -7.8698
Line10_11_12 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.021461 | 0.022361 | -0.093361 | 0.095161 | 94.7869 | -85.2131 | 0.7983 | 0.81461 | -8.1591 | -8.4368
Line11_12_13 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.022361 | 0.023261 | -0.095161 | 0.096961 | 94.7869 | -85.2131 | 0.81461 | 0.83093 | -8.4368 | -8.7037
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83093 | 0.83093 | -8.7037 | -8.7037
Line13_13_14 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.023261 | 0.024161 | -0.096961 | 0.098761 | 94.7869 | -85.2131 | 0.83093 | 0.84728 | -8.7037 | -8.9602
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83093 | 0.83093 | -8.7037 | -8.7037
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83093 | 0.83093 | -8.7037 | -8.7037
Line16_4_18 | 4.0407 | 4.0407 | 0 | 7.6729 | 2.7995 | 2.7995 | 0.48981 | -1e-07 | 0.97963 | -1e-07 | -71.0844 | 108.9156 | 0.39124 | 0 | -7.6495 | 0
Line17_5_19 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.020561 | 0.021461 | -0.091561 | 0.093361 | 94.7869 | -85.2131 | 0.78201 | 0.7983 | -7.8698 | -8.1591
Line1_1_3 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.019661 | 0.020561 | -0.089761 | 0.091561 | 94.7869 | -85.2131 | 0.76574 | 0.78201 | -7.5681 | -7.8698
Line2_1_4 | 3.8679 | 3.8679 | 0 | 0 | 2.6797 | 2.6797 | 0.92039 | -0.47158 | 1.834 | -0.93636 | -70.9181 | 109.0819 | 0.76574 | 0.39124 | -7.5681 | -7.6495
Line3_1_5 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.019661 | 0.020561 | -0.089761 | 0.091561 | 94.7869 | -85.2131 | 0.76574 | 0.78201 | -7.5681 | -7.8698
Line4_2_6 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.020561 | 0.021461 | -0.091561 | 0.093361 | 94.7869 | -85.2131 | 0.78201 | 0.7983 | -7.8698 | -8.1591
Line5_6_7 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.021461 | 0.022361 | -0.093361 | 0.095161 | 94.7869 | -85.2131 | 0.7983 | 0.81461 | -8.1591 | -8.4368
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81461 | 0.81461 | -8.4368 | -8.4368
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81461 | 0.81461 | -8.4368 | -8.4368
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81461 | 0.81461 | -8.4368 | -8.4368
Line9_3_11 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.020561 | 0.021461 | -0.091561 | 0.093361 | 94.7869 | -85.2131 | 0.78201 | 0.7983 | -7.8698 | -8.1591

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011082 | 0.011982 | -0.13355 | 0.13535 | 94.7872 | -85.2128 | 1.1167 | 1.1323 | 0.043555 | -0.27189
Line10_11_12 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.012882 | 0.013782 | -0.13715 | 0.13895 | 94.7872 | -85.2128 | 1.1479 | 1.1636 | -0.57875 | -0.87737
Line11_12_13 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.013782 | 0.014682 | -0.13895 | 0.14075 | 94.7872 | -85.2128 | 1.1636 | 1.1793 | -0.87737 | -1.1681
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1793 | 1.1793 | -1.1681 | -1.1681
Line13_13_14 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.014682 | 0.015582 | -0.14075 | 0.14255 | 94.7872 | -85.2128 | 1.1793 | 1.195 | -1.1681 | -1.4511
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1793 | 1.1793 | -1.1681 | -1.1681
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1793 | 1.1793 | -1.1681 | -1.1681
Line16_4_18 | 0.036789 | 0.036789 | 0 | 0.06962 | 0.025488 | 0.025488 | 0.020342 | -0.020301 | 0.020382 | -0.020301 | -45.2344 | 134.7656 | 1.1298 | 1.1264 | -0.17729 | -0.23442
Line17_5_19 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011982 | 0.012882 | -0.13535 | 0.13715 | 94.7872 | -85.2128 | 1.1323 | 1.1479 | -0.27189 | -0.57875
Line1_1_3 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011082 | 0.011982 | -0.13355 | 0.13535 | 94.7872 | -85.2128 | 1.1167 | 1.1323 | 0.043555 | -0.27189
Line2_1_4 | 0.14227 | 0.14227 | 0 | 0 | 0.098569 | 0.098569 | -0.015578 | 0.016185 | -0.10897 | 0.11018 | 98.1796 | -81.8204 | 1.1167 | 1.1298 | 0.043555 | -0.17729
Line3_1_5 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011082 | 0.011982 | -0.13355 | 0.13535 | 94.7872 | -85.2128 | 1.1167 | 1.1323 | 0.043555 | -0.27189
Line4_2_6 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011982 | 0.012882 | -0.13535 | 0.13715 | 94.7872 | -85.2128 | 1.1323 | 1.1479 | -0.27189 | -0.57875
Line5_6_7 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.012882 | 0.013782 | -0.13715 | 0.13895 | 94.7872 | -85.2128 | 1.1479 | 1.1636 | -0.57875 | -0.87737
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1636 | 1.1636 | -0.87737 | -0.87737
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1636 | 1.1636 | -0.87737 | -0.87737
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1636 | 1.1636 | -0.87737 | -0.87737
Line9_3_11 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011982 | 0.012882 | -0.13535 | 0.13715 | 94.7872 | -85.2128 | 1.1323 | 1.1479 | -0.27189 | -0.57875

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011631 | 0.012531 | -0.13989 | 0.14169 | 94.7869 | -85.2131 | 1.1697 | 1.1853 | 0.033934 | -0.26727
Line10_11_12 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.013431 | 0.014331 | -0.14349 | 0.14529 | 94.7869 | -85.2131 | 1.2009 | 1.2166 | -0.56065 | -0.84649
Line11_12_13 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.014331 | 0.015231 | -0.14529 | 0.14709 | 94.7869 | -85.2131 | 1.2166 | 1.2323 | -0.84649 | -1.1251
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2323 | 1.2323 | -1.1251 | -1.1251
Line13_13_14 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.015231 | 0.016131 | -0.14709 | 0.14889 | 94.7869 | -85.2131 | 1.2323 | 1.248 | -1.1251 | -1.3966
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2323 | 1.2323 | -1.1251 | -1.1251
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2323 | 1.2323 | -1.1251 | -1.1251
Line16_4_18 | 0.03851 | 0.03851 | 0 | 0.073126 | 0.02668 | 0.02668 | 0.022289 | -0.022245 | 0.022334 | -0.022245 | -45.2401 | 134.7599 | 1.1826 | 1.1791 | -0.18297 | -0.2401
Line17_5_19 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.012531 | 0.013431 | -0.14169 | 0.14349 | 94.7869 | -85.2131 | 1.1853 | 1.2009 | -0.26727 | -0.56065
Line1_1_3 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011631 | 0.012531 | -0.13989 | 0.14169 | 94.7869 | -85.2131 | 1.1697 | 1.1853 | 0.033934 | -0.26727
Line2_1_4 | 0.14099 | 0.14099 | 0 | 0 | 0.097684 | 0.097684 | -0.014756 | 0.015353 | -0.11331 | 0.1145 | 97.4539 | -82.5461 | 1.1697 | 1.1826 | 0.033934 | -0.18297
Line3_1_5 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.011631 | 0.012531 | -0.13989 | 0.14169 | 94.7869 | -85.2131 | 1.1697 | 1.1853 | 0.033934 | -0.26727
Line4_2_6 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.012531 | 0.013431 | -0.14169 | 0.14349 | 94.7869 | -85.2131 | 1.1853 | 1.2009 | -0.26727 | -0.56065
Line5_6_7 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.013431 | 0.014331 | -0.14349 | 0.14529 | 94.7869 | -85.2131 | 1.2009 | 1.2166 | -0.56065 | -0.84649
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2166 | 1.2166 | -0.84649 | -0.84649
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2166 | 1.2166 | -0.84649 | -0.84649
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2166 | 1.2166 | -0.84649 | -0.84649
Line9_3_11 | 0.1732 | 0.1732 | 0 | 0 | 0.12 | 0.12 | -0.012531 | 0.013431 | -0.14169 | 0.14349 | 94.7869 | -85.2131 | 1.1853 | 1.2009 | -0.26727 | -0.56065

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line16_4_18 | 2.8946 | 2.8946 | 0 | 4.7808 | 2.0055 | 2.0055 | 0.48263 | -1e-07 | 0.50274 | -1e-07 | -57.7717 | 122.2283 | 0.3475 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line2_1_4 | 2.8946 | 2.8946 | 0 | 0 | 2.0055 | 2.0055 | 0.96525 | -0.48263 | 1.0055 | -0.50274 | -57.7717 | 122.2283 | 0.695 | 0.3475 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 0.695 | -11.6026 | -11.6026

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line16_4_18 | 2.7423 | 2.7423 | 0 | 4.5292 | 1.8999 | 1.8999 | 0.43316 | -1e-07 | 0.45121 | -1e-07 | -57.7717 | 122.2283 | 0.32921 | 0 | -11.6026 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line2_1_4 | 2.7423 | 2.7423 | 0 | 0 | 1.8999 | 1.8999 | 0.86632 | -0.43316 | 0.90242 | -0.45121 | -57.7717 | 122.2283 | 0.65842 | 0.32921 | -11.6026 | -11.6026
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65842 | 0.65842 | -11.6026 | -11.6026

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line16_4_18 | 0.030706 | 0.030706 | 0 | 0.050714 | 0.021274 | 0.021274 | 0.014197 | -0.014143 | 0.014199 | -0.014143 | -45.1344 | 134.8656 | 0.94385 | 0.94017 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line2_1_4 | 0.030706 | 0.030706 | 0 | 0 | 0.021274 | 0.021274 | 0.014251 | -0.014197 | 0.014256 | -0.014199 | -45.1344 | 134.8656 | 0.94754 | 0.94385 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94754 | 0.94754 | -0.12527 | -0.12527

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line16_4_18 | 0.02909 | 0.02909 | 0 | 0.048045 | 0.020154 | 0.020154 | 0.012742 | -0.012693 | 0.012744 | -0.012693 | -45.1344 | 134.8656 | 0.89418 | 0.89069 | -0.1298 | -0.13436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line2_1_4 | 0.02909 | 0.02909 | 0 | 0 | 0.020154 | 0.020154 | 0.012791 | -0.012742 | 0.012795 | -0.012744 | -45.1344 | 134.8656 | 0.89767 | 0.89418 | -0.12527 | -0.1298
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89767 | 0.89767 | -0.12527 | -0.12527

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036085 | -0.012334 | 0.0011722 | 0.0039085 | 0.012634 | -0.00087224 | -0.044637 | -0.034079 | -0.031802 | 0.045237 | 0.034679 | 0.032402 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1196 | 0.90606 | 0.79558 | 1.1351 | 0.92272 | 0.81033 | 0.16542 | -135.109 | 126.8983 | -0.15091 | -135.2299 | 126.3292
Line10_11_12 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0042085 | -0.012934 | 0.00057224 | 0.0045085 | 0.013234 | -0.00027224 | -0.045837 | -0.035279 | -0.033002 | 0.046437 | 0.035879 | 0.033602 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1507 | 0.93938 | 0.82516 | 1.1664 | 0.95605 | 0.84007 | -0.45866 | -135.3465 | 125.7806 | -0.75817 | -135.4591 | 125.2514
Line11_12_13 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0045085 | -0.013234 | 0.00027224 | 0.0048085 | 0.013534 | 2.7756e-05 | -0.046437 | -0.035879 | -0.033602 | 0.047037 | 0.036479 | 0.034202 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1664 | 0.95605 | 0.84007 | 1.1821 | 0.97272 | 0.85504 | -0.75817 | -135.4591 | 125.2514 | -1.0497 | -135.5678 | 124.7407
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7193e-09 | -4.1476e-10 | -1.7999e-09 | -1.7193e-09 | 4.1476e-10 | 1.7999e-09 | 2.5012e-10 | 3.0152e-09 | -8.162e-10 | -2.5012e-10 | -3.0152e-09 | 8.162e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1821 | 0.97272 | 0.85504 | 1.1821 | 0.97272 | 0.85504 | -1.0497 | -135.5678 | 124.7407 | -1.0497 | -135.5678 | 124.7407
Line13_13_14 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0048085 | -0.013534 | -2.7754e-05 | 0.0051085 | 0.013834 | 0.00032775 | -0.047037 | -0.036479 | -0.034202 | 0.047637 | 0.037079 | 0.034802 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1821 | 0.97272 | 0.85504 | 1.1978 | 0.98939 | 0.87008 | -1.0497 | -135.5678 | 124.7407 | -1.3337 | -135.6729 | 124.2476
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1462e-09 | -2.7651e-10 | -1.1999e-09 | -1.1462e-09 | 2.7651e-10 | 1.1999e-09 | 1.6675e-10 | 2.0101e-09 | -5.4413e-10 | -1.6675e-10 | -2.0101e-09 | 5.4413e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1821 | 0.97272 | 0.85504 | 1.1821 | 0.97272 | 0.85504 | -1.0497 | -135.5678 | 124.7407 | -1.0497 | -135.5678 | 124.7407
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.731e-10 | -1.3825e-10 | -5.9997e-10 | -5.731e-10 | 1.3825e-10 | 5.9997e-10 | 8.3375e-11 | 1.0051e-09 | -2.7207e-10 | -8.3375e-11 | -1.0051e-09 | 2.7207e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1821 | 0.97272 | 0.85504 | 1.1821 | 0.97272 | 0.85504 | -1.0497 | -135.5678 | 124.7407 | -1.0497 | -135.5678 | 124.7407
Line16_4_18 | 0 | 3.3958 | 3.3958 | 0 | 3.3958 | 3.3958 | 0 | 0.78423 | 0.78423 | 0 | 0.78423 | 0.78423 | 3.5829e-10 | 0.53613 | -0.30549 | -3.5829e-10 | -0.42081 | 0.42081 | 1.3948e-16 | 0.084538 | 0.37673 | -2.6557e-16 | 0.1461 | -0.1461 | 0 | -160.8543 | 19.1457 | 0 | 19.1457 | -160.8543 | 1.136 | 0.69208 | 0.61847 | 1.136 | 0.56801 | 0.56801 | -4.5868e-06 | -151.8935 | 148.1848 | -4.5928e-06 | 180 | 180
Line17_5_19 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039085 | -0.012634 | 0.00087225 | 0.0042085 | 0.012934 | -0.00057225 | -0.045237 | -0.034679 | -0.032402 | 0.045837 | 0.035279 | 0.033002 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1351 | 0.92272 | 0.81033 | 1.1507 | 0.93938 | 0.82516 | -0.15091 | -135.2299 | 126.3292 | -0.45866 | -135.3465 | 125.7806
Line1_1_3 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036085 | -0.012334 | 0.0011722 | 0.0039085 | 0.012634 | -0.00087224 | -0.044637 | -0.034079 | -0.031802 | 0.045237 | 0.034679 | 0.032402 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1196 | 0.90606 | 0.79558 | 1.1351 | 0.92272 | 0.81033 | 0.16542 | -135.109 | 126.8983 | -0.15091 | -135.2299 | 126.3292
Line2_1_4 | 0.1732 | 3.2531 | 3.2415 | 0.1732 | 3.2531 | 3.2415 | 0.04 | 0.75128 | 0.74859 | 0.04 | 0.75128 | 0.74859 | -0.011807 | 0.6216 | -0.19497 | 0.012107 | -0.51577 | 0.30004 | -0.043198 | 0.27744 | 0.56274 | 0.043798 | -0.065781 | -0.3526 | 105.4524 | -159.1617 | 17.7888 | -74.5476 | 20.8383 | -162.2112 | 1.1196 | 0.90606 | 0.79558 | 1.136 | 0.69208 | 0.61847 | 0.16542 | -135.109 | 126.8983 | -4.5868e-06 | -151.8935 | 148.1848
Line3_1_5 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036085 | -0.012334 | 0.0011722 | 0.0039085 | 0.012634 | -0.00087225 | -0.044637 | -0.034079 | -0.031802 | 0.045237 | 0.034679 | 0.032402 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1196 | 0.90606 | 0.79558 | 1.1351 | 0.92272 | 0.81033 | 0.16542 | -135.109 | 126.8983 | -0.15091 | -135.2299 | 126.3292
Line4_2_6 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039085 | -0.012634 | 0.00087225 | 0.0042085 | 0.012934 | -0.00057225 | -0.045237 | -0.034679 | -0.032402 | 0.045837 | 0.035279 | 0.033002 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1351 | 0.92272 | 0.81033 | 1.1507 | 0.93938 | 0.82516 | -0.15091 | -135.2299 | 126.3292 | -0.45866 | -135.3465 | 125.7806
Line5_6_7 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0042085 | -0.012934 | 0.00057225 | 0.0045085 | 0.013234 | -0.00027225 | -0.045837 | -0.035279 | -0.033002 | 0.046437 | 0.035879 | 0.033602 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1507 | 0.93938 | 0.82516 | 1.1664 | 0.95605 | 0.84007 | -0.45866 | -135.3465 | 125.7806 | -0.75817 | -135.4591 | 125.2514
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4944e-09 | -5.8857e-10 | -1.8992e-09 | -1.4944e-09 | 5.8857e-10 | 1.8992e-09 | 1.7826e-10 | 2.9433e-09 | -8.8806e-10 | -1.7826e-10 | -2.9433e-09 | 8.8806e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1664 | 0.95605 | 0.84007 | 1.1664 | 0.95605 | 0.84007 | -0.75817 | -135.4591 | 125.2514 | -0.75817 | -135.4591 | 125.2514
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9813e-10 | -1.9619e-10 | -6.3307e-10 | -4.9813e-10 | 1.9619e-10 | 6.3307e-10 | 5.942e-11 | 9.8111e-10 | -2.9602e-10 | -5.942e-11 | -9.8111e-10 | 2.9602e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1664 | 0.95605 | 0.84007 | 1.1664 | 0.95605 | 0.84007 | -0.75817 | -135.4591 | 125.2514 | -0.75817 | -135.4591 | 125.2514
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9813e-10 | -1.9619e-10 | -6.3307e-10 | -4.9813e-10 | 1.9619e-10 | 6.3307e-10 | 5.942e-11 | 9.8111e-10 | -2.9602e-10 | -5.942e-11 | -9.8111e-10 | 2.9602e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1664 | 0.95605 | 0.84007 | 1.1664 | 0.95605 | 0.84007 | -0.75817 | -135.4591 | 125.2514 | -0.75817 | -135.4591 | 125.2514
Line9_3_11 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039085 | -0.012634 | 0.00087224 | 0.0042085 | 0.012934 | -0.00057224 | -0.045237 | -0.034679 | -0.032402 | 0.045837 | 0.035279 | 0.033002 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.1351 | 0.92272 | 0.81033 | 1.1507 | 0.93938 | 0.82516 | -0.15091 | -135.2299 | 126.3292 | -0.45866 | -135.3465 | 125.7806

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0037832 | -0.013154 | 0.0014315 | 0.0040832 | 0.013454 | -0.0011315 | -0.046762 | -0.03533 | -0.032931 | 0.047362 | 0.03593 | 0.033531 | 94.7868 | -25.213 | -145.2131 | -85.2132 | 154.787 | 34.7869 | 1.1729 | 0.94249 | 0.82405 | 1.1884 | 0.95916 | 0.83875 | 0.16146 | -135.6338 | 127.2759 | -0.14063 | -135.741 | 126.7195
Line10_11_12 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0043832 | -0.013754 | 0.00083146 | 0.0046832 | 0.014054 | -0.00053146 | -0.047962 | -0.03653 | -0.034131 | 0.048562 | 0.03713 | 0.034731 | 94.7868 | -25.213 | -145.2131 | -85.2132 | 154.787 | 34.7869 | 1.204 | 0.97584 | 0.85353 | 1.2197 | 0.99252 | 0.86838 | -0.43489 | -135.8446 | 126.1824 | -0.72162 | -135.9447 | 125.6636
Line11_12_13 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0046832 | -0.014054 | 0.00053146 | 0.0049832 | 0.014354 | -0.00023146 | -0.048562 | -0.03713 | -0.034731 | 0.049162 | 0.03773 | 0.035331 | 94.7868 | -25.213 | -145.2131 | -85.2132 | 154.787 | 34.7869 | 1.2197 | 0.99252 | 0.86838 | 1.2353 | 1.0092 | 0.88329 | -0.72162 | -135.9447 | 125.6636 | -1.0011 | -136.0414 | 125.1623
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8414e-09 | -5.324e-10 | -2.0622e-09 | -1.8414e-09 | 5.324e-10 | 2.0622e-09 | 2.6116e-10 | 3.3744e-09 | -9.6166e-10 | -2.6116e-10 | -3.3744e-09 | 9.6166e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2353 | 1.0092 | 0.88329 | 1.2353 | 1.0092 | 0.88329 | -1.0011 | -136.0414 | 125.1623 | -1.0011 | -136.0414 | 125.1623
Line13_13_14 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0049832 | -0.014354 | 0.00023146 | 0.0052832 | 0.014654 | 6.8538e-05 | -0.049162 | -0.03773 | -0.035331 | 0.049762 | 0.03833 | 0.035931 | 94.7869 | -25.213 | -145.2131 | -85.2131 | 154.787 | 34.7869 | 1.2353 | 1.0092 | 0.88329 | 1.251 | 1.0259 | 0.89828 | -1.0011 | -136.0414 | 125.1623 | -1.2735 | -136.1351 | 124.6776
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2276e-09 | -3.5493e-10 | -1.3748e-09 | -1.2276e-09 | 3.5493e-10 | 1.3748e-09 | 1.741e-10 | 2.2496e-09 | -6.411e-10 | -1.741e-10 | -2.2496e-09 | 6.411e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2353 | 1.0092 | 0.88329 | 1.2353 | 1.0092 | 0.88329 | -1.0011 | -136.0414 | 125.1623 | -1.0011 | -136.0414 | 125.1623
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1381e-10 | -1.7747e-10 | -6.8741e-10 | -6.1381e-10 | 1.7747e-10 | 6.8741e-10 | 8.7052e-11 | 1.1248e-09 | -3.2055e-10 | -8.7052e-11 | -1.1248e-09 | 3.2055e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2353 | 1.0092 | 0.88329 | 1.2353 | 1.0092 | 0.88329 | -1.0011 | -136.0414 | 125.1623 | -1.0011 | -136.0414 | 125.1623
Line16_4_18 | 0 | 3.4993 | 3.4993 | 0 | 3.4993 | 3.4993 | 0 | 0.80814 | 0.80814 | 0 | 0.80814 | 0.80814 | 3.8943e-10 | 0.57706 | -0.33215 | -3.8943e-10 | -0.45461 | 0.45461 | 2.7504e-16 | 0.089122 | 0.40069 | -4.0704e-16 | 0.15579 | -0.15579 | 0 | -161.0844 | 18.9156 | 0 | 18.9156 | -161.0844 | 1.1893 | 0.72253 | 0.64403 | 1.1893 | 0.59465 | 0.59465 | -4.8621e-06 | -152.305 | 148.5727 | -4.868e-06 | 180 | 180
Line17_5_19 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0040832 | -0.013454 | 0.0011315 | 0.0043832 | 0.013754 | -0.00083146 | -0.047362 | -0.03593 | -0.033531 | 0.047962 | 0.03653 | 0.034131 | 94.7868 | -25.213 | -145.2131 | -85.2132 | 154.787 | 34.7869 | 1.1884 | 0.95916 | 0.83875 | 1.204 | 0.97584 | 0.85353 | -0.14063 | -135.741 | 126.7195 | -0.43489 | -135.8446 | 126.1824
Line1_1_3 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0037832 | -0.013154 | 0.0014315 | 0.0040832 | 0.013454 | -0.0011315 | -0.046762 | -0.03533 | -0.032931 | 0.047362 | 0.03593 | 0.033531 | 94.7868 | -25.213 | -145.2131 | -85.2132 | 154.787 | 34.7869 | 1.1729 | 0.94249 | 0.82405 | 1.1884 | 0.95916 | 0.83875 | 0.16146 | -135.6338 | 127.2759 | -0.14063 | -135.741 | 126.7195
Line2_1_4 | 0.1732 | 3.3566 | 3.3449 | 0.1732 | 3.3566 | 3.3449 | 0.04 | 0.77518 | 0.77248 | 0.04 | 0.77518 | 0.77248 | -0.012171 | 0.66842 | -0.21431 | 0.012471 | -0.55575 | 0.3262 | -0.045308 | 0.29494 | 0.5994 | 0.045908 | -0.069598 | -0.37563 | 105.1981 | -159.4431 | 17.6017 | -74.8019 | 20.5569 | -162.3983 | 1.1729 | 0.94249 | 0.82405 | 1.1893 | 0.72253 | 0.64403 | 0.16146 | -135.6338 | 127.2759 | -4.8621e-06 | -152.305 | 148.5727
Line3_1_5 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0037832 | -0.013154 | 0.0014315 | 0.0040832 | 0.013454 | -0.0011315 | -0.046762 | -0.03533 | -0.032931 | 0.047362 | 0.03593 | 0.033531 | 94.7868 | -25.213 | -145.2131 | -85.2132 | 154.787 | 34.7869 | 1.1729 | 0.94249 | 0.82405 | 1.1884 | 0.95916 | 0.83875 | 0.16146 | -135.6338 | 127.2759 | -0.14063 | -135.741 | 126.7195
Line4_2_6 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0040832 | -0.013454 | 0.0011315 | 0.0043832 | 0.013754 | -0.00083146 | -0.047362 | -0.03593 | -0.033531 | 0.047962 | 0.03653 | 0.034131 | 94.7868 | -25.213 | -145.2131 | -85.2132 | 154.787 | 34.7869 | 1.1884 | 0.95916 | 0.83875 | 1.204 | 0.97584 | 0.85353 | -0.14063 | -135.741 | 126.7195 | -0.43489 | -135.8446 | 126.1824
Line5_6_7 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0043832 | -0.013754 | 0.00083146 | 0.0046832 | 0.014054 | -0.00053146 | -0.047962 | -0.03653 | -0.034131 | 0.048562 | 0.03713 | 0.034731 | 94.7868 | -25.213 | -145.2131 | -85.2132 | 154.787 | 34.7869 | 1.204 | 0.97584 | 0.85353 | 1.2197 | 0.99252 | 0.86838 | -0.43489 | -135.8446 | 126.1824 | -0.72162 | -135.9447 | 125.6636
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6068e-09 | -7.1135e-10 | -2.1612e-09 | -1.6068e-09 | 7.1135e-10 | 2.1612e-09 | 1.8587e-10 | 3.2991e-09 | -1.0369e-09 | -1.8587e-10 | -3.2991e-09 | 1.0369e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2197 | 0.99252 | 0.86838 | 1.2197 | 0.99252 | 0.86838 | -0.72162 | -135.9447 | 125.6636 | -0.72162 | -135.9447 | 125.6636
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3561e-10 | -2.3712e-10 | -7.204e-10 | -5.3561e-10 | 2.3712e-10 | 7.204e-10 | 6.1956e-11 | 1.0997e-09 | -3.4565e-10 | -6.1956e-11 | -1.0997e-09 | 3.4565e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2197 | 0.99252 | 0.86838 | 1.2197 | 0.99252 | 0.86838 | -0.72162 | -135.9447 | 125.6636 | -0.72162 | -135.9447 | 125.6636
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3561e-10 | -2.3712e-10 | -7.204e-10 | -5.3561e-10 | 2.3712e-10 | 7.204e-10 | 6.1956e-11 | 1.0997e-09 | -3.4565e-10 | -6.1956e-11 | -1.0997e-09 | 3.4565e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2197 | 0.99252 | 0.86838 | 1.2197 | 0.99252 | 0.86838 | -0.72162 | -135.9447 | 125.6636 | -0.72162 | -135.9447 | 125.6636
Line9_3_11 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0040832 | -0.013454 | 0.0011315 | 0.0043832 | 0.013754 | -0.00083146 | -0.047362 | -0.03593 | -0.033531 | 0.047962 | 0.03653 | 0.034131 | 94.7868 | -25.213 | -145.2131 | -85.2132 | 154.787 | 34.7869 | 1.1884 | 0.95916 | 0.83875 | 1.204 | 0.97584 | 0.85353 | -0.14063 | -135.741 | 126.7195 | -0.43489 | -135.8446 | 126.1824

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036085 | -0.0038394 | -0.0036305 | 0.0039085 | 0.0041394 | 0.0039305 | -0.044637 | -0.044529 | -0.044383 | 0.045237 | 0.045129 | 0.044983 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1196 | 1.1174 | 1.1133 | 1.1351 | 1.133 | 1.1289 | 0.16542 | -120.1408 | 120.1108 | -0.15091 | -120.4535 | 119.7935
Line10_11_12 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0042085 | -0.0044394 | -0.0042305 | 0.0045085 | 0.0047394 | 0.0045305 | -0.045837 | -0.045729 | -0.045583 | 0.046437 | 0.046329 | 0.046183 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1507 | 1.1486 | 1.1445 | 1.1664 | 1.1643 | 1.1601 | -0.45866 | -120.7577 | 119.4848 | -0.75817 | -121.0537 | 119.1845
Line11_12_13 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0045085 | -0.0047394 | -0.0045305 | 0.0048085 | 0.0050394 | 0.0048305 | -0.046437 | -0.046329 | -0.046183 | 0.047037 | 0.046929 | 0.046783 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1664 | 1.1643 | 1.1601 | 1.1821 | 1.18 | 1.1758 | -0.75817 | -121.0537 | 119.1845 | -1.0497 | -121.3419 | 118.8921
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7193e-09 | 1.6907e-09 | 1.6295e-09 | -1.7193e-09 | -1.6907e-09 | -1.6295e-09 | 2.5012e-10 | 3.1916e-10 | 2.6258e-10 | -2.5012e-10 | -3.1916e-10 | -2.6258e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1821 | 1.18 | 1.1758 | 1.1821 | 1.18 | 1.1758 | -1.0497 | -121.3419 | 118.8921 | -1.0497 | -121.3419 | 118.8921
Line13_13_14 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0048085 | -0.0050394 | -0.0048305 | 0.0051085 | 0.0053394 | 0.0051305 | -0.047037 | -0.046929 | -0.046783 | 0.047637 | 0.047529 | 0.047383 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1821 | 1.18 | 1.1758 | 1.1978 | 1.1957 | 1.1915 | -1.0497 | -121.3419 | 118.8921 | -1.3337 | -121.6225 | 118.6074
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1462e-09 | 1.1272e-09 | 1.0863e-09 | -1.1462e-09 | -1.1272e-09 | -1.0863e-09 | 1.6675e-10 | 2.1277e-10 | 1.7505e-10 | -1.6675e-10 | -2.1277e-10 | -1.7506e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1821 | 1.18 | 1.1758 | 1.1821 | 1.18 | 1.1758 | -1.0497 | -121.3419 | 118.8921 | -1.0497 | -121.3419 | 118.8921
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.731e-10 | 5.6358e-10 | 5.4317e-10 | -5.731e-10 | -5.6358e-10 | -5.4317e-10 | 8.3374e-11 | 1.0639e-10 | 8.7528e-11 | -8.3374e-11 | -1.0639e-10 | -8.7528e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1821 | 1.18 | 1.1758 | 1.1821 | 1.18 | 1.1758 | -1.0497 | -121.3419 | 118.8921 | -1.0497 | -121.3419 | 118.8921
Line16_4_18 | 0 | 0.063185 | 0.063185 | 0 | 0.063185 | 0.063185 | 0 | 0.014592 | 0.014592 | 0 | 0.014592 | 0.014592 | 3.5829e-10 | 0.015929 | 0.0041126 | -3.5829e-10 | -0.015889 | -0.0040727 | -1.4784e-16 | 0.0042476 | 0.015874 | 1.1634e-16 | -0.0041678 | -0.015794 | 0 | -135.4649 | 44.5351 | 0 | 44.5351 | -135.4649 | 1.136 | 1.1298 | 1.1238 | 1.136 | 1.1257 | 1.1178 | -1.1085e-07 | -120.5336 | 120.01 | -1.1681e-07 | -120.7668 | 120.0754
Line17_5_19 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039085 | -0.0041394 | -0.0039305 | 0.0042085 | 0.0044394 | 0.0042305 | -0.045237 | -0.045129 | -0.044983 | 0.045837 | 0.045729 | 0.045583 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1351 | 1.133 | 1.1289 | 1.1507 | 1.1486 | 1.1445 | -0.1509 | -120.4535 | 119.7935 | -0.45866 | -120.7577 | 119.4848
Line1_1_3 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036085 | -0.0038394 | -0.0036305 | 0.0039085 | 0.0041394 | 0.0039305 | -0.044637 | -0.044529 | -0.044383 | 0.045237 | 0.045129 | 0.044983 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1196 | 1.1174 | 1.1133 | 1.1351 | 1.133 | 1.1289 | 0.16542 | -120.1408 | 120.1108 | -0.15091 | -120.4535 | 119.7935
Line2_1_4 | 0.1732 | 0.15082 | 0.11003 | 0.1732 | 0.15082 | 0.11003 | 0.04 | 0.03483 | 0.025411 | 0.04 | 0.03483 | 0.025411 | -0.011807 | 0.0037105 | -0.0077352 | 0.012107 | -0.0034831 | 0.0078563 | -0.043198 | -0.03874 | -0.027212 | 0.043798 | 0.039195 | 0.027454 | 105.4525 | -35.6118 | -134.0207 | -74.5475 | 144.3882 | 45.9793 | 1.1196 | 1.1174 | 1.1133 | 1.136 | 1.1298 | 1.1238 | 0.16542 | -120.1408 | 120.1108 | -1.1085e-07 | -120.5336 | 120.01
Line3_1_5 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036085 | -0.0038394 | -0.0036305 | 0.0039085 | 0.0041394 | 0.0039305 | -0.044637 | -0.044529 | -0.044383 | 0.045237 | 0.045129 | 0.044983 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1196 | 1.1174 | 1.1133 | 1.1351 | 1.133 | 1.1289 | 0.16542 | -120.1408 | 120.1108 | -0.1509 | -120.4535 | 119.7935
Line4_2_6 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039085 | -0.0041394 | -0.0039305 | 0.0042085 | 0.0044394 | 0.0042305 | -0.045237 | -0.045129 | -0.044983 | 0.045837 | 0.045729 | 0.045583 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1351 | 1.133 | 1.1289 | 1.1507 | 1.1486 | 1.1445 | -0.15091 | -120.4535 | 119.7935 | -0.45866 | -120.7577 | 119.4848
Line5_6_7 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0042085 | -0.0044394 | -0.0042305 | 0.0045085 | 0.0047394 | 0.0045305 | -0.045837 | -0.045729 | -0.045583 | 0.046437 | 0.046329 | 0.046183 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1507 | 1.1486 | 1.1445 | 1.1664 | 1.1643 | 1.1601 | -0.45866 | -120.7577 | 119.4848 | -0.75817 | -121.0537 | 119.1845
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4944e-09 | 1.4657e-09 | 1.4066e-09 | -1.4944e-09 | -1.4657e-09 | -1.4066e-09 | 1.7826e-10 | 2.473e-10 | 1.9072e-10 | -1.7826e-10 | -2.473e-10 | -1.9072e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1664 | 1.1643 | 1.1601 | 1.1664 | 1.1643 | 1.1601 | -0.75817 | -121.0537 | 119.1845 | -0.75817 | -121.0537 | 119.1845
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9813e-10 | 4.8858e-10 | 4.6887e-10 | -4.9813e-10 | -4.8858e-10 | -4.6887e-10 | 5.942e-11 | 8.2432e-11 | 6.3573e-11 | -5.942e-11 | -8.2433e-11 | -6.3573e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1664 | 1.1643 | 1.1601 | 1.1664 | 1.1643 | 1.1601 | -0.75817 | -121.0537 | 119.1845 | -0.75817 | -121.0537 | 119.1845
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9813e-10 | 4.8858e-10 | 4.6887e-10 | -4.9813e-10 | -4.8858e-10 | -4.6887e-10 | 5.942e-11 | 8.2432e-11 | 6.3573e-11 | -5.942e-11 | -8.2433e-11 | -6.3573e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1664 | 1.1643 | 1.1601 | 1.1664 | 1.1643 | 1.1601 | -0.75817 | -121.0537 | 119.1845 | -0.75817 | -121.0537 | 119.1845
Line9_3_11 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039085 | -0.0041394 | -0.0039305 | 0.0042085 | 0.0044394 | 0.0042305 | -0.045237 | -0.045129 | -0.044983 | 0.045837 | 0.045729 | 0.045583 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1351 | 1.133 | 1.1289 | 1.1507 | 1.1486 | 1.1445 | -0.15091 | -120.4535 | 119.7935 | -0.45866 | -120.7577 | 119.4848

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0037833 | -0.0040363 | -0.0038074 | 0.0040833 | 0.0043363 | 0.0041074 | -0.046762 | -0.046644 | -0.046484 | 0.047362 | 0.047244 | 0.047084 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1729 | 1.1704 | 1.166 | 1.1884 | 1.1861 | 1.1816 | 0.16147 | -120.1589 | 120.1044 | -0.14062 | -120.4574 | 119.8013
Line10_11_12 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0043833 | -0.0046363 | -0.0044074 | 0.0046833 | 0.0049363 | 0.0047074 | -0.047962 | -0.047844 | -0.047684 | 0.048562 | 0.048444 | 0.048284 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.204 | 1.2017 | 1.1972 | 1.2197 | 1.2174 | 1.2128 | -0.43489 | -120.7481 | 119.5061 | -0.72162 | -121.0314 | 119.2185
Line11_12_13 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0046833 | -0.0049363 | -0.0047074 | 0.0049833 | 0.0052363 | 0.0050074 | -0.048562 | -0.048444 | -0.048284 | 0.049162 | 0.049044 | 0.048884 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.2197 | 1.2174 | 1.2128 | 1.2353 | 1.2331 | 1.2285 | -0.72162 | -121.0314 | 119.2185 | -1.0011 | -121.3074 | 118.9382
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8414e-09 | 1.8086e-09 | 1.7388e-09 | -1.8414e-09 | -1.8086e-09 | -1.7388e-09 | 2.6115e-10 | 3.4043e-10 | 2.7545e-10 | -2.6115e-10 | -3.4043e-10 | -2.7545e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2353 | 1.2331 | 1.2285 | 1.2353 | 1.2331 | 1.2285 | -1.0011 | -121.3074 | 118.9382 | -1.0011 | -121.3074 | 118.9382
Line13_13_14 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0049833 | -0.0052363 | -0.0050074 | 0.0052833 | 0.0055363 | 0.0053074 | -0.049162 | -0.049044 | -0.048884 | 0.049762 | 0.049644 | 0.049484 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.2353 | 1.2331 | 1.2285 | 1.251 | 1.2488 | 1.2442 | -1.0011 | -121.3074 | 118.9382 | -1.2735 | -121.5765 | 118.665
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2276e-09 | 1.2058e-09 | 1.1592e-09 | -1.2276e-09 | -1.2058e-09 | -1.1592e-09 | 1.741e-10 | 2.2695e-10 | 1.8363e-10 | -1.741e-10 | -2.2695e-10 | -1.8363e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2353 | 1.2331 | 1.2285 | 1.2353 | 1.2331 | 1.2285 | -1.0011 | -121.3074 | 118.9382 | -1.0011 | -121.3074 | 118.9382
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1381e-10 | 6.0288e-10 | 5.7959e-10 | -6.1381e-10 | -6.0288e-10 | -5.7959e-10 | 8.7051e-11 | 1.1348e-10 | 9.1815e-11 | -8.7051e-11 | -1.1348e-10 | -9.1815e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2353 | 1.2331 | 1.2285 | 1.2353 | 1.2331 | 1.2285 | -1.0011 | -121.3074 | 118.9382 | -1.0011 | -121.3074 | 118.9382
Line16_4_18 | 0 | 0.066133 | 0.066133 | 0 | 0.066133 | 0.066133 | 0 | 0.015273 | 0.015273 | 0 | 0.015273 | 0.015273 | 3.8943e-10 | 0.017453 | 0.0045026 | -3.8943e-10 | -0.017409 | -0.0044588 | -1.7687e-16 | 0.004653 | 0.01739 | 1.2189e-16 | -0.0045656 | -0.017302 | 0 | -135.4761 | 44.5239 | 0 | 44.5239 | -135.4761 | 1.1893 | 1.1826 | 1.1762 | 1.1893 | 1.1784 | 1.1699 | -1.1961e-07 | -120.5478 | 120.0075 | -1.2552e-07 | -120.781 | 120.073
Line17_5_19 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0040833 | -0.0043363 | -0.0041074 | 0.0043833 | 0.0046363 | 0.0044074 | -0.047362 | -0.047244 | -0.047084 | 0.047962 | 0.047844 | 0.047684 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1884 | 1.1861 | 1.1816 | 1.204 | 1.2017 | 1.1972 | -0.14062 | -120.4574 | 119.8013 | -0.43489 | -120.7481 | 119.5061
Line1_1_3 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0037833 | -0.0040363 | -0.0038074 | 0.0040833 | 0.0043363 | 0.0041074 | -0.046762 | -0.046644 | -0.046484 | 0.047362 | 0.047244 | 0.047084 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1729 | 1.1704 | 1.166 | 1.1884 | 1.1861 | 1.1816 | 0.16147 | -120.1589 | 120.1044 | -0.14062 | -120.4574 | 119.8013
Line2_1_4 | 0.1732 | 0.15062 | 0.10708 | 0.1732 | 0.15062 | 0.10708 | 0.04 | 0.034784 | 0.024729 | 0.04 | 0.034784 | 0.024729 | -0.012171 | 0.004842 | -0.0077103 | 0.012471 | -0.0046151 | 0.007825 | -0.045308 | -0.040424 | -0.027783 | 0.045908 | 0.040878 | 0.028013 | 105.1981 | -36.9893 | -134.3854 | -74.8019 | 143.0107 | 45.6146 | 1.1729 | 1.1704 | 1.166 | 1.1893 | 1.1826 | 1.1762 | 0.16147 | -120.1589 | 120.1044 | -1.1961e-07 | -120.5478 | 120.0075
Line3_1_5 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0037833 | -0.0040363 | -0.0038074 | 0.0040833 | 0.0043363 | 0.0041074 | -0.046762 | -0.046644 | -0.046484 | 0.047362 | 0.047244 | 0.047084 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1729 | 1.1704 | 1.166 | 1.1884 | 1.1861 | 1.1816 | 0.16147 | -120.1589 | 120.1044 | -0.14062 | -120.4574 | 119.8013
Line4_2_6 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0040833 | -0.0043363 | -0.0041074 | 0.0043833 | 0.0046363 | 0.0044074 | -0.047362 | -0.047244 | -0.047084 | 0.047962 | 0.047844 | 0.047684 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1884 | 1.1861 | 1.1816 | 1.204 | 1.2017 | 1.1972 | -0.14062 | -120.4574 | 119.8013 | -0.43489 | -120.7481 | 119.5061
Line5_6_7 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0043833 | -0.0046363 | -0.0044074 | 0.0046833 | 0.0049363 | 0.0047074 | -0.047962 | -0.047844 | -0.047684 | 0.048562 | 0.048444 | 0.048284 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.204 | 1.2017 | 1.1972 | 1.2197 | 1.2174 | 1.2128 | -0.43489 | -120.7481 | 119.5061 | -0.72162 | -121.0314 | 119.2185
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6068e-09 | 1.574e-09 | 1.5064e-09 | -1.6068e-09 | -1.574e-09 | -1.5064e-09 | 1.8587e-10 | 2.6514e-10 | 2.0016e-10 | -1.8587e-10 | -2.6514e-10 | -2.0016e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2197 | 1.2174 | 1.2128 | 1.2197 | 1.2174 | 1.2128 | -0.72162 | -121.0314 | 119.2185 | -0.72162 | -121.0314 | 119.2185
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3561e-10 | 5.2465e-10 | 5.0212e-10 | -5.3561e-10 | -5.2465e-10 | -5.0212e-10 | 6.1956e-11 | 8.838e-11 | 6.6719e-11 | -6.1956e-11 | -8.838e-11 | -6.672e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2197 | 1.2174 | 1.2128 | 1.2197 | 1.2174 | 1.2128 | -0.72162 | -121.0314 | 119.2185 | -0.72162 | -121.0314 | 119.2185
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3561e-10 | 5.2465e-10 | 5.0212e-10 | -5.3561e-10 | -5.2465e-10 | -5.0212e-10 | 6.1956e-11 | 8.838e-11 | 6.672e-11 | -6.1956e-11 | -8.838e-11 | -6.672e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2197 | 1.2174 | 1.2128 | 1.2197 | 1.2174 | 1.2128 | -0.72162 | -121.0314 | 119.2185 | -0.72162 | -121.0314 | 119.2185
Line9_3_11 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0040833 | -0.0043363 | -0.0041074 | 0.0043833 | 0.0046363 | 0.0044074 | -0.047362 | -0.047244 | -0.047084 | 0.047962 | 0.047844 | 0.047684 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1884 | 1.1861 | 1.1816 | 1.204 | 1.2017 | 1.1972 | -0.14062 | -120.4574 | 119.8013 | -0.43489 | -120.7481 | 119.5061

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2305e-16 | -1.4366e-09 | -3.9666e-09 | -1.4063e-16 | 1.4366e-09 | 3.9666e-09 | 7.0314e-17 | 4.6273e-09 | -2.4518e-10 | -7.0314e-17 | -4.6273e-09 | 2.4518e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.7779e-13 | -135.3123 | 120.9775 | 1.7841e-13 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -1.4366e-09 | -3.9666e-09 | 2.3287e-31 | 1.4366e-09 | 3.9666e-09 | 7.0314e-17 | 4.6273e-09 | -2.4518e-10 | -7.0314e-17 | -4.6273e-09 | 2.4518e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.8567e-13 | -135.3123 | 120.9775 | 1.8976e-13 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.1525e-17 | -1.1971e-09 | -3.3055e-09 | 2.6368e-17 | 1.1971e-09 | 3.3055e-09 | 1.2305e-16 | 3.8561e-09 | -2.0432e-10 | -1.4063e-16 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.8976e-13 | -135.3123 | 120.9775 | 1.9344e-13 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -7.1829e-10 | -1.9833e-09 | 8.7893e-18 | 7.1829e-10 | 1.9833e-09 | 1.7579e-17 | 2.3136e-09 | -1.2259e-10 | 2.9924e-32 | -2.3136e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.9344e-13 | -135.3123 | 120.9775 | 1.9507e-13 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -2.3943e-10 | -6.611e-10 | 1.186e-31 | 2.3943e-10 | 6.611e-10 | 7.0314e-17 | 7.7122e-10 | -4.0864e-11 | -3.5157e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.9344e-13 | -135.3123 | 120.9775 | 1.9329e-13 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6368e-17 | -4.7886e-10 | -1.3222e-09 | -8.7893e-18 | 4.7886e-10 | 1.3222e-09 | 3.5157e-17 | 1.5424e-09 | -8.1728e-11 | -1.7579e-17 | -1.5424e-09 | 8.1728e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.9507e-13 | -135.3123 | 120.9775 | 1.9633e-13 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -2.3943e-10 | -6.611e-10 | 1.7579e-17 | 2.3943e-10 | 6.611e-10 | 1.7579e-17 | 7.7122e-10 | -4.0864e-11 | -1.7579e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.9633e-13 | -135.3123 | 120.9775 | 1.9662e-13 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | 1.4063e-16 | 0.35328 | -0.11197 | -7.0314e-17 | -0.23262 | 0.23262 | 4.3711e-31 | -0.020967 | 0.27233 | -2.17e-31 | 0.14665 | -0.14665 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.6113 | 0.50862 | 0.95 | 0.475 | 0.475 | 1.7809e-13 | -151.1682 | 144.5775 | 1.7682e-13 | -180 | 180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.4892e-32 | -2.3943e-10 | -6.611e-10 | 5.498e-32 | 2.3943e-10 | 6.611e-10 | 1.7579e-17 | 7.7122e-10 | -4.0864e-11 | -1.7579e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.7892e-13 | -135.3123 | 120.9775 | 1.792e-13 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3636e-31 | -1.9154e-09 | -5.2888e-09 | -1.7579e-17 | 1.9154e-09 | 5.2888e-09 | 1.4063e-16 | 6.1697e-09 | -3.2691e-10 | -1.2305e-16 | -6.1697e-09 | 3.2691e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.7779e-13 | -135.3123 | 120.9775 | 1.8157e-13 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.5068 | 2.5068 | 0 | 2.5068 | 2.5068 | 0 | 0.57893 | 0.57893 | 0 | 0.57893 | 0.57893 | -3.5157e-17 | 0.47394 | 0.0086903 | 3.5157e-17 | -0.35328 | 0.11197 | -1.0909e-31 | 0.10472 | 0.39802 | 1.0928e-31 | 0.020967 | -0.27233 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.6113 | 0.50862 | 1.7779e-13 | -135.3123 | 120.9775 | 1.7809e-13 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7579e-17 | -4.7886e-10 | -1.3222e-09 | 1.7579e-17 | 4.7886e-10 | 1.3222e-09 | 7.0314e-17 | 1.5424e-09 | -8.1728e-11 | -5.2736e-17 | -1.5424e-09 | 8.1728e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.7779e-13 | -135.3123 | 120.9775 | 1.7892e-13 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6368e-17 | -1.1971e-09 | -3.3055e-09 | -4.3946e-17 | 1.1971e-09 | 3.3055e-09 | 1.5821e-16 | 3.8561e-09 | -2.0432e-10 | -1.7579e-16 | -3.8561e-09 | 2.0432e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.7841e-13 | -135.3123 | 120.9775 | 1.7995e-13 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6682e-17 | -9.5772e-10 | -2.6444e-09 | -9.6682e-17 | 9.5772e-10 | 2.6444e-09 | 7.0314e-17 | 3.0849e-09 | -1.6346e-10 | -8.7893e-17 | -3.0849e-09 | 1.6346e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.7995e-13 | -135.3123 | 120.9775 | 1.8075e-13 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3946e-17 | -7.1829e-10 | -1.9833e-09 | -4.3946e-17 | 7.1829e-10 | 1.9833e-09 | 1.4063e-16 | 2.3136e-09 | -1.2259e-10 | -1.2305e-16 | -2.3136e-09 | 1.2259e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.8075e-13 | -135.3123 | 120.9775 | 1.8215e-13 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6765e-31 | -2.3943e-10 | -6.611e-10 | 1.6751e-31 | 2.3943e-10 | 6.611e-10 | 5.2736e-17 | 7.7122e-10 | -4.0864e-11 | -5.2736e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.8215e-13 | -135.3123 | 120.9775 | 1.82e-13 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7893e-18 | -2.3943e-10 | -6.611e-10 | -8.7893e-18 | 2.3943e-10 | 6.611e-10 | 7.0314e-17 | 7.7122e-10 | -4.0864e-11 | -7.0314e-17 | -7.7122e-10 | 4.0864e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.8215e-13 | -135.3123 | 120.9775 | 1.8263e-13 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7893e-18 | -1.676e-09 | -4.6277e-09 | -8.7893e-18 | 1.676e-09 | 4.6277e-09 | 1.2305e-16 | 5.3985e-09 | -2.8605e-10 | -1.0547e-16 | -5.3985e-09 | 2.8605e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.83839 | 0.68767 | 0.95 | 0.83839 | 0.68767 | 1.8157e-13 | -135.3123 | 120.9775 | 1.8567e-13 | -135.3123 | 120.9775

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1657e-16 | -1.2893e-09 | -3.56e-09 | -1.3323e-16 | 1.2893e-09 | 3.56e-09 | 1.1657e-16 | 4.153e-09 | -2.2006e-10 | -1.1657e-16 | -4.153e-09 | 2.2006e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.7918e-13 | -135.3123 | 120.9775 | 1.7972e-13 | -135.3123 | 120.9775
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -1.2893e-09 | -3.56e-09 | 8.3267e-18 | 1.2893e-09 | 3.56e-09 | 1.3323e-16 | 4.153e-09 | -2.2006e-10 | -9.992e-17 | -4.153e-09 | 2.2006e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.8706e-13 | -135.3123 | 120.9775 | 1.9115e-13 | -135.3123 | 120.9775
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -1.0744e-09 | -2.9667e-09 | 2.498e-17 | 1.0744e-09 | 2.9667e-09 | 1.3323e-16 | 3.4609e-09 | -1.8338e-10 | -9.992e-17 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.9115e-13 | -135.3123 | 120.9775 | 1.9483e-13 | -135.3123 | 120.9775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6629e-32 | -6.4467e-10 | -1.78e-09 | 1.6653e-17 | 6.4467e-10 | 1.78e-09 | -1.6653e-17 | 2.0765e-09 | -1.1003e-10 | 1.6653e-17 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.9483e-13 | -135.3123 | 120.9775 | 1.9646e-13 | -135.3123 | 120.9775
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3307e-17 | -2.1489e-10 | -5.9334e-10 | -3.3307e-17 | 2.1489e-10 | 5.9334e-10 | 1.1326e-31 | 6.9217e-10 | -3.6676e-11 | -1.1317e-31 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.9483e-13 | -135.3123 | 120.9775 | 1.9468e-13 | -135.3123 | 120.9775
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -4.2978e-10 | -1.1867e-09 | 2.498e-17 | 4.2978e-10 | 1.1867e-09 | 1.6653e-17 | 1.3843e-09 | -7.3352e-11 | -3.3307e-17 | -1.3843e-09 | 7.3352e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.9646e-13 | -135.3123 | 120.9775 | 1.9772e-13 | -135.3123 | 120.9775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.3267e-18 | -2.1489e-10 | -5.9334e-10 | 8.3267e-18 | 2.1489e-10 | 5.9334e-10 | -2.8735e-32 | 6.9217e-10 | -3.6676e-11 | 2.8776e-32 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.9772e-13 | -135.3123 | 120.9775 | 1.9801e-13 | -135.3123 | 120.9775
Line16_4_18 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | 2.0827e-31 | 0.31707 | -0.10049 | -2.0725e-31 | -0.20878 | 0.20878 | -6.6613e-17 | -0.018818 | 0.24442 | 6.6613e-17 | 0.13162 | -0.13162 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.57913 | 0.48185 | 0.9 | 0.45 | 0.45 | 1.7914e-13 | -151.1682 | 144.5775 | 1.7826e-13 | -180 | 180
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.1633e-17 | -2.1489e-10 | -5.9334e-10 | 5.8287e-17 | 2.1489e-10 | 5.9334e-10 | 1.6653e-17 | 6.9217e-10 | -3.6676e-11 | -4.996e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.8031e-13 | -135.3123 | 120.9775 | 1.806e-13 | -135.3123 | 120.9775
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -1.7191e-09 | -4.7467e-09 | -2.498e-17 | 1.7191e-09 | 4.7467e-09 | 9.992e-17 | 5.5374e-09 | -2.9341e-10 | -9.992e-17 | -5.5374e-09 | 2.9341e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.7918e-13 | -135.3123 | 120.9775 | 1.8296e-13 | -135.3123 | 120.9775
Line2_1_4 | 0 | 2.3749 | 2.3749 | 0 | 2.3749 | 2.3749 | 0 | 0.54846 | 0.54846 | 0 | 0.54846 | 0.54846 | -3.3307e-17 | 0.42536 | 0.0077996 | 0 | -0.31707 | 0.10049 | 3.3307e-17 | 0.093984 | 0.35722 | 0 | 0.018818 | -0.24442 | 0 | -147.7717 | 32.2283 | 0 | 32.2283 | -147.7717 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.57913 | 0.48185 | 1.7918e-13 | -135.3123 | 120.9775 | 1.7914e-13 | -151.1682 | 144.5775
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6653e-17 | -4.2978e-10 | -1.1867e-09 | -3.3307e-17 | 4.2978e-10 | 1.1867e-09 | 3.3307e-17 | 1.3843e-09 | -7.3352e-11 | -3.3307e-17 | -1.3843e-09 | 7.3352e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.7918e-13 | -135.3123 | 120.9775 | 1.8031e-13 | -135.3123 | 120.9775
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.996e-17 | -1.0744e-09 | -2.9667e-09 | -3.3307e-17 | 1.0744e-09 | 2.9667e-09 | 9.992e-17 | 3.4609e-09 | -1.8338e-10 | -9.992e-17 | -3.4609e-09 | 1.8338e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.7972e-13 | -135.3123 | 120.9775 | 1.8116e-13 | -135.3123 | 120.9775
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.498e-17 | -8.5956e-10 | -2.3734e-09 | -2.498e-17 | 8.5956e-10 | 2.3734e-09 | 1.4988e-16 | 2.7687e-09 | -1.467e-10 | -1.4988e-16 | -2.7687e-09 | 1.467e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.8116e-13 | -135.3123 | 120.9775 | 1.8263e-13 | -135.3123 | 120.9775
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.996e-17 | -6.4467e-10 | -1.78e-09 | -3.3307e-17 | 6.4467e-10 | 1.78e-09 | 8.3267e-17 | 2.0765e-09 | -1.1003e-10 | -9.992e-17 | -2.0765e-09 | 1.1003e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.8263e-13 | -135.3123 | 120.9775 | 1.8423e-13 | -135.3123 | 120.9775
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1633e-17 | -2.1489e-10 | -5.9334e-10 | -8.3267e-18 | 2.1489e-10 | 5.9334e-10 | 1.3387e-31 | 6.9217e-10 | -3.6676e-11 | 1.6653e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.8423e-13 | -135.3123 | 120.9775 | 1.8407e-13 | -135.3123 | 120.9775
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3267e-18 | -2.1489e-10 | -5.9334e-10 | 2.498e-17 | 2.1489e-10 | 5.9334e-10 | 3.3307e-17 | 6.9217e-10 | -3.6676e-11 | -3.3307e-17 | -6.9217e-10 | 3.6676e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.8423e-13 | -135.3123 | 120.9775 | 1.8473e-13 | -135.3123 | 120.9775
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5953e-31 | -1.5042e-09 | -4.1534e-09 | -3.3307e-17 | 1.5042e-09 | 4.1534e-09 | 4.996e-17 | 4.8452e-09 | -2.5673e-10 | -6.6613e-17 | -4.8452e-09 | 2.5673e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.79426 | 0.65148 | 0.9 | 0.79426 | 0.65148 | 1.8296e-13 | -135.3123 | 120.9775 | 1.8706e-13 | -135.3123 | 120.9775

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.472e-18 | -3.8862e-11 | -1.1288e-10 | -2.472e-18 | 3.8862e-11 | 1.1288e-10 | 2.1973e-18 | 1.0829e-10 | 1.9912e-11 | -2.1973e-18 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.1852e-15 | -120.3131 | 119.9422 | 3.2099e-15 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0987e-18 | -3.8862e-11 | -1.1288e-10 | -1.0987e-18 | 3.8862e-11 | 1.1288e-10 | 2.7466e-18 | 1.0829e-10 | 1.9912e-11 | -2.7466e-18 | -1.0829e-10 | -1.9912e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.3279e-15 | -120.3131 | 119.9422 | 3.4029e-15 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3047e-18 | -3.2385e-11 | -9.4068e-11 | 1.3047e-18 | 3.2385e-11 | 9.4068e-11 | 2.7466e-18 | 9.0245e-11 | 1.6593e-11 | -2.7466e-18 | -9.0245e-11 | -1.6593e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.4029e-15 | -120.3131 | 119.9422 | 3.4744e-15 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4333e-19 | -1.9431e-11 | -5.6441e-11 | 3.4333e-19 | 1.9431e-11 | 5.6441e-11 | -2.0819e-35 | 5.4147e-11 | 9.9561e-12 | -1.0987e-18 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.4744e-15 | -120.3131 | 119.9422 | 3.5115e-15 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8066e-19 | -6.477e-12 | -1.8814e-11 | -4.8066e-19 | 6.477e-12 | 1.8814e-11 | 2.9147e-35 | 1.8049e-11 | 3.3187e-12 | -1.0987e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.4744e-15 | -120.3131 | 119.9422 | 3.4733e-15 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5533e-19 | -1.2954e-11 | -3.7627e-11 | 7.5533e-19 | 1.2954e-11 | 3.7627e-11 | 1.648e-18 | 3.6098e-11 | 6.6374e-12 | -1.0987e-18 | -3.6098e-11 | -6.6374e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.5115e-15 | -120.3131 | 119.9422 | 3.5443e-15 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3981e-35 | -6.477e-12 | -1.8814e-11 | 5.4933e-19 | 6.477e-12 | 1.8814e-11 | 5.4933e-19 | 1.8049e-11 | 3.3187e-12 | -5.4933e-19 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.5443e-15 | -120.3131 | 119.9422 | 3.5565e-15 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | -1.0987e-18 | 0.011082 | 0.0028784 | -1.0987e-18 | -0.011029 | -0.0028252 | -1.0987e-18 | 0.0029185 | 0.011047 | -1.0987e-18 | -0.0028631 | -0.010991 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94272 | 0.93905 | 0.95 | 0.93734 | 0.93354 | 3.2247e-15 | -120.5122 | 120.1294 | 3.2156e-15 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8666e-20 | -6.477e-12 | -1.8814e-11 | 2.06e-19 | 6.477e-12 | 1.8814e-11 | 1.0987e-18 | 1.8049e-11 | 3.3187e-12 | -5.4933e-19 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.2157e-15 | -120.3131 | 119.9422 | 3.2279e-15 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.266e-18 | -5.1816e-11 | -1.5051e-10 | -2.266e-18 | 5.1816e-11 | 1.5051e-10 | 1.648e-18 | 1.4439e-10 | 2.655e-11 | -2.1973e-18 | -1.4439e-10 | -2.655e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.1852e-15 | -120.3131 | 119.9422 | 3.2541e-15 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.052639 | 0.052639 | 0 | 0.052639 | 0.052639 | 0 | 0.012156 | 0.012156 | 0 | 0.012156 | 0.012156 | 5.4933e-19 | 0.011136 | 0.0029316 | -1.0987e-18 | -0.011082 | -0.0028784 | -1.0987e-18 | 0.0029739 | 0.011102 | -6.1835e-35 | -0.0029185 | -0.011047 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94272 | 0.93905 | 3.1852e-15 | -120.3131 | 119.9422 | 3.2247e-15 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.18e-19 | -1.2954e-11 | -3.7627e-11 | -6.8666e-20 | 1.2954e-11 | 3.7627e-11 | 1.0987e-18 | 3.6098e-11 | 6.6374e-12 | -1.0987e-18 | -3.6098e-11 | -6.6374e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.1852e-15 | -120.3131 | 119.9422 | 3.2157e-15 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.884e-18 | -3.2385e-11 | -9.4068e-11 | -2.884e-18 | 3.2385e-11 | 9.4068e-11 | 3.296e-18 | 9.0245e-11 | 1.6593e-11 | -3.296e-18 | -9.0245e-11 | -1.6593e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.2099e-15 | -120.3131 | 119.9422 | 3.2362e-15 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3733e-18 | -2.5908e-11 | -7.5255e-11 | -1.648e-18 | 2.5908e-11 | 7.5255e-11 | 1.648e-18 | 7.2196e-11 | 1.3275e-11 | -1.648e-18 | -7.2196e-11 | -1.3275e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.2362e-15 | -120.3131 | 119.9422 | 3.2595e-15 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8666e-19 | -1.9431e-11 | -5.6441e-11 | -9.6133e-19 | 1.9431e-11 | 5.6441e-11 | 3.296e-18 | 5.4147e-11 | 9.9561e-12 | -2.1973e-18 | -5.4147e-11 | -9.9561e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.2595e-15 | -120.3131 | 119.9422 | 3.2936e-15 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.18e-19 | -6.477e-12 | -1.8814e-11 | 6.18e-19 | 6.477e-12 | 1.8814e-11 | 5.4933e-19 | 1.8049e-11 | 3.3187e-12 | -1.0987e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.2936e-15 | -120.3131 | 119.9422 | 3.2925e-15 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.4333e-19 | -6.477e-12 | -1.8814e-11 | 6.18e-19 | 6.477e-12 | 1.8814e-11 | 5.4933e-19 | 1.8049e-11 | 3.3187e-12 | -1.0987e-18 | -1.8049e-11 | -3.3187e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.2936e-15 | -120.3131 | 119.9422 | 3.3089e-15 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4933e-19 | -4.5339e-11 | -1.317e-10 | -8.2399e-19 | 4.5339e-11 | 1.317e-10 | 3.296e-18 | 1.2634e-10 | 2.3231e-11 | -3.296e-18 | -1.2634e-10 | -2.3231e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94812 | 0.94457 | 0.95 | 0.94812 | 0.94457 | 3.2541e-15 | -120.3131 | 119.9422 | 3.3279e-15 | -120.3131 | 119.9422

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8623e-18 | -3.4879e-11 | -1.0131e-10 | -2.8623e-18 | 3.4879e-11 | 1.0131e-10 | 1.0408e-18 | 9.7195e-11 | 1.7871e-11 | -5.2042e-19 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.1741e-15 | -120.3131 | 119.9422 | 3.189e-15 | -120.3131 | 119.9422
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5052e-19 | -3.4879e-11 | -1.0131e-10 | -3.9031e-19 | 3.4879e-11 | 1.0131e-10 | 1.5613e-18 | 9.7195e-11 | 1.7871e-11 | -2.0817e-18 | -9.7195e-11 | -1.7871e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.3168e-15 | -120.3131 | 119.9422 | 3.3918e-15 | -120.3131 | 119.9422
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.236e-18 | -2.9066e-11 | -8.4427e-11 | 1.4962e-18 | 2.9066e-11 | 8.4427e-11 | 4.1633e-18 | 8.0996e-11 | 1.4893e-11 | -4.1633e-18 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.3918e-15 | -120.3131 | 119.9422 | 3.4633e-15 | -120.3131 | 119.9422
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.301e-19 | -1.7439e-11 | -5.0656e-11 | -1.301e-19 | 1.7439e-11 | 5.0656e-11 | 5.2042e-19 | 4.8598e-11 | 8.9356e-12 | -1.0408e-18 | -4.8598e-11 | -8.9357e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.4633e-15 | -120.3131 | 119.9422 | 3.5004e-15 | -120.3131 | 119.9422
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9516e-19 | -5.8131e-12 | -1.6885e-11 | 6.5052e-20 | 5.8131e-12 | 1.6885e-11 | -5.2042e-19 | 1.6199e-11 | 2.9786e-12 | 3.9309e-36 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.4633e-15 | -120.3131 | 119.9422 | 3.4622e-15 | -120.3131 | 119.9422
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9031e-19 | -1.1626e-11 | -3.3771e-11 | 3.9031e-19 | 1.1626e-11 | 3.3771e-11 | 1.0408e-18 | 3.2398e-11 | 5.9571e-12 | -1.0408e-18 | -3.2398e-11 | -5.9571e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.5004e-15 | -120.3131 | 119.9422 | 3.5332e-15 | -120.3131 | 119.9422
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.236e-18 | -5.8131e-12 | -1.6885e-11 | 9.7578e-19 | 5.8131e-12 | 1.6885e-11 | -7.6218e-35 | 1.6199e-11 | 2.9785e-12 | -5.2042e-19 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.5332e-15 | -120.3131 | 119.9422 | 3.5455e-15 | -120.3131 | 119.9422
Line16_4_18 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | -3.1225e-18 | 0.0099465 | 0.0025834 | 2.0817e-18 | -0.0098987 | -0.0025356 | -1.7492e-34 | 0.0026194 | 0.0099144 | 1.1675e-34 | -0.0025697 | -0.0098647 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89311 | 0.88962 | 0.9 | 0.888 | 0.8844 | 3.2097e-15 | -120.5122 | 120.1294 | 3.2135e-15 | -120.7135 | 120.3187
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0408e-18 | -5.8131e-12 | -1.6885e-11 | 7.8063e-19 | 5.8131e-12 | 1.6885e-11 | 5.2042e-19 | 1.6199e-11 | 2.9785e-12 | 4.3828e-35 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.2046e-15 | -120.3131 | 119.9422 | 3.2168e-15 | -120.3131 | 119.9422
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4311e-18 | -4.6505e-11 | -1.3508e-10 | -1.4311e-18 | 4.6505e-11 | 1.3508e-10 | 2.6021e-18 | 1.2959e-10 | 2.3828e-11 | -2.0817e-18 | -1.2959e-10 | -2.3828e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.1741e-15 | -120.3131 | 119.9422 | 3.243e-15 | -120.3131 | 119.9422
Line2_1_4 | 0 | 0.049869 | 0.049869 | 0 | 0.049869 | 0.049869 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | -5.7661e-35 | 0.0099942 | 0.0026311 | 1.0408e-18 | -0.0099465 | -0.0025834 | 1.0408e-18 | 0.0026691 | 0.0099642 | -2.0817e-18 | -0.0026194 | -0.0099144 | 0 | -135.266 | 44.734 | 0 | 44.734 | -135.266 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89311 | 0.88962 | 3.1741e-15 | -120.3131 | 119.9422 | 3.2097e-15 | -120.5122 | 120.1294
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8547e-19 | -1.1626e-11 | -3.3771e-11 | -5.8547e-19 | 1.1626e-11 | 3.3771e-11 | 1.5613e-18 | 3.2398e-11 | 5.9571e-12 | -1.5613e-18 | -3.2398e-11 | -5.9571e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.1741e-15 | -120.3131 | 119.9422 | 3.2046e-15 | -120.3131 | 119.9422
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8215e-18 | -2.9066e-11 | -8.4427e-11 | -2.0817e-18 | 2.9066e-11 | 8.4427e-11 | 3.1225e-18 | 8.0996e-11 | 1.4893e-11 | -2.6021e-18 | -8.0996e-11 | -1.4893e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.189e-15 | -120.3131 | 119.9422 | 3.2125e-15 | -120.3131 | 119.9422
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5613e-18 | -2.3253e-11 | -6.7542e-11 | -1.8215e-18 | 2.3253e-11 | 6.7542e-11 | 2.0817e-18 | 6.4797e-11 | 1.1914e-11 | -2.0817e-18 | -6.4797e-11 | -1.1914e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.2125e-15 | -120.3131 | 119.9422 | 3.2301e-15 | -120.3131 | 119.9422
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.236e-18 | -1.7439e-11 | -5.0656e-11 | -9.7578e-19 | 1.7439e-11 | 5.0656e-11 | 2.6021e-18 | 4.8598e-11 | 8.9356e-12 | -2.0817e-18 | -4.8598e-11 | -8.9357e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.2301e-15 | -120.3131 | 119.9422 | 3.2613e-15 | -120.3131 | 119.9422
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2526e-19 | -5.8131e-12 | -1.6885e-11 | 5.8547e-19 | 5.8131e-12 | 1.6885e-11 | 5.2042e-19 | 1.6199e-11 | 2.9786e-12 | -1.0408e-18 | -1.6199e-11 | -2.9785e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.2613e-15 | -120.3131 | 119.9422 | 3.2602e-15 | -120.3131 | 119.9422
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5052e-20 | -5.8131e-12 | -1.6885e-11 | 3.2526e-19 | 5.8131e-12 | 1.6885e-11 | 1.0408e-18 | 1.6199e-11 | 2.9786e-12 | -1.5613e-18 | -1.6199e-11 | -2.9786e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.2613e-15 | -120.3131 | 119.9422 | 3.2776e-15 | -120.3131 | 119.9422
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1709e-18 | -4.0692e-11 | -1.182e-10 | -1.1709e-18 | 4.0692e-11 | 1.182e-10 | 2.0817e-18 | 1.1339e-10 | 2.085e-11 | -2.0817e-18 | -1.1339e-10 | -2.085e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89822 | 0.89485 | 0.9 | 0.89822 | 0.89485 | 3.243e-15 | -120.3131 | 119.9422 | 3.3168e-15 | -120.3131 | 119.9422

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0057135 | -0.001643 | -0.006938 | 0.0060135 | 0.001943 | 0.007238 | -0.029079 | -0.041927 | -0.04429 | 0.029679 | 0.042527 | 0.04489 | 94.7873 | -25.2129 | -145.2127 | -85.2127 | 154.7871 | 34.7873 | 0.74088 | 1.049 | 1.1207 | 0.75706 | 1.0643 | 1.1367 | -6.3286 | -117.4569 | 115.8842 | -6.6667 | -117.8288 | 115.6277
Line10_11_12 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0063135 | -0.002243 | -0.007538 | 0.0066135 | 0.002543 | 0.007838 | -0.030279 | -0.043127 | -0.04549 | 0.030879 | 0.043727 | 0.04609 | 94.7873 | -25.2129 | -145.2127 | -85.2127 | 154.7871 | 34.7873 | 0.77326 | 1.0796 | 1.1527 | 0.78948 | 1.095 | 1.1688 | -6.9907 | -118.19 | 115.3784 | -7.3013 | -118.5412 | 115.1359
Line11_12_13 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0066135 | -0.002543 | -0.007838 | 0.0069135 | 0.002843 | 0.008138 | -0.030879 | -0.043727 | -0.04609 | 0.031479 | 0.044327 | 0.04669 | 94.7873 | -25.2129 | -145.2127 | -85.2127 | 154.7871 | 34.7873 | 0.78948 | 1.095 | 1.1688 | 0.80573 | 1.1105 | 1.1848 | -7.3013 | -118.5412 | 115.1359 | -7.5994 | -118.8826 | 114.8999
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.083e-10 | 1.9823e-08 | -1.9662e-08 | 4.8887e-10 | -1.3463e-08 | 1.2504e-08 | 1.7022e-08 | -1.1221e-08 | -8.2938e-09 | -1.1758e-08 | 7.5639e-09 | 5.1237e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80573 | 1.1105 | 1.1848 | 0.80573 | 1.1105 | 1.1848 | -7.5994 | -118.8826 | 114.8999 | -7.5994 | -118.8826 | 114.8999
Line13_13_14 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0069135 | -0.002843 | -0.008138 | 0.0072135 | 0.003143 | 0.008438 | -0.031479 | -0.044327 | -0.04669 | 0.032079 | 0.044927 | 0.04729 | 94.7873 | -25.2128 | -145.2128 | -85.2127 | 154.7872 | 34.7872 | 0.80573 | 1.1105 | 1.1848 | 0.822 | 1.1259 | 1.2009 | -7.5994 | -118.8826 | 114.8999 | -7.8857 | -119.2146 | 114.6703
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0553e-10 | 1.3216e-08 | -1.3108e-08 | 5.9164e-10 | -6.8548e-09 | 5.9503e-09 | 1.1348e-08 | -7.4805e-09 | -5.5292e-09 | -6.0842e-09 | 3.8236e-09 | 2.3591e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80573 | 1.1105 | 1.1848 | 0.80573 | 1.1105 | 1.1848 | -7.5994 | -118.8826 | 114.8999 | -7.5994 | -118.8826 | 114.8999
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0277e-10 | 6.6078e-09 | -6.5541e-09 | 6.944e-10 | -2.4697e-10 | -6.0386e-10 | 5.6739e-09 | -3.7403e-09 | -2.7646e-09 | -4.1024e-10 | 8.3375e-11 | -4.0551e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80573 | 1.1105 | 1.1848 | 0.80573 | 1.1105 | 1.1848 | -7.5994 | -118.8826 | 114.8999 | -7.5994 | -118.8826 | 114.8999
Line16_4_18 | 4.6946 | 0 | 0 | 4.6946 | 0 | 0 | 1.0842 | 0 | 0 | 1.0842 | 0 | 0 | 0.18366 | 1.5593e-08 | -1.5834e-08 | -4.4763e-15 | 4.8229e-11 | -1.3322e-10 | 0.36732 | -6.5439e-09 | -6.8794e-09 | 8.3688e-14 | 7.0145e-10 | -7.9146e-10 | -69.8693 | 0 | 0 | 110.1307 | 0 | 0 | 0.3788 | 1.0402 | 1.0989 | 0 | 1.0202 | 1.0644 | -6.4344 | -113.7775 | 112.4374 | 0 | -109.7129 | 108.8638
Line17_5_19 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0060135 | -0.001943 | -0.007238 | 0.0063135 | 0.002243 | 0.007538 | -0.029679 | -0.042527 | -0.04489 | 0.030279 | 0.043127 | 0.04549 | 94.7873 | -25.2128 | -145.2128 | -85.2127 | 154.7872 | 34.7872 | 0.75706 | 1.0643 | 1.1367 | 0.77326 | 1.0796 | 1.1527 | -6.6667 | -117.8288 | 115.6277 | -6.9907 | -118.19 | 115.3784
Line1_1_3 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0057135 | -0.0016429 | -0.006938 | 0.0060135 | 0.001943 | 0.007238 | -0.029079 | -0.041927 | -0.04429 | 0.029679 | 0.042527 | 0.04489 | 94.7873 | -25.2129 | -145.2127 | -85.2127 | 154.7871 | 34.7873 | 0.74088 | 1.049 | 1.1207 | 0.75706 | 1.0643 | 1.1367 | -6.3286 | -117.4569 | 115.8842 | -6.6667 | -117.8288 | 115.6277
Line2_1_4 | 4.522 | 0.17321 | 0.1732 | 4.522 | 0.17321 | 0.1732 | 1.0443 | 0.04 | 0.04 | 1.0443 | 0.04 | 0.04 | 0.3469 | -0.009374 | -0.015015 | -0.17801 | 0.006674 | 0.017185 | 0.69158 | -0.040899 | -0.04224 | -0.35326 | 0.041071 | 0.040456 | -69.6903 | -14.5476 | -134.5474 | 110.3097 | 165.4524 | 45.4526 | 0.74088 | 1.049 | 1.1207 | 0.3788 | 1.0402 | 1.0989 | -6.3286 | -117.4569 | 115.8842 | -6.4344 | -113.7775 | 112.4374
Line3_1_5 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0057135 | -0.001643 | -0.006938 | 0.0060135 | 0.001943 | 0.007238 | -0.029079 | -0.041927 | -0.04429 | 0.029679 | 0.042527 | 0.04489 | 94.7873 | -25.2128 | -145.2128 | -85.2127 | 154.7872 | 34.7872 | 0.74088 | 1.049 | 1.1207 | 0.75706 | 1.0643 | 1.1367 | -6.3286 | -117.4569 | 115.8842 | -6.6667 | -117.8288 | 115.6277
Line4_2_6 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0060135 | -0.001943 | -0.007238 | 0.0063135 | 0.002243 | 0.007538 | -0.029679 | -0.042527 | -0.04489 | 0.030279 | 0.043127 | 0.04549 | 94.7873 | -25.2129 | -145.2127 | -85.2127 | 154.7871 | 34.7873 | 0.75706 | 1.0643 | 1.1367 | 0.77326 | 1.0796 | 1.1527 | -6.6667 | -117.8288 | 115.6277 | -6.9907 | -118.19 | 115.3784
Line5_6_7 | 0.1732 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0063135 | -0.002243 | -0.007538 | 0.0066135 | 0.002543 | 0.007838 | -0.030279 | -0.043127 | -0.04549 | 0.030879 | 0.043727 | 0.04609 | 94.7873 | -25.2129 | -145.2127 | -85.2127 | 154.7872 | 34.7873 | 0.77326 | 1.0796 | 1.1527 | 0.78948 | 1.095 | 1.1688 | -6.9907 | -118.19 | 115.3784 | -7.3013 | -118.5412 | 115.1359
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4281e-11 | 1.9428e-08 | -1.9568e-08 | 6.7997e-10 | -1.3134e-08 | 1.252e-08 | 1.6643e-08 | -1.1028e-08 | -8.324e-09 | -1.1482e-08 | 7.4593e-09 | 5.1678e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78948 | 1.095 | 1.1688 | 0.78948 | 1.095 | 1.1688 | -7.3013 | -118.5412 | 115.1359 | -7.3013 | -118.5412 | 115.1359
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4761e-11 | 6.476e-09 | -6.5228e-09 | 7.2949e-10 | -1.8215e-10 | -5.2526e-10 | 5.5478e-09 | -3.676e-09 | -2.7747e-09 | -3.8628e-10 | 1.0733e-10 | -3.8155e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78948 | 1.095 | 1.1688 | 0.78948 | 1.095 | 1.1688 | -7.3013 | -118.5412 | 115.1359 | -7.3013 | -118.5412 | 115.1359
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.476e-11 | 6.476e-09 | -6.5228e-09 | 7.2949e-10 | -1.8215e-10 | -5.2526e-10 | 5.5478e-09 | -3.676e-09 | -2.7747e-09 | -3.8628e-10 | 1.0733e-10 | -3.8155e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78948 | 1.095 | 1.1688 | 0.78948 | 1.095 | 1.1688 | -7.3013 | -118.5412 | 115.1359 | -7.3013 | -118.5412 | 115.1359
Line9_3_11 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0060135 | -0.001943 | -0.007238 | 0.0063135 | 0.002243 | 0.007538 | -0.029679 | -0.042527 | -0.04489 | 0.030279 | 0.043127 | 0.04549 | 94.7873 | -25.2129 | -145.2127 | -85.2127 | 154.7871 | 34.7873 | 0.75706 | 1.0643 | 1.1367 | 0.77326 | 1.0796 | 1.1527 | -6.6667 | -117.8288 | 115.6277 | -6.9907 | -118.19 | 115.3784

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0059968 | -0.0016499 | -0.0073772 | 0.0062968 | 0.0019499 | 0.0076772 | -0.029966 | -0.043844 | -0.046373 | 0.030566 | 0.044444 | 0.046973 | 94.787 | -25.2132 | -145.213 | -85.213 | 154.7868 | 34.787 | 0.764 | 1.0969 | 1.1739 | 0.7802 | 1.1122 | 1.1899 | -6.5297 | -117.3683 | 115.7479 | -6.8536 | -117.7254 | 115.5048
Line10_11_12 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0065968 | -0.0022499 | -0.0079772 | 0.0068968 | 0.0025499 | 0.0082772 | -0.031166 | -0.045044 | -0.047573 | 0.031766 | 0.045644 | 0.048173 | 94.787 | -25.2132 | -145.213 | -85.213 | 154.7868 | 34.787 | 0.79641 | 1.1275 | 1.2059 | 0.81265 | 1.1429 | 1.222 | -7.1643 | -118.0727 | 115.268 | -7.4626 | -118.4107 | 115.0375
Line11_12_13 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0068968 | -0.0025499 | -0.0082772 | 0.0071968 | 0.0028499 | 0.0085772 | -0.031766 | -0.045644 | -0.048173 | 0.032366 | 0.046244 | 0.048773 | 94.787 | -25.2132 | -145.213 | -85.213 | 154.7868 | 34.7869 | 0.81265 | 1.1429 | 1.222 | 0.82891 | 1.1583 | 1.238 | -7.4626 | -118.4107 | 115.0375 | -7.7493 | -118.7398 | 114.813
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5753e-10 | 2.2287e-08 | -2.2237e-08 | 6.2171e-10 | -1.5106e-08 | 1.4178e-08 | 1.8875e-08 | -1.2521e-08 | -9.4115e-09 | -1.3034e-08 | 8.4498e-09 | 5.8229e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82891 | 1.1583 | 1.238 | 0.82891 | 1.1583 | 1.238 | -7.7493 | -118.7398 | 114.813 | -7.7493 | -118.7398 | 114.813
Line13_13_14 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0071968 | -0.0028499 | -0.0085772 | 0.0074968 | 0.00315 | 0.0088772 | -0.032366 | -0.046244 | -0.048773 | 0.032966 | 0.046844 | 0.049373 | 94.787 | -25.2132 | -145.2131 | -85.213 | 154.7869 | 34.7869 | 0.82891 | 1.1583 | 1.238 | 0.84519 | 1.1737 | 1.2541 | -7.7493 | -118.7398 | 114.813 | -8.0249 | -119.0601 | 114.5942
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7169e-10 | 1.4858e-08 | -1.4825e-08 | 7.0756e-10 | -7.6776e-09 | 6.7652e-09 | 1.2584e-08 | -8.3471e-09 | -6.2744e-09 | -6.7426e-09 | 4.2763e-09 | 2.6857e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82891 | 1.1583 | 1.238 | 0.82891 | 1.1583 | 1.238 | -7.7493 | -118.7398 | 114.813 | -7.7493 | -118.7398 | 114.813
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5843e-11 | 7.4289e-09 | -7.4124e-09 | 7.934e-10 | -2.4866e-10 | -6.4712e-10 | 6.2918e-09 | -4.1736e-09 | -3.1372e-09 | -4.508e-10 | 1.0275e-10 | -4.5144e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82891 | 1.1583 | 1.238 | 0.82891 | 1.1583 | 1.238 | -7.7493 | -118.7398 | 114.813 | -7.7493 | -118.7398 | 114.813
Line16_4_18 | 4.8379 | 0 | 0 | 4.8379 | 0 | 0 | 1.1173 | 0 | 0 | 1.1173 | 0 | 0 | 0.19505 | 1.7135e-08 | -1.7406e-08 | 1.2265e-13 | 5.8768e-11 | -1.4627e-10 | 0.39009 | -7.1339e-09 | -7.5789e-09 | -1.5346e-13 | 7.6793e-10 | -8.6977e-10 | -70.0684 | 0 | 0 | 109.9316 | 0 | 0 | 0.39036 | 1.0877 | 1.1508 | 0 | 1.0673 | 1.115 | -6.6335 | -113.7334 | 112.3598 | 0 | -109.7244 | 108.8486
Line17_5_19 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0062968 | -0.0019499 | -0.0076772 | 0.0065968 | 0.0022499 | 0.0079772 | -0.030566 | -0.044444 | -0.046973 | 0.031166 | 0.045044 | 0.047573 | 94.787 | -25.2132 | -145.2131 | -85.213 | 154.7869 | 34.7869 | 0.7802 | 1.1122 | 1.1899 | 0.79641 | 1.1275 | 1.2059 | -6.8536 | -117.7254 | 115.5048 | -7.1643 | -118.0727 | 115.268
Line1_1_3 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0059968 | -0.0016499 | -0.0073772 | 0.0062968 | 0.0019499 | 0.0076772 | -0.029966 | -0.043844 | -0.046373 | 0.030566 | 0.044444 | 0.046973 | 94.787 | -25.2132 | -145.213 | -85.213 | 154.7868 | 34.787 | 0.764 | 1.0969 | 1.1739 | 0.7802 | 1.1122 | 1.1899 | -6.5297 | -117.3683 | 115.7479 | -6.8536 | -117.7254 | 115.5048
Line2_1_4 | 4.6653 | 0.17321 | 0.1732 | 4.6653 | 0.17321 | 0.1732 | 1.0774 | 0.04 | 0.04 | 1.0774 | 0.04 | 0.04 | 0.36904 | -0.0095458 | -0.015636 | -0.18924 | 0.0067546 | 0.017866 | 0.73578 | -0.042824 | -0.044277 | -0.3756 | 0.04298 | 0.042422 | -69.8929 | -14.802 | -134.8018 | 110.1071 | 165.198 | 45.1982 | 0.764 | 1.0969 | 1.1739 | 0.39036 | 1.0877 | 1.1508 | -6.5297 | -117.3683 | 115.7479 | -6.6335 | -113.7334 | 112.3598
Line3_1_5 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0059968 | -0.0016499 | -0.0073772 | 0.0062968 | 0.0019499 | 0.0076772 | -0.029966 | -0.043844 | -0.046373 | 0.030566 | 0.044444 | 0.046973 | 94.787 | -25.2132 | -145.2131 | -85.213 | 154.7868 | 34.7869 | 0.764 | 1.0969 | 1.1739 | 0.7802 | 1.1122 | 1.1899 | -6.5297 | -117.3683 | 115.7479 | -6.8536 | -117.7254 | 115.5048
Line4_2_6 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0062968 | -0.0019499 | -0.0076772 | 0.0065968 | 0.0022499 | 0.0079772 | -0.030566 | -0.044444 | -0.046973 | 0.031166 | 0.045044 | 0.047573 | 94.787 | -25.2132 | -145.213 | -85.213 | 154.7868 | 34.7869 | 0.7802 | 1.1122 | 1.1899 | 0.79641 | 1.1275 | 1.2059 | -6.8536 | -117.7254 | 115.5048 | -7.1643 | -118.0727 | 115.268
Line5_6_7 | 0.1732 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0065968 | -0.0022499 | -0.0079772 | 0.0068968 | 0.0025499 | 0.0082772 | -0.031166 | -0.045044 | -0.047573 | 0.031766 | 0.045644 | 0.048173 | 94.787 | -25.2132 | -145.2131 | -85.213 | 154.7868 | 34.7869 | 0.79641 | 1.1275 | 1.2059 | 0.81265 | 1.1429 | 1.222 | -7.1643 | -118.0727 | 115.268 | -7.4626 | -118.4107 | 115.0375
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4642e-11 | 2.1867e-08 | -2.2128e-08 | 8.1869e-10 | -1.4759e-08 | 1.4187e-08 | 1.8469e-08 | -1.2311e-08 | -9.4406e-09 | -1.2738e-08 | 8.3353e-09 | 5.8674e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81265 | 1.1429 | 1.222 | 0.81265 | 1.1429 | 1.222 | -7.4626 | -118.4107 | 115.0375 | -7.4626 | -118.4107 | 115.0375
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8808e-12 | 7.289e-09 | -7.3759e-09 | 8.2846e-10 | -1.8142e-10 | -5.6504e-10 | 6.1564e-09 | -4.1037e-09 | -3.1469e-09 | -4.2571e-10 | 1.2784e-10 | -4.2635e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81265 | 1.1429 | 1.222 | 0.81265 | 1.1429 | 1.222 | -7.4626 | -118.4107 | 115.0375 | -7.4626 | -118.4107 | 115.0375
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8807e-12 | 7.289e-09 | -7.3759e-09 | 8.2846e-10 | -1.8142e-10 | -5.6504e-10 | 6.1564e-09 | -4.1037e-09 | -3.1469e-09 | -4.2571e-10 | 1.2784e-10 | -4.2635e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81265 | 1.1429 | 1.222 | 0.81265 | 1.1429 | 1.222 | -7.4626 | -118.4107 | 115.0375 | -7.4626 | -118.4107 | 115.0375
Line9_3_11 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0062968 | -0.0019499 | -0.0076772 | 0.0065968 | 0.0022499 | 0.0079772 | -0.030566 | -0.044444 | -0.046973 | 0.031166 | 0.045044 | 0.047573 | 94.787 | -25.2132 | -145.213 | -85.213 | 154.7868 | 34.787 | 0.7802 | 1.1122 | 1.1899 | 0.79641 | 1.1275 | 1.2059 | -6.8536 | -117.7254 | 115.5048 | -7.1643 | -118.0727 | 115.268

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036745 | -0.0036034 | -0.0036334 | 0.0039745 | 0.0039034 | 0.0039334 | -0.044533 | -0.044611 | -0.044645 | 0.045133 | 0.045211 | 0.045245 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1171 | 1.1189 | 1.1198 | 1.1327 | 1.1345 | 1.1354 | 0.07034 | -119.8307 | 120.1346 | -0.24536 | -120.1472 | 119.8187
Line10_11_12 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0042745 | -0.0042034 | -0.0042334 | 0.0045745 | 0.0045034 | 0.0045334 | -0.045733 | -0.045811 | -0.045845 | 0.046333 | 0.046411 | 0.046445 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1483 | 1.1501 | 1.151 | 1.164 | 1.1657 | 1.1667 | -0.55248 | -120.4552 | 119.5115 | -0.85136 | -120.7549 | 119.2124
Line11_12_13 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0045745 | -0.0045034 | -0.0045334 | 0.0048745 | 0.0048034 | 0.0048334 | -0.046333 | -0.046411 | -0.046445 | 0.046933 | 0.047011 | 0.047045 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.164 | 1.1657 | 1.1667 | 1.1796 | 1.1814 | 1.1823 | -0.85136 | -120.7549 | 119.2124 | -1.1423 | -121.0467 | 118.9213
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7677e-09 | 1.8106e-09 | 1.5398e-09 | -1.74e-09 | -1.777e-09 | -1.601e-09 | 4.3534e-10 | 9.5615e-11 | 2.4672e-10 | -3.8076e-10 | -1.4683e-10 | -2.5017e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1796 | 1.1814 | 1.1823 | 1.1796 | 1.1814 | 1.1823 | -1.1423 | -121.0467 | 118.9213 | -1.1423 | -121.0467 | 118.9213
Line13_13_14 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0048745 | -0.0048034 | -0.0048334 | 0.0051745 | 0.0051034 | 0.0051334 | -0.046933 | -0.047011 | -0.047045 | 0.047533 | 0.047611 | 0.047645 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1796 | 1.1814 | 1.1823 | 1.1953 | 1.1971 | 1.198 | -1.1423 | -121.0467 | 118.9213 | -1.4256 | -121.3309 | 118.6378
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1784e-09 | 1.2071e-09 | 1.0265e-09 | -1.1508e-09 | -1.1735e-09 | -1.0877e-09 | 2.9022e-10 | 6.3743e-11 | 1.6448e-10 | -2.3565e-10 | -1.1496e-10 | -1.6793e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1796 | 1.1814 | 1.1823 | 1.1796 | 1.1814 | 1.1823 | -1.1423 | -121.0467 | 118.9213 | -1.1423 | -121.0467 | 118.9213
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8922e-10 | 6.0354e-10 | 5.1326e-10 | -5.6161e-10 | -5.6995e-10 | -5.7446e-10 | 1.4511e-10 | 3.1872e-11 | 8.224e-11 | -9.0539e-11 | -8.3089e-11 | -8.5693e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1796 | 1.1814 | 1.1823 | 1.1796 | 1.1814 | 1.1823 | -1.1423 | -121.0467 | 118.9213 | -1.1423 | -121.0467 | 118.9213
Line16_4_18 | 0.036838 | 0 | 0 | 0.036838 | 0 | 0 | 0.0085073 | 0 | 0 | 0.0085073 | 0 | 0 | 0.0067964 | 4.4121e-10 | 2.1656e-10 | -0.0067851 | -3.514e-10 | -3.5839e-10 | 0.0068077 | -1.1527e-10 | -1.4582e-11 | -0.0067851 | 3.334e-12 | -6.7998e-12 | -45.1891 | 0 | 0 | 134.8109 | 0 | 0 | 1.1307 | 1.1349 | 1.1362 | 1.1279 | 1.1345 | 1.136 | -0.14145 | -119.9763 | 119.9403 | -0.18907 | -119.9563 | 119.9109
Line17_5_19 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039745 | -0.0039034 | -0.0039334 | 0.0042745 | 0.0042034 | 0.0042334 | -0.045133 | -0.045211 | -0.045245 | 0.045733 | 0.045811 | 0.045845 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1327 | 1.1345 | 1.1354 | 1.1483 | 1.1501 | 1.151 | -0.24536 | -120.1472 | 119.8187 | -0.55248 | -120.4552 | 119.5115
Line1_1_3 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036745 | -0.0036034 | -0.0036334 | 0.0039745 | 0.0039034 | 0.0039334 | -0.044533 | -0.044611 | -0.044645 | 0.045133 | 0.045211 | 0.045245 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1171 | 1.1189 | 1.1198 | 1.1327 | 1.1345 | 1.1354 | 0.07034 | -119.8307 | 120.1346 | -0.24536 | -120.1472 | 119.8187
Line2_1_4 | 0.14225 | 0.17321 | 0.1732 | 0.14225 | 0.17321 | 0.1732 | 0.032851 | 0.04 | 0.04 | 0.032851 | 0.04 | 0.04 | -0.0051632 | -0.011797 | -0.011833 | 0.0053621 | 0.012077 | 0.012154 | -0.036333 | -0.043174 | -0.043202 | 0.036757 | 0.043761 | 0.043791 | 98.1583 | -14.5475 | -134.5475 | -81.8417 | 165.4525 | 45.4525 | 1.1171 | 1.1189 | 1.1198 | 1.1307 | 1.1349 | 1.1362 | 0.07034 | -119.8307 | 120.1346 | -0.14145 | -119.9763 | 119.9403
Line3_1_5 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036745 | -0.0036034 | -0.0036334 | 0.0039745 | 0.0039034 | 0.0039334 | -0.044533 | -0.044611 | -0.044645 | 0.045133 | 0.045211 | 0.045245 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1171 | 1.1189 | 1.1198 | 1.1327 | 1.1345 | 1.1354 | 0.07034 | -119.8307 | 120.1346 | -0.24536 | -120.1472 | 119.8187
Line4_2_6 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039745 | -0.0039034 | -0.0039334 | 0.0042745 | 0.0042034 | 0.0042334 | -0.045133 | -0.045211 | -0.045245 | 0.045733 | 0.045811 | 0.045845 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1327 | 1.1345 | 1.1354 | 1.1483 | 1.1501 | 1.151 | -0.24536 | -120.1472 | 119.8187 | -0.55248 | -120.4552 | 119.5115
Line5_6_7 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0042745 | -0.0042034 | -0.0042334 | 0.0045745 | 0.0045034 | 0.0045334 | -0.045733 | -0.045811 | -0.045845 | 0.046333 | 0.046411 | 0.046445 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1483 | 1.1501 | 1.151 | 1.164 | 1.1657 | 1.1667 | -0.55248 | -120.4552 | 119.5115 | -0.85136 | -120.7549 | 119.2124
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5414e-09 | 1.5854e-09 | 1.3172e-09 | -1.5144e-09 | -1.552e-09 | -1.3775e-09 | 3.6171e-10 | 2.6298e-11 | 1.7407e-10 | -3.0772e-10 | -7.6666e-11 | -1.7779e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.164 | 1.1657 | 1.1667 | 1.164 | 1.1657 | 1.1667 | -0.85136 | -120.7549 | 119.2124 | -0.85136 | -120.7549 | 119.2124
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.138e-10 | 5.2846e-10 | 4.3906e-10 | -4.8683e-10 | -4.9505e-10 | -4.9943e-10 | 1.2057e-10 | 8.7658e-12 | 5.8025e-11 | -6.6584e-11 | -5.9134e-11 | -6.1738e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.164 | 1.1657 | 1.1667 | 1.164 | 1.1657 | 1.1667 | -0.85136 | -120.7549 | 119.2124 | -0.85136 | -120.7549 | 119.2124
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.138e-10 | 5.2846e-10 | 4.3906e-10 | -4.8683e-10 | -4.9505e-10 | -4.9943e-10 | 1.2057e-10 | 8.7659e-12 | 5.8025e-11 | -6.6584e-11 | -5.9134e-11 | -6.1738e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.164 | 1.1657 | 1.1667 | 1.164 | 1.1657 | 1.1667 | -0.85136 | -120.7549 | 119.2124 | -0.85136 | -120.7549 | 119.2124
Line9_3_11 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039745 | -0.0039034 | -0.0039334 | 0.0042745 | 0.0042034 | 0.0042334 | -0.045133 | -0.045211 | -0.045245 | 0.045733 | 0.045811 | 0.045845 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1327 | 1.1345 | 1.1354 | 1.1483 | 1.1501 | 1.151 | -0.24536 | -120.1472 | 119.8187 | -0.55248 | -120.4552 | 119.5115

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0038556 | -0.0037776 | -0.0038106 | 0.0041556 | 0.0040776 | 0.0041106 | -0.046648 | -0.046734 | -0.046771 | 0.047248 | 0.047334 | 0.047371 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1702 | 1.1722 | 1.1732 | 1.1858 | 1.1877 | 1.1887 | 0.061974 | -119.8344 | 120.1292 | -0.23949 | -120.1368 | 119.8276
Line10_11_12 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0044556 | -0.0043776 | -0.0044106 | 0.0047556 | 0.0046776 | 0.0047106 | -0.047848 | -0.047934 | -0.047971 | 0.048448 | 0.048534 | 0.048571 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.2014 | 1.2033 | 1.2043 | 1.217 | 1.219 | 1.22 | -0.53313 | -120.4313 | 119.5338 | -0.81923 | -120.7182 | 119.2475
Line11_12_13 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0047556 | -0.0046776 | -0.0047106 | 0.0050556 | 0.0049776 | 0.0050106 | -0.048448 | -0.048534 | -0.048571 | 0.049048 | 0.049134 | 0.049171 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.217 | 1.219 | 1.22 | 1.2327 | 1.2346 | 1.2356 | -0.81923 | -120.7182 | 119.2475 | -1.0981 | -120.9979 | 118.9685
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8966e-09 | 1.9462e-09 | 1.6359e-09 | -1.8651e-09 | -1.9077e-09 | -1.7059e-09 | 4.7335e-10 | 8.4363e-11 | 2.5709e-10 | -4.1084e-10 | -1.4296e-10 | -2.6111e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2327 | 1.2346 | 1.2356 | 1.2327 | 1.2346 | 1.2356 | -1.0981 | -120.9979 | 118.9685 | -1.0981 | -120.9979 | 118.9685
Line13_13_14 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0050556 | -0.0049776 | -0.0050106 | 0.0053556 | 0.0052776 | 0.0053106 | -0.049048 | -0.049134 | -0.049171 | 0.049648 | 0.049734 | 0.049771 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.2327 | 1.2346 | 1.2356 | 1.2484 | 1.2503 | 1.2513 | -1.0981 | -120.9979 | 118.9685 | -1.3699 | -121.2705 | 118.6965
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2644e-09 | 1.2974e-09 | 1.0906e-09 | -1.2329e-09 | -1.2589e-09 | -1.1607e-09 | 3.1556e-10 | 5.6242e-11 | 1.7139e-10 | -2.5306e-10 | -1.1484e-10 | -1.7541e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2327 | 1.2346 | 1.2356 | 1.2327 | 1.2346 | 1.2356 | -1.0981 | -120.9979 | 118.9685 | -1.0981 | -120.9979 | 118.9685
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3221e-10 | 6.4872e-10 | 5.4529e-10 | -6.0066e-10 | -6.1021e-10 | -6.1536e-10 | 1.5778e-10 | 2.8121e-11 | 8.5697e-11 | -9.5278e-11 | -8.6722e-11 | -8.9716e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2327 | 1.2346 | 1.2356 | 1.2327 | 1.2346 | 1.2356 | -1.0981 | -120.9979 | 118.9685 | -1.0981 | -120.9979 | 118.9685
Line16_4_18 | 0.038562 | 0 | 0 | 0.038562 | 0 | 0 | 0.0089055 | 0 | 0 | 0.0089055 | 0 | 0 | 0.0074475 | 4.8185e-10 | 2.3118e-10 | -0.0074351 | -3.8173e-10 | -3.896e-10 | 0.0074598 | -1.2881e-10 | -1.6089e-11 | -0.0074351 | 3.6724e-12 | -7.5789e-12 | -45.1935 | 0 | 0 | 134.8065 | 0 | 0 | 1.1837 | 1.1881 | 1.1895 | 1.1807 | 1.1877 | 1.1893 | -0.14587 | -119.9761 | 119.9388 | -0.1935 | -119.9561 | 119.9095
Line17_5_19 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0041556 | -0.0040776 | -0.0041106 | 0.0044556 | 0.0043776 | 0.0044106 | -0.047248 | -0.047334 | -0.047371 | 0.047848 | 0.047934 | 0.047971 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1858 | 1.1877 | 1.1887 | 1.2014 | 1.2033 | 1.2043 | -0.23949 | -120.1368 | 119.8276 | -0.53313 | -120.4313 | 119.5338
Line1_1_3 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0038556 | -0.0037776 | -0.0038106 | 0.0041556 | 0.0040776 | 0.0041106 | -0.046648 | -0.046734 | -0.046771 | 0.047248 | 0.047334 | 0.047371 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1702 | 1.1722 | 1.1732 | 1.1858 | 1.1877 | 1.1887 | 0.061974 | -119.8344 | 120.1292 | -0.23949 | -120.1368 | 119.8276
Line2_1_4 | 0.14097 | 0.17321 | 0.1732 | 0.14097 | 0.17321 | 0.1732 | 0.032556 | 0.04 | 0.04 | 0.032556 | 0.04 | 0.04 | -0.0048861 | -0.012161 | -0.0122 | 0.0050811 | 0.01244 | 0.012522 | -0.037782 | -0.045281 | -0.045312 | 0.038199 | 0.045868 | 0.045901 | 97.4309 | -14.8019 | -134.8019 | -82.5691 | 165.1981 | 45.1981 | 1.1702 | 1.1722 | 1.1732 | 1.1837 | 1.1881 | 1.1895 | 0.061974 | -119.8344 | 120.1292 | -0.14587 | -119.9761 | 119.9388
Line3_1_5 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0038556 | -0.0037776 | -0.0038106 | 0.0041556 | 0.0040776 | 0.0041106 | -0.046648 | -0.046734 | -0.046771 | 0.047248 | 0.047334 | 0.047371 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1702 | 1.1722 | 1.1732 | 1.1858 | 1.1877 | 1.1887 | 0.061974 | -119.8344 | 120.1292 | -0.23949 | -120.1368 | 119.8276
Line4_2_6 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0041556 | -0.0040776 | -0.0041106 | 0.0044556 | 0.0043776 | 0.0044106 | -0.047248 | -0.047334 | -0.047371 | 0.047848 | 0.047934 | 0.047971 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1858 | 1.1877 | 1.1887 | 1.2014 | 1.2033 | 1.2043 | -0.23949 | -120.1368 | 119.8276 | -0.53313 | -120.4313 | 119.5338
Line5_6_7 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0044556 | -0.0043776 | -0.0044106 | 0.0047556 | 0.0046776 | 0.0047106 | -0.047848 | -0.047934 | -0.047971 | 0.048448 | 0.048534 | 0.048571 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.2014 | 1.2033 | 1.2043 | 1.217 | 1.219 | 1.22 | -0.53313 | -120.4313 | 119.5338 | -0.81923 | -120.7182 | 119.2475
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6606e-09 | 1.7112e-09 | 1.4038e-09 | -1.6297e-09 | -1.6729e-09 | -1.473e-09 | 3.9613e-10 | 1.1866e-11 | 1.8095e-10 | -3.3427e-10 | -6.9537e-11 | -1.8525e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.217 | 1.219 | 1.22 | 1.217 | 1.219 | 1.22 | -0.81923 | -120.7182 | 119.2475 | -0.81923 | -120.7182 | 119.2475
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5352e-10 | 5.704e-10 | 4.6794e-10 | -5.2267e-10 | -5.3209e-10 | -5.371e-10 | 1.3204e-10 | 3.9553e-12 | 6.0315e-11 | -7.0182e-11 | -6.1627e-11 | -6.462e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.217 | 1.219 | 1.22 | 1.217 | 1.219 | 1.22 | -0.81923 | -120.7182 | 119.2475 | -0.81923 | -120.7182 | 119.2475
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5352e-10 | 5.704e-10 | 4.6794e-10 | -5.2267e-10 | -5.3209e-10 | -5.371e-10 | 1.3204e-10 | 3.9553e-12 | 6.0316e-11 | -7.0182e-11 | -6.1627e-11 | -6.462e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.217 | 1.219 | 1.22 | 1.217 | 1.219 | 1.22 | -0.81923 | -120.7182 | 119.2475 | -0.81923 | -120.7182 | 119.2475
Line9_3_11 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0041556 | -0.0040776 | -0.0041106 | 0.0044556 | 0.0043776 | 0.0044106 | -0.047248 | -0.047334 | -0.047371 | 0.047848 | 0.047934 | 0.047971 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1858 | 1.1877 | 1.1887 | 1.2014 | 1.2033 | 1.2043 | -0.23949 | -120.1368 | 119.8276 | -0.53313 | -120.4313 | 119.5338

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0869e-09 | 1.8644e-08 | -2.823e-08 | -3.6253e-09 | -1.534e-08 | 2.3465e-08 | 2.1729e-08 | -1.8708e-08 | -4.9233e-09 | -1.8556e-08 | 1.566e-08 | 3.8846e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0869e-09 | 1.8644e-08 | -2.823e-08 | -3.6253e-09 | -1.534e-08 | 2.3465e-08 | 2.1729e-08 | -1.8708e-08 | -4.9233e-09 | -1.8556e-08 | 1.566e-08 | 3.8846e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2391e-09 | 1.5536e-08 | -2.3525e-08 | -2.7775e-09 | -1.2233e-08 | 1.876e-08 | 1.8107e-08 | -1.559e-08 | -4.1027e-09 | -1.4935e-08 | 1.2542e-08 | 3.0641e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5435e-09 | 9.3219e-09 | -1.4115e-08 | -1.0819e-09 | -6.018e-09 | 9.3497e-09 | 1.0864e-08 | -9.3539e-09 | -2.4616e-09 | -7.692e-09 | 6.3056e-09 | 1.423e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4782e-10 | 3.1073e-09 | -4.7051e-09 | 6.1377e-10 | 1.966e-10 | -6.0435e-11 | 3.6214e-09 | -3.118e-09 | -8.2055e-10 | -4.4915e-10 | 6.9703e-11 | -2.181e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6956e-09 | 6.2146e-09 | -9.4101e-09 | -2.3406e-10 | -2.9107e-09 | 4.6446e-09 | 7.2429e-09 | -6.2359e-09 | -1.6411e-09 | -4.0706e-09 | 3.1877e-09 | 6.0244e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4782e-10 | 3.1073e-09 | -4.7051e-09 | 6.1377e-10 | 1.966e-10 | -6.0435e-11 | 3.6214e-09 | -3.118e-09 | -8.2055e-10 | -4.4915e-10 | 6.9703e-11 | -2.181e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line16_4_18 | 3.4541 | 0 | 0 | 3.4541 | 0 | 0 | 0.7977 | 0 | 0 | 0.7977 | 0 | 0 | 0.1909 | 1.0508e-08 | -1.1499e-08 | -7.9008e-14 | 2.4582e-10 | 1.4437e-10 | 0.19885 | -5.024e-09 | -4.5734e-09 | 8.2324e-14 | 5.2427e-10 | -5.8284e-10 | -56.9218 | 0 | 0 | 123.0782 | 0 | 0 | 0.34556 | 0.87066 | 0.9251 | 0 | 0.85701 | 0.88871 | -10.7527 | -114.3803 | 112.861 | 0 | -109.8853 | 109.1478
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4782e-10 | 3.1073e-09 | -4.705e-09 | 6.1377e-10 | 1.966e-10 | -6.0435e-11 | 3.6214e-09 | -3.118e-09 | -8.2054e-10 | -4.4915e-10 | 6.9703e-11 | -2.181e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7826e-09 | 2.4858e-08 | -3.764e-08 | -5.321e-09 | -2.1554e-08 | 3.2875e-08 | 2.8971e-08 | -2.4944e-08 | -6.5644e-09 | -2.5799e-08 | 2.1896e-08 | 5.5257e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line2_1_4 | 3.4541 | 0 | 0 | 3.4541 | 0 | 0 | 0.7977 | 0 | 0 | 0.7977 | 0 | 0 | 0.38179 | 1.5804e-08 | -1.8773e-08 | -0.1909 | -1.0269e-08 | 1.1559e-08 | 0.3977 | -1.0055e-08 | -7.786e-09 | -0.19885 | 5.321e-09 | 4.173e-09 | -56.9218 | 0 | 0 | 123.0782 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.34556 | 0.87066 | 0.9251 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -114.3803 | 112.861
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6956e-09 | 6.2146e-09 | -9.4101e-09 | -2.3406e-10 | -2.9107e-09 | 4.6446e-09 | 7.2429e-09 | -6.2359e-09 | -1.6411e-09 | -4.0706e-09 | 3.1877e-09 | 6.0244e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2391e-09 | 1.5536e-08 | -2.3525e-08 | -2.7775e-09 | -1.2233e-08 | 1.876e-08 | 1.8107e-08 | -1.559e-08 | -4.1027e-09 | -1.4935e-08 | 1.2542e-08 | 3.0641e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3913e-09 | 1.2429e-08 | -1.882e-08 | -1.9297e-09 | -9.1253e-09 | 1.4055e-08 | 1.4486e-08 | -1.2472e-08 | -3.2822e-09 | -1.1313e-08 | 9.4236e-09 | 2.2435e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5435e-09 | 9.3219e-09 | -1.4115e-08 | -1.0819e-09 | -6.018e-09 | 9.3497e-09 | 1.0864e-08 | -9.3539e-09 | -2.4616e-09 | -7.692e-09 | 6.3056e-09 | 1.423e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4782e-10 | 3.1073e-09 | -4.705e-09 | 6.1377e-10 | 1.966e-10 | -6.0435e-11 | 3.6214e-09 | -3.118e-09 | -8.2054e-10 | -4.4915e-10 | 6.9703e-11 | -2.181e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4782e-10 | 3.1073e-09 | -4.705e-09 | 6.1377e-10 | 1.966e-10 | -6.0435e-11 | 3.6214e-09 | -3.118e-09 | -8.2054e-10 | -4.4915e-10 | 6.9703e-11 | -2.181e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9348e-09 | 2.1751e-08 | -3.2935e-08 | -4.4732e-09 | -1.8447e-08 | 2.817e-08 | 2.535e-08 | -2.1826e-08 | -5.7438e-09 | -2.2178e-08 | 1.8778e-08 | 4.7052e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69112 | 0.88948 | 0.96508 | 0.69112 | 0.88948 | 0.96508 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5656e-09 | 1.6733e-08 | -2.5337e-08 | -3.2538e-09 | -1.3768e-08 | 2.106e-08 | 1.9502e-08 | -1.679e-08 | -4.4187e-09 | -1.6654e-08 | 1.4055e-08 | 3.4865e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5656e-09 | 1.6733e-08 | -2.5337e-08 | -3.2538e-09 | -1.3768e-08 | 2.106e-08 | 1.9502e-08 | -1.679e-08 | -4.4187e-09 | -1.6654e-08 | 1.4055e-08 | 3.4865e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8046e-09 | 1.3944e-08 | -2.1114e-08 | -2.4928e-09 | -1.0979e-08 | 1.6837e-08 | 1.6251e-08 | -1.3992e-08 | -3.6822e-09 | -1.3404e-08 | 1.1256e-08 | 2.75e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2828e-09 | 8.3665e-09 | -1.2668e-08 | -9.7099e-10 | -5.4012e-09 | 8.3914e-09 | 9.7508e-09 | -8.3952e-09 | -2.2093e-09 | -6.9036e-09 | 5.6594e-09 | 1.2771e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6093e-10 | 2.7888e-09 | -4.2228e-09 | 5.5086e-10 | 1.7645e-10 | -5.4241e-11 | 3.2503e-09 | -2.7984e-09 | -7.3645e-10 | -4.0311e-10 | 6.2559e-11 | -1.9575e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5219e-09 | 5.5776e-09 | -8.4456e-09 | -2.1007e-10 | -2.6124e-09 | 4.1686e-09 | 6.5005e-09 | -5.5968e-09 | -1.4729e-09 | -3.6534e-09 | 2.861e-09 | 5.407e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6093e-10 | 2.7888e-09 | -4.2228e-09 | 5.5086e-10 | 1.7645e-10 | -5.4241e-11 | 3.2503e-09 | -2.7984e-09 | -7.3645e-10 | -4.0311e-10 | 6.2559e-11 | -1.9575e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line16_4_18 | 3.2723 | 0 | 0 | 3.2723 | 0 | 0 | 0.75571 | 0 | 0 | 0.75571 | 0 | 0 | 0.17133 | 9.431e-09 | -1.0321e-08 | -7.0941e-14 | 2.2062e-10 | 1.2957e-10 | 0.17847 | -4.5091e-09 | -4.1047e-09 | 7.3943e-14 | 4.7053e-10 | -5.231e-10 | -56.9218 | 0 | 0 | 123.0782 | 0 | 0 | 0.32737 | 0.82483 | 0.87641 | 0 | 0.8119 | 0.84193 | -10.7527 | -114.3803 | 112.861 | 0 | -109.8853 | 109.1478
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6093e-10 | 2.7888e-09 | -4.2228e-09 | 5.5086e-10 | 1.7645e-10 | -5.4241e-11 | 3.2503e-09 | -2.7984e-09 | -7.3644e-10 | -4.0311e-10 | 6.2559e-11 | -1.9575e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0874e-09 | 2.2311e-08 | -3.3783e-08 | -4.7756e-09 | -1.9345e-08 | 2.9505e-08 | 2.6002e-08 | -2.2387e-08 | -5.8916e-09 | -2.3155e-08 | 1.9651e-08 | 4.9594e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line2_1_4 | 3.2723 | 0 | 0 | 3.2723 | 0 | 0 | 0.75571 | 0 | 0 | 0.75571 | 0 | 0 | 0.34266 | 1.4184e-08 | -1.6849e-08 | -0.17133 | -9.2167e-09 | 1.0374e-08 | 0.35694 | -9.0244e-09 | -6.988e-09 | -0.17847 | 4.7756e-09 | 3.7453e-09 | -56.9218 | 0 | 0 | 123.0782 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.32737 | 0.82483 | 0.87641 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -114.3803 | 112.861
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5219e-09 | 5.5776e-09 | -8.4456e-09 | -2.1007e-10 | -2.6124e-09 | 4.1686e-09 | 6.5005e-09 | -5.5968e-09 | -1.4729e-09 | -3.6534e-09 | 2.861e-09 | 5.4069e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8046e-09 | 1.3944e-08 | -2.1114e-08 | -2.4928e-09 | -1.0979e-08 | 1.6837e-08 | 1.6251e-08 | -1.3992e-08 | -3.6822e-09 | -1.3404e-08 | 1.1256e-08 | 2.75e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0437e-09 | 1.1155e-08 | -1.6891e-08 | -1.7319e-09 | -8.19e-09 | 1.2614e-08 | 1.3001e-08 | -1.1194e-08 | -2.9458e-09 | -1.0154e-08 | 8.4578e-09 | 2.0136e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2828e-09 | 8.3664e-09 | -1.2668e-08 | -9.7099e-10 | -5.4012e-09 | 8.3914e-09 | 9.7508e-09 | -8.3952e-09 | -2.2093e-09 | -6.9036e-09 | 5.6594e-09 | 1.2771e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6093e-10 | 2.7888e-09 | -4.2228e-09 | 5.5086e-10 | 1.7645e-10 | -5.4241e-11 | 3.2503e-09 | -2.7984e-09 | -7.3644e-10 | -4.0311e-10 | 6.2559e-11 | -1.9575e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6093e-10 | 2.7888e-09 | -4.2228e-09 | 5.5086e-10 | 1.7645e-10 | -5.4241e-11 | 3.2503e-09 | -2.7984e-09 | -7.3644e-10 | -4.0311e-10 | 6.2559e-11 | -1.9575e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3265e-09 | 1.9522e-08 | -2.956e-08 | -4.0147e-09 | -1.6556e-08 | 2.5283e-08 | 2.2752e-08 | -1.9589e-08 | -5.1551e-09 | -1.9905e-08 | 1.6853e-08 | 4.2229e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65474 | 0.84266 | 0.91428 | 0.65474 | 0.84266 | 0.91428 | -10.7527 | -118.7109 | 116.2801 | -10.7527 | -118.7109 | 116.2801

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.749e-11 | 1.3228e-10 | -2.5112e-10 | -4.8859e-11 | -1.0826e-10 | 2.0847e-10 | 2.6404e-10 | -2.1335e-10 | -7.7368e-12 | -2.2567e-10 | 1.7801e-10 | 4.6293e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.749e-11 | 1.3228e-10 | -2.5112e-10 | -4.8859e-11 | -1.0826e-10 | 2.0847e-10 | 2.6404e-10 | -2.1335e-10 | -7.7369e-12 | -2.2567e-10 | 1.7801e-10 | 4.6294e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6241e-11 | 1.1023e-10 | -2.0927e-10 | -3.761e-11 | -8.6217e-11 | 1.6662e-10 | 2.2004e-10 | -1.7779e-10 | -6.4474e-12 | -1.8166e-10 | 1.4245e-10 | 3.3399e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3745e-11 | 6.614e-11 | -1.2556e-10 | -1.5114e-11 | -4.2123e-11 | 8.2911e-11 | 1.3202e-10 | -1.0667e-10 | -3.8685e-12 | -9.365e-11 | 7.1337e-11 | 7.6092e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1248e-11 | 2.2047e-11 | -4.1853e-11 | 7.3828e-12 | 1.9701e-12 | -7.9488e-13 | 4.4007e-11 | -3.5558e-11 | -1.2895e-12 | -5.6359e-12 | 2.2167e-13 | -1.818e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2497e-11 | 4.4094e-11 | -8.3706e-11 | -3.8655e-12 | -2.0077e-11 | 4.1058e-11 | 8.8014e-11 | -7.1116e-11 | -2.579e-12 | -4.9643e-11 | 3.5779e-11 | -5.2856e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1248e-11 | 2.2047e-11 | -4.1853e-11 | 7.3828e-12 | 1.9701e-12 | -7.9488e-13 | 4.4007e-11 | -3.5558e-11 | -1.2895e-12 | -5.6359e-12 | 2.2167e-13 | -1.818e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line16_4_18 | 0.030757 | 0 | 0 | 0.030757 | 0 | 0 | 0.0071029 | 0 | 0 | 0.0071029 | 0 | 0 | 0.0047449 | 8.2746e-11 | -1.0824e-10 | -0.0047298 | 4.1736e-12 | 1.2707e-12 | 0.0047456 | -7.7037e-11 | -3.2982e-11 | -0.0047298 | 3.8941e-12 | -5.57e-12 | -45.1054 | 0 | 0 | 134.8946 | 0 | 0 | 0.9448 | 0.94912 | 0.94993 | 0.94172 | 0.9488 | 0.94963 | -0.10158 | -119.9643 | 119.936 | -0.10539 | -119.9325 | 119.9035
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1248e-11 | 2.2047e-11 | -4.1853e-11 | 7.3828e-12 | 1.9701e-12 | -7.9488e-13 | 4.4007e-11 | -3.5558e-11 | -1.2895e-12 | -5.6359e-12 | 2.2167e-13 | -1.818e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9986e-11 | 1.7637e-10 | -3.3482e-10 | -7.1355e-11 | -1.5236e-10 | 2.9218e-10 | 3.5206e-10 | -2.8446e-10 | -1.0316e-11 | -3.1369e-10 | 2.4913e-10 | 7.2083e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line2_1_4 | 0.030757 | 0 | 0 | 0.030757 | 0 | 0 | 0.0071029 | 0 | 0 | 0.0071029 | 0 | 0 | 0.0047601 | 1.2464e-10 | -1.7259e-10 | -0.0047449 | -7.9673e-11 | 1.0848e-10 | 0.0047613 | -1.2713e-10 | -4.4306e-11 | -0.0047456 | 7.9095e-11 | 2.9288e-11 | -45.1054 | 0 | 0 | 134.8946 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.9448 | 0.94912 | 0.94993 | -0.097801 | -119.9962 | 119.9685 | -0.10158 | -119.9643 | 119.936
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2497e-11 | 4.4093e-11 | -8.3706e-11 | -3.8655e-12 | -2.0077e-11 | 4.1058e-11 | 8.8014e-11 | -7.1116e-11 | -2.5789e-12 | -4.9643e-11 | 3.5779e-11 | -5.2858e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6241e-11 | 1.1023e-10 | -2.0927e-10 | -3.761e-11 | -8.6217e-11 | 1.6662e-10 | 2.2004e-10 | -1.7779e-10 | -6.4474e-12 | -1.8166e-10 | 1.4245e-10 | 3.3399e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4993e-11 | 8.8187e-11 | -1.6741e-10 | -2.6362e-11 | -6.417e-11 | 1.2476e-10 | 1.7603e-10 | -1.4223e-10 | -5.1579e-12 | -1.3766e-10 | 1.0689e-10 | 2.0504e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3745e-11 | 6.614e-11 | -1.2556e-10 | -1.5114e-11 | -4.2123e-11 | 8.2911e-11 | 1.3202e-10 | -1.0667e-10 | -3.8684e-12 | -9.365e-11 | 7.1337e-11 | 7.609e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1248e-11 | 2.2047e-11 | -4.1853e-11 | 7.3828e-12 | 1.9701e-12 | -7.9488e-13 | 4.4007e-11 | -3.5558e-11 | -1.2895e-12 | -5.6359e-12 | 2.2167e-13 | -1.818e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1248e-11 | 2.2047e-11 | -4.1853e-11 | 7.3828e-12 | 1.9701e-12 | -7.9488e-13 | 4.4007e-11 | -3.5558e-11 | -1.2895e-12 | -5.6359e-12 | 2.2167e-13 | -1.818e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8738e-11 | 1.5433e-10 | -2.9297e-10 | -6.0107e-11 | -1.3031e-10 | 2.5032e-10 | 3.0805e-10 | -2.489e-10 | -9.0264e-12 | -2.6968e-10 | 2.1357e-10 | 5.9188e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94787 | 0.94943 | 0.95023 | 0.94787 | 0.94943 | 0.95023 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0572e-11 | 1.1872e-10 | -2.2538e-10 | -4.3851e-11 | -9.7167e-11 | 1.871e-10 | 2.3698e-10 | -1.9148e-10 | -6.9439e-12 | -2.0254e-10 | 1.5977e-10 | 4.1548e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0572e-11 | 1.1872e-10 | -2.2538e-10 | -4.3851e-11 | -9.7167e-11 | 1.871e-10 | 2.3698e-10 | -1.9148e-10 | -6.9439e-12 | -2.0254e-10 | 1.5977e-10 | 4.1549e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0477e-11 | 9.8936e-11 | -1.8782e-10 | -3.3756e-11 | -7.738e-11 | 1.4954e-10 | 1.9748e-10 | -1.5957e-10 | -5.7866e-12 | -1.6304e-10 | 1.2785e-10 | 2.9976e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0286e-11 | 5.9361e-11 | -1.1269e-10 | -1.3565e-11 | -3.7806e-11 | 7.4413e-11 | 1.1849e-10 | -9.574e-11 | -3.472e-12 | -8.4052e-11 | 6.4026e-11 | 6.8293e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0095e-11 | 1.9787e-11 | -3.7563e-11 | 6.6261e-12 | 1.7682e-12 | -7.1341e-13 | 3.9497e-11 | -3.1913e-11 | -1.1573e-12 | -5.0583e-12 | 1.9895e-13 | -1.6317e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0191e-11 | 3.9574e-11 | -7.5127e-11 | -3.4693e-12 | -1.8019e-11 | 3.685e-11 | 7.8993e-11 | -6.3827e-11 | -2.3146e-12 | -4.4555e-11 | 3.2112e-11 | -4.7439e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0095e-11 | 1.9787e-11 | -3.7563e-11 | 6.6261e-12 | 1.7682e-12 | -7.1341e-13 | 3.9497e-11 | -3.1913e-11 | -1.1573e-12 | -5.0583e-12 | 1.9895e-13 | -1.6317e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line16_4_18 | 0.029138 | 0 | 0 | 0.029138 | 0 | 0 | 0.0067291 | 0 | 0 | 0.0067291 | 0 | 0 | 0.0042586 | 7.4265e-11 | -9.7145e-11 | -0.004245 | 3.7458e-12 | 1.1405e-12 | 0.0042592 | -6.9141e-11 | -2.9602e-11 | -0.004245 | 3.4949e-12 | -4.9991e-12 | -45.1054 | 0 | 0 | 134.8946 | 0 | 0 | 0.89507 | 0.89916 | 0.89993 | 0.89216 | 0.89886 | 0.89965 | -0.10158 | -119.9643 | 119.936 | -0.10539 | -119.9325 | 119.9035
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0095e-11 | 1.9787e-11 | -3.7563e-11 | 6.6261e-12 | 1.7682e-12 | -7.1341e-13 | 3.9497e-11 | -3.1913e-11 | -1.1573e-12 | -5.0583e-12 | 1.9895e-13 | -1.6317e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0763e-11 | 1.583e-10 | -3.0051e-10 | -6.4042e-11 | -1.3674e-10 | 2.6223e-10 | 3.1597e-10 | -2.5531e-10 | -9.2585e-12 | -2.8153e-10 | 2.2359e-10 | 6.4695e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line2_1_4 | 0.029138 | 0 | 0 | 0.029138 | 0 | 0 | 0.0067291 | 0 | 0 | 0.0067291 | 0 | 0 | 0.0042722 | 1.1186e-10 | -1.549e-10 | -0.0042586 | -7.1507e-11 | 9.736e-11 | 0.0042733 | -1.141e-10 | -3.9765e-11 | -0.0042592 | 7.0988e-11 | 2.6286e-11 | -45.1054 | 0 | 0 | 134.8946 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89507 | 0.89916 | 0.89993 | -0.097801 | -119.9962 | 119.9685 | -0.10158 | -119.9643 | 119.936
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0191e-11 | 3.9574e-11 | -7.5127e-11 | -3.4693e-12 | -1.8019e-11 | 3.685e-11 | 7.8993e-11 | -6.3827e-11 | -2.3146e-12 | -4.4555e-11 | 3.2112e-11 | -4.7441e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0477e-11 | 9.8936e-11 | -1.8782e-10 | -3.3756e-11 | -7.738e-11 | 1.4954e-10 | 1.9748e-10 | -1.5957e-10 | -5.7866e-12 | -1.6304e-10 | 1.2785e-10 | 2.9975e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0382e-11 | 7.9148e-11 | -1.5025e-10 | -2.366e-11 | -5.7593e-11 | 1.1198e-10 | 1.5799e-10 | -1.2765e-10 | -4.6293e-12 | -1.2355e-10 | 9.5939e-11 | 1.8402e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0286e-11 | 5.9361e-11 | -1.1269e-10 | -1.3565e-11 | -3.7806e-11 | 7.4413e-11 | 1.1849e-10 | -9.574e-11 | -3.4719e-12 | -8.4052e-11 | 6.4026e-11 | 6.8292e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0095e-11 | 1.9787e-11 | -3.7563e-11 | 6.6261e-12 | 1.7682e-12 | -7.1341e-13 | 3.9497e-11 | -3.1913e-11 | -1.1573e-12 | -5.0583e-12 | 1.9895e-13 | -1.6317e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0095e-11 | 1.9787e-11 | -3.7563e-11 | 6.6261e-12 | 1.7682e-12 | -7.1341e-13 | 3.9497e-11 | -3.1913e-11 | -1.1573e-12 | -5.0583e-12 | 1.9895e-13 | -1.6317e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0668e-11 | 1.3851e-10 | -2.6294e-10 | -5.3946e-11 | -1.1695e-10 | 2.2467e-10 | 2.7648e-10 | -2.2339e-10 | -8.1012e-12 | -2.4204e-10 | 1.9168e-10 | 5.3122e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89799 | 0.89946 | 0.90022 | 0.89799 | 0.89946 | 0.90022 | -0.097801 | -119.9962 | 119.9685 | -0.097801 | -119.9962 | 119.9685

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0054037 | -0.0059373 | -0.0058849 | 0.0057037 | 0.0062372 | 0.0061849 | -0.040876 | -0.029623 | -0.02849 | 0.041476 | 0.030223 | 0.02909 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0308 | 0.75531 | 0.72728 | 1.0466 | 0.7715 | 0.7435 | -2.7436 | -126.5461 | 113.1163 | -3.043 | -126.8733 | 112.7841
Line10_11_12 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0060037 | -0.0065373 | -0.0064849 | 0.0063037 | 0.0068372 | 0.0067849 | -0.042076 | -0.030823 | -0.02969 | 0.042676 | 0.031423 | 0.03029 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0625 | 0.78772 | 0.75974 | 1.0785 | 0.80396 | 0.77601 | -3.3334 | -127.187 | 112.4661 | -3.6153 | -127.4881 | 112.1614
Line11_12_13 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0063037 | -0.0068372 | -0.0067849 | 0.0066037 | 0.0071372 | 0.0070849 | -0.042676 | -0.031423 | -0.03029 | 0.043276 | 0.032023 | 0.03089 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0785 | 0.80396 | 0.77601 | 1.0944 | 0.82022 | 0.7923 | -3.6153 | -127.4881 | 112.1614 | -3.889 | -127.7773 | 111.8693
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4327e-09 | -1.7434e-08 | 1.629e-08 | 1.4339e-09 | 1.2284e-08 | -1.0142e-08 | -2.5985e-08 | 1.4363e-08 | 7.7853e-09 | 1.7037e-08 | -1.0003e-08 | -5.6216e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0944 | 0.82022 | 0.7923 | 1.0944 | 0.82022 | 0.7923 | -3.889 | -127.7773 | 111.8693 | -3.889 | -127.7773 | 111.8693
Line13_13_14 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0066037 | -0.0071372 | -0.0070849 | 0.0069037 | 0.0074372 | 0.0073849 | -0.043276 | -0.032023 | -0.03089 | 0.043876 | 0.032623 | 0.03149 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0944 | 0.82022 | 0.7923 | 1.1104 | 0.83651 | 0.8086 | -3.889 | -127.7773 | 111.8693 | -4.1548 | -128.0552 | 111.5889
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6218e-09 | -1.1622e-08 | 1.086e-08 | 6.2297e-10 | 6.4732e-09 | -4.7121e-09 | -1.7323e-08 | 9.5754e-09 | 5.1902e-09 | 8.3758e-09 | -5.215e-09 | -3.0265e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0944 | 0.82022 | 0.7923 | 1.0944 | 0.82022 | 0.7923 | -3.889 | -127.7773 | 111.8693 | -3.889 | -127.7773 | 111.8693
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1089e-10 | -5.8112e-09 | 5.4301e-09 | -1.8792e-10 | 6.62e-10 | 7.1799e-10 | -8.6616e-09 | 4.7877e-09 | 2.5951e-09 | -2.8577e-10 | -4.2733e-10 | -4.3142e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0944 | 0.82022 | 0.7923 | 1.0944 | 0.82022 | 0.7923 | -3.889 | -127.7773 | 111.8693 | -3.889 | -127.7773 | 111.8693
Line16_4_18 | 0 | 4.5741 | 4.3844 | 0 | 4.5741 | 4.3844 | 0 | 1.0563 | 1.0125 | 0 | 1.0563 | 1.0125 | -9.1537e-10 | 0.11323 | 0.23128 | 5.9893e-10 | 6.3144e-14 | 3.7982e-14 | -1.8939e-08 | 0.39172 | 0.2973 | -1.3953e-10 | 5.2438e-14 | 3.3233e-14 | 0 | 159.4778 | 60.9011 | 0 | -20.5222 | -119.0989 | 0.95312 | 0.38601 | 0.372 | 0.85888 | 0 | 0 | -2.6704 | -126.6452 | 113.021 | -2.4183 | 0 | 0
Line17_5_19 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0057037 | -0.0062372 | -0.0061849 | 0.0060037 | 0.0065372 | 0.0064849 | -0.041476 | -0.030223 | -0.02909 | 0.042076 | 0.030823 | 0.02969 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0466 | 0.7715 | 0.7435 | 1.0625 | 0.78772 | 0.75974 | -3.043 | -126.8733 | 112.7841 | -3.3334 | -127.187 | 112.4661
Line1_1_3 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0054037 | -0.0059373 | -0.0058849 | 0.0057037 | 0.0062373 | 0.0061849 | -0.040876 | -0.029623 | -0.02849 | 0.041476 | 0.030223 | 0.02909 | 94.7872 | -25.2126 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0308 | 0.75531 | 0.72728 | 1.0466 | 0.7715 | 0.7435 | -2.7436 | -126.5461 | 113.1163 | -3.043 | -126.8733 | 112.7841
Line2_1_4 | 0.1732 | 4.4018 | 4.2177 | 0.1732 | 4.4018 | 4.2177 | 0.04 | 1.0166 | 0.97404 | 0.04 | 1.0166 | 0.97404 | -0.012875 | 0.20892 | 0.44013 | 0.011859 | -0.10743 | -0.2256 | -0.039169 | 0.73885 | 0.55508 | 0.036233 | -0.37742 | -0.28355 | 105.4525 | 159.2431 | 61.5279 | -74.5475 | -20.7569 | -118.4721 | 1.0308 | 0.75531 | 0.72728 | 0.95312 | 0.38601 | 0.372 | -2.7436 | -126.5461 | 113.1163 | -2.6704 | -126.6452 | 113.021
Line3_1_5 | 0.17321 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0054037 | -0.0059372 | -0.0058849 | 0.0057037 | 0.0062372 | 0.0061849 | -0.040876 | -0.029623 | -0.02849 | 0.041476 | 0.030223 | 0.02909 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0308 | 0.75531 | 0.72728 | 1.0466 | 0.7715 | 0.7435 | -2.7436 | -126.5461 | 113.1163 | -3.043 | -126.8733 | 112.7841
Line4_2_6 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0057037 | -0.0062372 | -0.0061849 | 0.0060037 | 0.0065372 | 0.0064849 | -0.041476 | -0.030223 | -0.02909 | 0.042076 | 0.030823 | 0.02969 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0466 | 0.7715 | 0.7435 | 1.0625 | 0.78772 | 0.75974 | -3.043 | -126.8733 | 112.7841 | -3.3334 | -127.187 | 112.4661
Line5_6_7 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0060037 | -0.0065372 | -0.0064849 | 0.0063037 | 0.0068372 | 0.0067849 | -0.042076 | -0.030823 | -0.02969 | 0.042676 | 0.031423 | 0.03029 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0625 | 0.78772 | 0.75974 | 1.0785 | 0.80396 | 0.77601 | -3.3334 | -127.187 | 112.4661 | -3.6153 | -127.4881 | 112.1614
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4639e-09 | -1.7303e-08 | 1.5777e-08 | 1.5218e-09 | 1.2234e-08 | -9.7665e-09 | -2.5679e-08 | 1.3955e-08 | 7.6721e-09 | 1.6858e-08 | -9.7069e-09 | -5.5222e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0785 | 0.80396 | 0.77601 | 1.0785 | 0.80396 | 0.77601 | -3.6153 | -127.4881 | 112.1614 | -3.6153 | -127.4881 | 112.1614
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2131e-10 | -5.7675e-09 | 5.2591e-09 | -1.2083e-10 | 6.9889e-10 | 7.5169e-10 | -8.5598e-09 | 4.6518e-09 | 2.5574e-09 | -2.6182e-10 | -4.0337e-10 | -4.0746e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0785 | 0.80396 | 0.77601 | 1.0785 | 0.80396 | 0.77601 | -3.6153 | -127.4881 | 112.1614 | -3.6153 | -127.4881 | 112.1614
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2131e-10 | -5.7675e-09 | 5.2591e-09 | -1.2083e-10 | 6.9889e-10 | 7.5169e-10 | -8.5598e-09 | 4.6518e-09 | 2.5574e-09 | -2.6182e-10 | -4.0337e-10 | -4.0746e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0785 | 0.80396 | 0.77601 | 1.0785 | 0.80396 | 0.77601 | -3.6153 | -127.4881 | 112.1614 | -3.6153 | -127.4881 | 112.1614
Line9_3_11 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0057037 | -0.0062373 | -0.0061849 | 0.0060037 | 0.0065373 | 0.0064849 | -0.041476 | -0.030223 | -0.02909 | 0.042076 | 0.030823 | 0.02969 | 94.7872 | -25.2127 | -145.2128 | -85.2128 | 154.7873 | 34.7872 | 1.0466 | 0.7715 | 0.7435 | 1.0625 | 0.78772 | 0.75974 | -3.043 | -126.8733 | 112.7841 | -3.3334 | -127.187 | 112.4661

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00571 | -0.0062399 | -0.006173 | 0.00601 | 0.0065399 | 0.006473 | -0.042694 | -0.030541 | -0.029338 | 0.043294 | 0.031141 | 0.029938 | 94.7869 | -25.213 | -145.2131 | -85.2131 | 154.787 | 34.7869 | 1.0769 | 0.7793 | 0.74951 | 1.0927 | 0.79551 | 0.76574 | -2.8308 | -126.7602 | 112.9046 | -3.1163 | -127.0732 | 112.5865
Line10_11_12 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00631 | -0.0068399 | -0.006773 | 0.00661 | 0.0071399 | 0.007073 | -0.043894 | -0.031741 | -0.030538 | 0.044494 | 0.032341 | 0.031138 | 94.7869 | -25.213 | -145.2131 | -85.2131 | 154.787 | 34.7869 | 1.1086 | 0.81174 | 0.782 | 1.1246 | 0.828 | 0.79828 | -3.3936 | -127.3737 | 112.2817 | -3.6631 | -127.6623 | 111.9893
Line11_12_13 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00661 | -0.0071399 | -0.007073 | 0.00691 | 0.0074399 | 0.007373 | -0.044494 | -0.032341 | -0.031138 | 0.045094 | 0.032941 | 0.031738 | 94.7869 | -25.213 | -145.2131 | -85.2131 | 154.787 | 34.7869 | 1.1246 | 0.828 | 0.79828 | 1.1405 | 0.84427 | 0.81458 | -3.6631 | -127.6623 | 111.9893 | -3.9251 | -127.9399 | 111.7085
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7647e-09 | -1.9424e-08 | 1.7998e-08 | 1.6629e-09 | 1.3709e-08 | -1.1181e-08 | -2.9232e-08 | 1.5936e-08 | 8.617e-09 | 1.9173e-08 | -1.1094e-08 | -6.2185e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1405 | 0.84427 | 0.81458 | 1.1405 | 0.84427 | 0.81458 | -3.9251 | -127.9399 | 111.7085 | -3.9251 | -127.9399 | 111.7085
Line13_13_14 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00691 | -0.0074398 | -0.007373 | 0.00721 | 0.0077398 | 0.007673 | -0.045094 | -0.032941 | -0.031738 | 0.045694 | 0.033541 | 0.032338 | 94.7869 | -25.213 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1405 | 0.84427 | 0.81458 | 1.1565 | 0.86057 | 0.83089 | -3.9251 | -127.9399 | 111.7085 | -4.1798 | -128.207 | 111.4388
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.8431e-09 | -1.295e-08 | 1.1999e-08 | 7.4132e-10 | 7.2338e-09 | -5.1813e-09 | -1.9488e-08 | 1.0624e-08 | 5.7447e-09 | 9.4292e-09 | -5.7822e-09 | -3.3461e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1405 | 0.84427 | 0.81458 | 1.1405 | 0.84427 | 0.81458 | -3.9251 | -127.9399 | 111.7085 | -3.9251 | -127.9399 | 111.7085
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.2155e-10 | -6.4748e-09 | 5.9994e-09 | -1.8024e-10 | 7.59e-10 | 8.1816e-10 | -9.744e-09 | 5.3119e-09 | 2.8723e-09 | -3.1488e-10 | -4.7038e-10 | -4.7379e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1405 | 0.84427 | 0.81458 | 1.1405 | 0.84427 | 0.81458 | -3.9251 | -127.9399 | 111.7085 | -3.9251 | -127.9399 | 111.7085
Line16_4_18 | 0 | 4.7167 | 4.515 | 0 | 4.7167 | 4.515 | 0 | 1.0893 | 1.0427 | 0 | 1.0893 | 1.0427 | -1.0083e-09 | 0.12049 | 0.24536 | 6.5859e-10 | 1.8124e-13 | 9.4277e-14 | -2.0787e-08 | 0.41646 | 0.31524 | -1.5787e-10 | -7.6123e-14 | -1.2285e-13 | 0 | 159.2789 | 60.7058 | 0 | -20.7211 | -119.2942 | 0.99632 | 0.39801 | 0.38312 | 0.89921 | 0 | 0 | -2.7507 | -126.8571 | 112.8112 | -2.4948 | 0 | 0
Line17_5_19 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00601 | -0.0065398 | -0.006473 | 0.00631 | 0.0068398 | 0.006773 | -0.043294 | -0.031141 | -0.029938 | 0.043894 | 0.031741 | 0.030538 | 94.7869 | -25.213 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.0927 | 0.79551 | 0.76574 | 1.1086 | 0.81174 | 0.782 | -3.1163 | -127.0732 | 112.5865 | -3.3936 | -127.3737 | 112.2817
Line1_1_3 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00571 | -0.0062399 | -0.006173 | 0.00601 | 0.0065399 | 0.006473 | -0.042694 | -0.030541 | -0.029338 | 0.043294 | 0.031141 | 0.029938 | 94.7869 | -25.213 | -145.2132 | -85.2131 | 154.787 | 34.7868 | 1.0769 | 0.7793 | 0.74951 | 1.0927 | 0.79551 | 0.76574 | -2.8308 | -126.7602 | 112.9046 | -3.1163 | -127.0732 | 112.5865
Line2_1_4 | 0.1732 | 4.5444 | 4.3484 | 0.1732 | 4.5444 | 4.3484 | 0.04 | 1.0495 | 1.0042 | 0.04 | 1.0495 | 1.0042 | -0.013331 | 0.22288 | 0.46763 | 0.012281 | -0.11451 | -0.23953 | -0.04096 | 0.78691 | 0.58976 | 0.037913 | -0.4017 | -0.30107 | 105.1981 | 159.0537 | 61.316 | -74.8019 | -20.9463 | -118.684 | 1.0769 | 0.7793 | 0.74951 | 0.99632 | 0.39801 | 0.38312 | -2.8308 | -126.7602 | 112.9046 | -2.7507 | -126.8571 | 112.8112
Line3_1_5 | 0.17321 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00571 | -0.0062399 | -0.006173 | 0.00601 | 0.0065398 | 0.006473 | -0.042694 | -0.030541 | -0.029338 | 0.043294 | 0.031141 | 0.029938 | 94.7869 | -25.213 | -145.2131 | -85.2131 | 154.787 | 34.7869 | 1.0769 | 0.7793 | 0.74951 | 1.0927 | 0.79551 | 0.76574 | -2.8308 | -126.7602 | 112.9046 | -3.1163 | -127.0732 | 112.5865
Line4_2_6 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00601 | -0.0065399 | -0.006473 | 0.00631 | 0.0068399 | 0.006773 | -0.043294 | -0.031141 | -0.029938 | 0.043894 | 0.031741 | 0.030538 | 94.7869 | -25.213 | -145.2131 | -85.2131 | 154.787 | 34.7869 | 1.0927 | 0.79551 | 0.76574 | 1.1086 | 0.81174 | 0.782 | -3.1163 | -127.0732 | 112.5865 | -3.3936 | -127.3737 | 112.2817
Line5_6_7 | 0.17321 | 0.1732 | 0.17321 | 0.17321 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00631 | -0.0068399 | -0.006773 | 0.00661 | 0.0071399 | 0.007073 | -0.043894 | -0.031741 | -0.030538 | 0.044494 | 0.032341 | 0.031138 | 94.7869 | -25.213 | -145.2131 | -85.2131 | 154.787 | 34.7869 | 1.1086 | 0.81174 | 0.782 | 1.1246 | 0.828 | 0.79828 | -3.3936 | -127.3737 | 112.2817 | -3.6631 | -127.6623 | 111.9893
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7914e-09 | -1.9274e-08 | 1.7454e-08 | 1.7503e-09 | 1.3645e-08 | -1.0784e-08 | -2.89e-08 | 1.5499e-08 | 8.4959e-09 | 1.8977e-08 | -1.0778e-08 | -6.1126e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1246 | 0.828 | 0.79828 | 1.1246 | 0.828 | 0.79828 | -3.6631 | -127.6623 | 111.9893 | -3.6631 | -127.6623 | 111.9893
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.3045e-10 | -6.4245e-09 | 5.8179e-09 | -1.1057e-10 | 7.9598e-10 | 8.5173e-10 | -9.6333e-09 | 5.1662e-09 | 2.832e-09 | -2.8979e-10 | -4.4528e-10 | -4.487e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1246 | 0.828 | 0.79828 | 1.1246 | 0.828 | 0.79828 | -3.6631 | -127.6623 | 111.9893 | -3.6631 | -127.6623 | 111.9893
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.3045e-10 | -6.4245e-09 | 5.8179e-09 | -1.1057e-10 | 7.9598e-10 | 8.5173e-10 | -9.6333e-09 | 5.1662e-09 | 2.832e-09 | -2.8979e-10 | -4.4528e-10 | -4.487e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1246 | 0.828 | 0.79828 | 1.1246 | 0.828 | 0.79828 | -3.6631 | -127.6623 | 111.9893 | -3.6631 | -127.6623 | 111.9893
Line9_3_11 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.00601 | -0.0065399 | -0.006473 | 0.00631 | 0.0068399 | 0.006773 | -0.043294 | -0.031141 | -0.029938 | 0.043894 | 0.031741 | 0.030538 | 94.7869 | -25.213 | -145.2132 | -85.2131 | 154.787 | 34.7869 | 1.0927 | 0.79551 | 0.76574 | 1.1086 | 0.81174 | 0.782 | -3.1163 | -127.0732 | 112.5865 | -3.3936 | -127.3737 | 112.2817

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036283 | -0.0036992 | -0.0036693 | 0.0039283 | 0.0039992 | 0.0039693 | -0.04462 | -0.044541 | -0.044507 | 0.04522 | 0.045141 | 0.045107 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1192 | 1.1174 | 1.1165 | 1.1347 | 1.133 | 1.132 | 0.1384 | -119.9603 | 120.0743 | -0.17767 | -120.2755 | 119.7583
Line10_11_12 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0042283 | -0.0042992 | -0.0042693 | 0.0045283 | 0.0045992 | 0.0045693 | -0.04582 | -0.045741 | -0.045707 | 0.04642 | 0.046341 | 0.046307 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1504 | 1.1486 | 1.1477 | 1.166 | 1.1642 | 1.1633 | -0.48516 | -120.5822 | 119.451 | -0.78441 | -120.8806 | 119.1519
Line11_12_13 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0045283 | -0.0045992 | -0.0045693 | 0.0048283 | 0.0048992 | 0.0048693 | -0.04642 | -0.046341 | -0.046307 | 0.04702 | 0.046941 | 0.046907 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.166 | 1.1642 | 1.1633 | 1.1817 | 1.1799 | 1.179 | -0.78441 | -120.8806 | 119.1519 | -1.0757 | -121.171 | 118.8608
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6309e-09 | 1.5885e-09 | 1.8588e-09 | -1.6586e-09 | -1.622e-09 | -1.7977e-09 | 9.1981e-11 | 4.3248e-10 | 2.8074e-10 | -1.4673e-10 | -3.8116e-10 | -2.7741e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1817 | 1.1799 | 1.179 | 1.1817 | 1.1799 | 1.179 | -1.0757 | -121.171 | 118.8608 | -1.0757 | -121.171 | 118.8608
Line13_13_14 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0048283 | -0.0048992 | -0.0048693 | 0.0051283 | 0.0051992 | 0.0051693 | -0.04702 | -0.046941 | -0.046907 | 0.04762 | 0.047541 | 0.047507 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1817 | 1.1799 | 1.179 | 1.1974 | 1.1956 | 1.1947 | -1.0757 | -121.171 | 118.8608 | -1.3594 | -121.4539 | 118.5773
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0873e-09 | 1.059e-09 | 1.2392e-09 | -1.1149e-09 | -1.0925e-09 | -1.1781e-09 | 6.1321e-11 | 2.8832e-10 | 1.8716e-10 | -1.1607e-10 | -2.37e-10 | -1.8383e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1817 | 1.1799 | 1.179 | 1.1817 | 1.1799 | 1.179 | -1.0757 | -121.171 | 118.8608 | -1.0757 | -121.171 | 118.8608
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4363e-10 | 5.2951e-10 | 6.1961e-10 | -5.713e-10 | -5.6296e-10 | -5.5849e-10 | 3.066e-11 | 1.4416e-10 | 9.3581e-11 | -8.5411e-11 | -9.2839e-11 | -9.0247e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1817 | 1.1799 | 1.179 | 1.1817 | 1.1799 | 1.179 | -1.0757 | -121.171 | 118.8608 | -1.0757 | -121.171 | 118.8608
Line16_4_18 | 0 | 0.036838 | 0.036788 | 0 | 0.036838 | 0.036788 | 0 | 0.0085075 | 0.0084958 | 0 | 0.0085075 | 0.0084958 | 2.9934e-10 | 0.0067939 | 0.0067831 | -3.5148e-10 | -0.0067854 | -0.0067667 | -1.3013e-10 | 0.0068122 | 0.0067896 | -3.4751e-12 | -0.0067854 | -0.0067667 | 0 | -165.278 | 74.8548 | 0 | 14.722 | -105.1452 | 1.1351 | 1.1309 | 1.1297 | 1.1345 | 1.1279 | 1.1264 | -0.036133 | -120.2009 | 119.8823 | -0.045586 | -120.278 | 119.8548
Line17_5_19 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039283 | -0.0039992 | -0.0039693 | 0.0042283 | 0.0042992 | 0.0042693 | -0.04522 | -0.045141 | -0.045107 | 0.04582 | 0.045741 | 0.045707 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1347 | 1.133 | 1.132 | 1.1504 | 1.1486 | 1.1477 | -0.17767 | -120.2755 | 119.7583 | -0.48516 | -120.5822 | 119.451
Line1_1_3 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036283 | -0.0036992 | -0.0036693 | 0.0039283 | 0.0039992 | 0.0039693 | -0.04462 | -0.044541 | -0.044507 | 0.04522 | 0.045141 | 0.045107 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1192 | 1.1174 | 1.1165 | 1.1347 | 1.133 | 1.132 | 0.1384 | -119.9603 | 120.0743 | -0.17767 | -120.2755 | 119.7583
Line2_1_4 | 0.1732 | 0.14221 | 0.14231 | 0.1732 | 0.14221 | 0.14231 | 0.04 | 0.032843 | 0.032864 | 0.04 | 0.032843 | 0.032864 | -0.011823 | -0.0051942 | -0.0051616 | 0.012125 | 0.0054114 | 0.0053457 | -0.043177 | -0.036328 | -0.036327 | 0.043753 | 0.036745 | 0.036738 | 105.4525 | -21.8233 | -141.8388 | -74.5475 | 158.1767 | 38.1612 | 1.1192 | 1.1174 | 1.1165 | 1.1351 | 1.1309 | 1.1297 | 0.1384 | -119.9603 | 120.0743 | -0.036133 | -120.2009 | 119.8823
Line3_1_5 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0036283 | -0.0036992 | -0.0036693 | 0.0039283 | 0.0039992 | 0.0039693 | -0.04462 | -0.044541 | -0.044507 | 0.04522 | 0.045141 | 0.045107 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1192 | 1.1174 | 1.1165 | 1.1347 | 1.133 | 1.132 | 0.1384 | -119.9603 | 120.0743 | -0.17767 | -120.2755 | 119.7583
Line4_2_6 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039283 | -0.0039992 | -0.0039693 | 0.0042283 | 0.0042992 | 0.0042693 | -0.04522 | -0.045141 | -0.045107 | 0.04582 | 0.045741 | 0.045707 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1347 | 1.133 | 1.132 | 1.1504 | 1.1486 | 1.1477 | -0.17767 | -120.2755 | 119.7583 | -0.48516 | -120.5822 | 119.451
Line5_6_7 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0042283 | -0.0042992 | -0.0042693 | 0.0045283 | 0.0045992 | 0.0045693 | -0.04582 | -0.045741 | -0.045707 | 0.04642 | 0.046341 | 0.046307 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1504 | 1.1486 | 1.1477 | 1.166 | 1.1642 | 1.1633 | -0.48516 | -120.5822 | 119.451 | -0.78441 | -120.8806 | 119.1519
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.408e-09 | 1.3646e-09 | 1.6322e-09 | -1.435e-09 | -1.3979e-09 | -1.5719e-09 | 2.1881e-11 | 3.5806e-10 | 2.0966e-10 | -7.6044e-11 | -3.0759e-10 | -2.0607e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.166 | 1.1642 | 1.1633 | 1.166 | 1.1642 | 1.1633 | -0.78441 | -120.8806 | 119.1519 | -0.78441 | -120.8806 | 119.1519
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6932e-10 | 4.5487e-10 | 5.4408e-10 | -4.9635e-10 | -4.8812e-10 | -4.8379e-10 | 7.2936e-12 | 1.1935e-10 | 6.9888e-11 | -6.1456e-11 | -6.8884e-11 | -6.6292e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.166 | 1.1642 | 1.1633 | 1.166 | 1.1642 | 1.1633 | -0.78441 | -120.8806 | 119.1519 | -0.78441 | -120.8806 | 119.1519
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6932e-10 | 4.5487e-10 | 5.4408e-10 | -4.9635e-10 | -4.8812e-10 | -4.8379e-10 | 7.2935e-12 | 1.1935e-10 | 6.9888e-11 | -6.1456e-11 | -6.8884e-11 | -6.6292e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.166 | 1.1642 | 1.1633 | 1.166 | 1.1642 | 1.1633 | -0.78441 | -120.8806 | 119.1519 | -0.78441 | -120.8806 | 119.1519
Line9_3_11 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.0039283 | -0.0039992 | -0.0039693 | 0.0042283 | 0.0042992 | 0.0042693 | -0.04522 | -0.045141 | -0.045107 | 0.04582 | 0.045741 | 0.045707 | 94.7872 | -25.2128 | -145.2128 | -85.2128 | 154.7872 | 34.7872 | 1.1347 | 1.133 | 1.132 | 1.1504 | 1.1486 | 1.1477 | -0.17767 | -120.2755 | 119.7583 | -0.48516 | -120.5822 | 119.451

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.003805 | -0.0038827 | -0.0038499 | 0.004105 | 0.0041827 | 0.0041499 | -0.046743 | -0.046657 | -0.04662 | 0.047343 | 0.047257 | 0.04722 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1724 | 1.1705 | 1.1695 | 1.188 | 1.186 | 1.185 | 0.13318 | -119.9701 | 120.0661 | -0.16865 | -120.2711 | 119.7644
Line10_11_12 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.004405 | -0.0044827 | -0.0044499 | 0.004705 | 0.0047827 | 0.0047499 | -0.047943 | -0.047857 | -0.04782 | 0.048543 | 0.048457 | 0.04842 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.2036 | 1.2017 | 1.2007 | 1.2193 | 1.2173 | 1.2163 | -0.46266 | -120.5642 | 119.4705 | -0.74913 | -120.8499 | 119.1842
Line11_12_13 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.004705 | -0.0047827 | -0.0047499 | 0.005005 | 0.0050827 | 0.0050499 | -0.048543 | -0.048457 | -0.04842 | 0.049143 | 0.049057 | 0.04902 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.2193 | 1.2173 | 1.2163 | 1.2349 | 1.233 | 1.232 | -0.74913 | -120.8499 | 119.1842 | -1.0283 | -121.1282 | 118.9052
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7404e-09 | 1.6916e-09 | 2.0012e-09 | -1.772e-09 | -1.7299e-09 | -1.9312e-09 | 8.0029e-11 | 4.6993e-10 | 2.9646e-10 | -1.4274e-10 | -4.1121e-10 | -2.9258e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2349 | 1.233 | 1.232 | 1.2349 | 1.233 | 1.232 | -1.0283 | -121.1282 | 118.9052 | -1.0283 | -121.1282 | 118.9052
Line13_13_14 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.005005 | -0.0050827 | -0.0050499 | 0.005305 | 0.0053827 | 0.0053499 | -0.049143 | -0.049057 | -0.04902 | 0.049743 | 0.049657 | 0.04962 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.2349 | 1.233 | 1.232 | 1.2506 | 1.2487 | 1.2477 | -1.0283 | -121.1282 | 118.9052 | -1.3005 | -121.3996 | 118.6332
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1603e-09 | 1.1277e-09 | 1.3341e-09 | -1.1919e-09 | -1.1661e-09 | -1.2642e-09 | 5.3352e-11 | 3.1328e-10 | 1.9764e-10 | -1.1607e-10 | -2.5456e-10 | -1.9376e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2349 | 1.233 | 1.232 | 1.2349 | 1.233 | 1.232 | -1.0283 | -121.1282 | 118.9052 | -1.0283 | -121.1282 | 118.9052
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8013e-10 | 5.6386e-10 | 6.6706e-10 | -6.1175e-10 | -6.022e-10 | -5.9709e-10 | 2.6676e-11 | 1.5664e-10 | 9.8819e-11 | -8.9391e-11 | -9.7921e-11 | -9.4941e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2349 | 1.233 | 1.232 | 1.2349 | 1.233 | 1.232 | -1.0283 | -121.1282 | 118.9052 | -1.0283 | -121.1282 | 118.9052
Line16_4_18 | 0 | 0.038563 | 0.038509 | 0 | 0.038563 | 0.038509 | 0 | 0.0089057 | 0.0088932 | 0 | 0.0089057 | 0.0088932 | 3.2343e-10 | 0.0074448 | 0.0074324 | -3.8188e-10 | -0.0074355 | -0.0074145 | -1.4521e-10 | 0.0074649 | 0.0074396 | -3.9171e-12 | -0.0074355 | -0.0074145 | 0 | -165.2839 | 74.8506 | 0 | 14.7161 | -105.1494 | 1.1883 | 1.1838 | 1.1825 | 1.1877 | 1.1807 | 1.1791 | -0.037401 | -120.2068 | 119.8781 | -0.046852 | -120.2839 | 119.8506
Line17_5_19 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.004105 | -0.0041827 | -0.0041499 | 0.004405 | 0.0044827 | 0.0044499 | -0.047343 | -0.047257 | -0.04722 | 0.047943 | 0.047857 | 0.04782 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.188 | 1.186 | 1.185 | 1.2036 | 1.2017 | 1.2007 | -0.16865 | -120.2711 | 119.7644 | -0.46266 | -120.5642 | 119.4705
Line1_1_3 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.003805 | -0.0038827 | -0.0038499 | 0.004105 | 0.0041826 | 0.0041499 | -0.046743 | -0.046657 | -0.04662 | 0.047343 | 0.047257 | 0.04722 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1724 | 1.1705 | 1.1695 | 1.188 | 1.186 | 1.185 | 0.13318 | -119.9701 | 120.0661 | -0.16865 | -120.2711 | 119.7644
Line2_1_4 | 0.1732 | 0.14093 | 0.14103 | 0.1732 | 0.14093 | 0.14103 | 0.04 | 0.032547 | 0.03257 | 0.04 | 0.032547 | 0.03257 | -0.012189 | -0.0049199 | -0.0048849 | 0.012491 | 0.0051339 | 0.0050646 | -0.045286 | -0.037776 | -0.037775 | 0.045861 | 0.038187 | 0.038179 | 105.1981 | -22.5497 | -142.5655 | -74.8019 | 157.4503 | 37.4345 | 1.1724 | 1.1705 | 1.1695 | 1.1883 | 1.1838 | 1.1825 | 0.13318 | -119.9701 | 120.0661 | -0.037401 | -120.2068 | 119.8781
Line3_1_5 | 0.1732 | 0.1732 | 0.17321 | 0.1732 | 0.1732 | 0.17321 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.003805 | -0.0038827 | -0.0038499 | 0.004105 | 0.0041827 | 0.0041499 | -0.046743 | -0.046657 | -0.04662 | 0.047343 | 0.047257 | 0.04722 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.1724 | 1.1705 | 1.1695 | 1.188 | 1.186 | 1.185 | 0.13318 | -119.9701 | 120.0661 | -0.16865 | -120.2711 | 119.7644
Line4_2_6 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.004105 | -0.0041827 | -0.0041499 | 0.004405 | 0.0044827 | 0.0044499 | -0.047343 | -0.047257 | -0.04722 | 0.047943 | 0.047857 | 0.04782 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.188 | 1.186 | 1.185 | 1.2036 | 1.2017 | 1.2007 | -0.16865 | -120.2711 | 119.7644 | -0.46266 | -120.5642 | 119.4705
Line5_6_7 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.004405 | -0.0044827 | -0.0044499 | 0.004705 | 0.0047827 | 0.0047499 | -0.047943 | -0.047857 | -0.04782 | 0.048543 | 0.048457 | 0.04842 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.2036 | 1.2017 | 1.2007 | 1.2193 | 1.2173 | 1.2163 | -0.46266 | -120.5642 | 119.4705 | -0.74913 | -120.8499 | 119.1842
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.508e-09 | 1.4581e-09 | 1.7647e-09 | -1.5389e-09 | -1.4962e-09 | -1.6957e-09 | 6.6743e-12 | 3.9185e-10 | 2.2203e-10 | -6.8745e-11 | -3.3406e-10 | -2.1787e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2193 | 1.2173 | 1.2163 | 1.2193 | 1.2173 | 1.2163 | -0.74913 | -120.8499 | 119.1842 | -0.74913 | -120.8499 | 119.1842
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0265e-10 | 4.8602e-10 | 5.8824e-10 | -5.3357e-10 | -5.2415e-10 | -5.1919e-10 | 2.2247e-12 | 1.3062e-10 | 7.401e-11 | -6.4296e-11 | -7.2825e-11 | -6.9845e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2193 | 1.2173 | 1.2163 | 1.2193 | 1.2173 | 1.2163 | -0.74913 | -120.8499 | 119.1842 | -0.74913 | -120.8499 | 119.1842
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0265e-10 | 4.8602e-10 | 5.8824e-10 | -5.3357e-10 | -5.2415e-10 | -5.1919e-10 | 2.2247e-12 | 1.3062e-10 | 7.401e-11 | -6.4296e-11 | -7.2825e-11 | -6.9845e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2193 | 1.2173 | 1.2163 | 1.2193 | 1.2173 | 1.2163 | -0.74913 | -120.8499 | 119.1842 | -0.74913 | -120.8499 | 119.1842
Line9_3_11 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.1732 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | -0.004105 | -0.0041827 | -0.0041499 | 0.004405 | 0.0044826 | 0.0044499 | -0.047343 | -0.047257 | -0.04722 | 0.047943 | 0.047857 | 0.04782 | 94.7869 | -25.2131 | -145.2131 | -85.2131 | 154.7869 | 34.7869 | 1.188 | 1.186 | 1.185 | 1.2036 | 1.2017 | 1.2007 | -0.16865 | -120.2711 | 119.7644 | -0.46266 | -120.5642 | 119.4705

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1844e-08 | -1.8352e-08 | 2.1822e-08 | 1.0049e-08 | 1.5886e-08 | -1.7561e-08 | -3.0675e-08 | 2.4637e-08 | 4.3052e-09 | 2.5374e-08 | -2.0987e-08 | -4.059e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1844e-08 | -1.8352e-08 | 2.1822e-08 | 1.0049e-08 | 1.5886e-08 | -1.7561e-08 | -3.0675e-08 | 2.4637e-08 | 4.3052e-09 | 2.5374e-08 | -2.0987e-08 | -4.059e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.8702e-09 | -1.5293e-08 | 1.8185e-08 | 8.075e-09 | 1.2828e-08 | -1.3924e-08 | -2.5562e-08 | 2.0531e-08 | 3.5877e-09 | 2.0261e-08 | -1.6881e-08 | -3.3414e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9221e-09 | -9.1758e-09 | 1.0911e-08 | 4.1269e-09 | 6.7104e-09 | -6.6503e-09 | -1.5337e-08 | 1.2319e-08 | 2.1526e-09 | 1.0037e-08 | -8.6683e-09 | -1.9064e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.974e-09 | -3.0586e-09 | 3.637e-09 | 1.7878e-10 | 5.9323e-10 | 6.2367e-10 | -5.1124e-09 | 4.1062e-09 | 7.1753e-10 | -1.8836e-10 | -4.5591e-10 | -4.7129e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9481e-09 | -6.1172e-09 | 7.2739e-09 | 2.1528e-09 | 3.6518e-09 | -3.0133e-09 | -1.0225e-08 | 8.2123e-09 | 1.4351e-09 | 4.9241e-09 | -4.5621e-09 | -1.1888e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.974e-09 | -3.0586e-09 | 3.637e-09 | 1.7878e-10 | 5.9323e-10 | 6.2367e-10 | -5.1124e-09 | 4.1062e-09 | 7.1753e-10 | -1.8836e-10 | -4.5591e-10 | -4.7129e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line16_4_18 | 0 | 3.3553 | 3.2357 | 0 | 3.3553 | 3.2357 | 0 | 0.77488 | 0.74724 | 0 | 0.77488 | 0.74724 | -1.229e-09 | 0.14985 | 0.20871 | 5.9908e-10 | -6.8486e-14 | -6.3081e-14 | -1.3347e-08 | 0.22763 | 0.14586 | -8.9929e-11 | 7.6155e-14 | 1.0679e-13 | 0 | 172.6328 | 73.5997 | 0 | -7.3672 | -106.4003 | 0.80859 | 0.3517 | 0.34075 | 0.7236 | 0 | 0 | -2.8316 | -130.7237 | 108.549 | -2.0447 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.974e-09 | -3.0586e-09 | 3.637e-09 | 1.7878e-10 | 5.9323e-10 | 6.2367e-10 | -5.1124e-09 | 4.1062e-09 | 7.1753e-10 | -1.8836e-10 | -4.5591e-10 | -4.7129e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5792e-08 | -2.4469e-08 | 2.9096e-08 | 1.3997e-08 | 2.2003e-08 | -2.4835e-08 | -4.09e-08 | 3.2849e-08 | 5.7403e-09 | 3.5599e-08 | -2.9199e-08 | -5.494e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line2_1_4 | 0 | 3.3553 | 3.2357 | 0 | 3.3553 | 3.2357 | 0 | 0.77488 | 0.74724 | 0 | 0.77488 | 0.74724 | -3.4389e-09 | 0.29969 | 0.41741 | 1.6448e-09 | -0.14985 | -0.20871 | -2.3066e-08 | 0.45526 | 0.29172 | 1.3208e-08 | -0.22763 | -0.14586 | 0 | 172.6328 | 73.5997 | 0 | -7.3672 | -106.4003 | 0.8937 | 0.7034 | 0.68151 | 0.80859 | 0.3517 | 0.34075 | -3.4688 | -130.7237 | 108.549 | -2.8316 | -130.7237 | 108.549
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9481e-09 | -6.1172e-09 | 7.2739e-09 | 2.1528e-09 | 3.6518e-09 | -3.0133e-09 | -1.0225e-08 | 8.2123e-09 | 1.4351e-09 | 4.9241e-09 | -4.5621e-09 | -1.1888e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.8702e-09 | -1.5293e-08 | 1.8185e-08 | 8.075e-09 | 1.2828e-08 | -1.3924e-08 | -2.5562e-08 | 2.0531e-08 | 3.5877e-09 | 2.0261e-08 | -1.6881e-08 | -3.3414e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.8962e-09 | -1.2234e-08 | 1.4548e-08 | 6.1009e-09 | 9.7691e-09 | -1.0287e-08 | -2.045e-08 | 1.6425e-08 | 2.8701e-09 | 1.5149e-08 | -1.2774e-08 | -2.6239e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9221e-09 | -9.1758e-09 | 1.0911e-08 | 4.1269e-09 | 6.7104e-09 | -6.6503e-09 | -1.5337e-08 | 1.2319e-08 | 2.1526e-09 | 1.0037e-08 | -8.6683e-09 | -1.9064e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.974e-09 | -3.0586e-09 | 3.637e-09 | 1.7878e-10 | 5.9323e-10 | 6.2367e-10 | -5.1124e-09 | 4.1062e-09 | 7.1753e-10 | -1.8836e-10 | -4.5591e-10 | -4.7129e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.974e-09 | -3.0586e-09 | 3.637e-09 | 1.7878e-10 | 5.9323e-10 | 6.2367e-10 | -5.1124e-09 | 4.1062e-09 | 7.1753e-10 | -1.8836e-10 | -4.5591e-10 | -4.7129e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3818e-08 | -2.141e-08 | 2.5459e-08 | 1.2023e-08 | 1.8945e-08 | -2.1198e-08 | -3.5787e-08 | 2.8743e-08 | 5.0227e-09 | 3.0486e-08 | -2.5093e-08 | -4.7765e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8937 | 0.7034 | 0.68151 | 0.8937 | 0.7034 | 0.68151 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.063e-08 | -1.6471e-08 | 1.9585e-08 | 9.0191e-09 | 1.4258e-08 | -1.5761e-08 | -2.7531e-08 | 2.2112e-08 | 3.8639e-09 | 2.2773e-08 | -1.8836e-08 | -3.6429e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.063e-08 | -1.6471e-08 | 1.9585e-08 | 9.0191e-09 | 1.4258e-08 | -1.5761e-08 | -2.7531e-08 | 2.2112e-08 | 3.8639e-09 | 2.2773e-08 | -1.8836e-08 | -3.6429e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.8586e-09 | -1.3726e-08 | 1.6321e-08 | 7.2473e-09 | 1.1513e-08 | -1.2497e-08 | -2.2942e-08 | 1.8427e-08 | 3.2199e-09 | 1.8185e-08 | -1.515e-08 | -2.9989e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3152e-09 | -8.2354e-09 | 9.7926e-09 | 3.7039e-09 | 6.0227e-09 | -5.9687e-09 | -1.3765e-08 | 1.1056e-08 | 1.932e-09 | 9.0079e-09 | -7.7798e-09 | -1.711e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7717e-09 | -2.7451e-09 | 3.2642e-09 | 1.6046e-10 | 5.3243e-10 | 5.5975e-10 | -4.5885e-09 | 3.6853e-09 | 6.4399e-10 | -1.6905e-10 | -4.0918e-10 | -4.2299e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5434e-09 | -5.4902e-09 | 6.5284e-09 | 1.9322e-09 | 3.2776e-09 | -2.7045e-09 | -9.1769e-09 | 7.3706e-09 | 1.288e-09 | 4.4194e-09 | -4.0945e-09 | -1.067e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7717e-09 | -2.7451e-09 | 3.2642e-09 | 1.6046e-10 | 5.3243e-10 | 5.5975e-10 | -4.5885e-09 | 3.6853e-09 | 6.4399e-10 | -1.6905e-10 | -4.0918e-10 | -4.2299e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line16_4_18 | 0 | 3.1787 | 3.0654 | 0 | 3.1787 | 3.0654 | 0 | 0.7341 | 0.70791 | 0 | 0.7341 | 0.70791 | -1.1031e-09 | 0.13449 | 0.18731 | 5.3768e-10 | -6.166e-14 | -5.6599e-14 | -1.1979e-08 | 0.2043 | 0.13091 | -8.0712e-11 | 6.8208e-14 | 9.5992e-14 | 0 | 172.6328 | 73.5997 | 0 | -7.3672 | -106.4003 | 0.76603 | 0.33319 | 0.32282 | 0.68551 | 0 | 0 | -2.8316 | -130.7237 | 108.549 | -2.0447 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7717e-09 | -2.7451e-09 | 3.2642e-09 | 1.6046e-10 | 5.3243e-10 | 5.5975e-10 | -4.5885e-09 | 3.6853e-09 | 6.4399e-10 | -1.6905e-10 | -4.0918e-10 | -4.2299e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4174e-08 | -2.1961e-08 | 2.6114e-08 | 1.2563e-08 | 1.9748e-08 | -2.229e-08 | -3.6708e-08 | 2.9483e-08 | 5.1519e-09 | 3.195e-08 | -2.6206e-08 | -4.9309e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line2_1_4 | 0 | 3.1787 | 3.0654 | 0 | 3.1787 | 3.0654 | 0 | 0.7341 | 0.70791 | 0 | 0.7341 | 0.70791 | -3.0864e-09 | 0.26898 | 0.37463 | 1.4763e-09 | -0.13449 | -0.18731 | -2.0702e-08 | 0.4086 | 0.26182 | 1.1854e-08 | -0.2043 | -0.13091 | 0 | 172.6328 | 73.5997 | 0 | -7.3672 | -106.4003 | 0.84666 | 0.66637 | 0.64564 | 0.76603 | 0.33319 | 0.32282 | -3.4688 | -130.7237 | 108.549 | -2.8316 | -130.7237 | 108.549
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5434e-09 | -5.4902e-09 | 6.5284e-09 | 1.9322e-09 | 3.2775e-09 | -2.7045e-09 | -9.1769e-09 | 7.3706e-09 | 1.288e-09 | 4.4194e-09 | -4.0945e-09 | -1.067e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.8586e-09 | -1.3726e-08 | 1.6321e-08 | 7.2474e-09 | 1.1513e-08 | -1.2497e-08 | -2.2942e-08 | 1.8427e-08 | 3.2199e-09 | 1.8185e-08 | -1.515e-08 | -2.9989e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.0869e-09 | -1.098e-08 | 1.3057e-08 | 5.4756e-09 | 8.7678e-09 | -9.2329e-09 | -1.8354e-08 | 1.4741e-08 | 2.576e-09 | 1.3596e-08 | -1.1465e-08 | -2.355e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3152e-09 | -8.2354e-09 | 9.7926e-09 | 3.7039e-09 | 6.0227e-09 | -5.9687e-09 | -1.3765e-08 | 1.1056e-08 | 1.932e-09 | 9.0079e-09 | -7.7798e-09 | -1.711e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7717e-09 | -2.7451e-09 | 3.2642e-09 | 1.6046e-10 | 5.3243e-10 | 5.5975e-10 | -4.5885e-09 | 3.6853e-09 | 6.4399e-10 | -1.6905e-10 | -4.0918e-10 | -4.2299e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7717e-09 | -2.7451e-09 | 3.2642e-09 | 1.6046e-10 | 5.3243e-10 | 5.5975e-10 | -4.5885e-09 | 3.6853e-09 | 6.4399e-10 | -1.6905e-10 | -4.0918e-10 | -4.2299e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2402e-08 | -1.9216e-08 | 2.2849e-08 | 1.0791e-08 | 1.7003e-08 | -1.9025e-08 | -3.2119e-08 | 2.5797e-08 | 4.5079e-09 | 2.7362e-08 | -2.2521e-08 | -4.2869e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84666 | 0.66637 | 0.64564 | 0.84666 | 0.66637 | 0.64564 | -3.4688 | -130.7237 | 108.549 | -3.4688 | -130.7237 | 108.549

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1908e-10 | -1.8308e-10 | 1.9959e-10 | 1.0041e-10 | 1.5916e-10 | -1.5699e-10 | -2.2152e-10 | 2.5709e-10 | 5.0686e-11 | 1.83e-10 | -2.2168e-10 | -4.7651e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1908e-10 | -1.8308e-10 | 1.9959e-10 | 1.0041e-10 | 1.5916e-10 | -1.5699e-10 | -2.2152e-10 | 2.5709e-10 | 5.0686e-11 | 1.83e-10 | -2.2168e-10 | -4.7651e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.9235e-11 | -1.5257e-10 | 1.6632e-10 | 8.0566e-11 | 1.2865e-10 | -1.2373e-10 | -1.846e-10 | 2.1424e-10 | 4.2239e-11 | 1.4608e-10 | -1.7883e-10 | -3.9203e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9541e-11 | -9.1541e-11 | 9.9794e-11 | 4.0872e-11 | 6.7618e-11 | -5.7201e-11 | -1.1076e-10 | 1.2855e-10 | 2.5343e-11 | 7.2242e-11 | -9.3134e-11 | -2.2308e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9847e-11 | -3.0514e-11 | 3.3265e-11 | 1.1776e-12 | 6.5908e-12 | 9.3278e-12 | -3.6921e-11 | 4.2849e-11 | 8.4477e-12 | -1.5996e-12 | -7.4361e-12 | -5.4127e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9694e-11 | -6.1027e-11 | 6.6529e-11 | 2.1025e-11 | 3.7105e-11 | -2.3937e-11 | -7.3842e-11 | 8.5697e-11 | 1.6895e-11 | 3.5321e-11 | -5.0285e-11 | -1.386e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9847e-11 | -3.0514e-11 | 3.3265e-11 | 1.1776e-12 | 6.5908e-12 | 9.3278e-12 | -3.6921e-11 | 4.2849e-11 | 8.4477e-12 | -1.5996e-12 | -7.4361e-12 | -5.4127e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line16_4_18 | 0 | 0.030745 | 0.030718 | 0 | 0.030745 | 0.030718 | 0 | 0.0071002 | 0.007094 | 0 | 0.0071002 | 0.007094 | -2.5562e-11 | 0.0047401 | 0.0047372 | 5.4624e-12 | -0.0047262 | -0.0047179 | -1.1031e-10 | 0.0047461 | 0.0047326 | -1.6815e-12 | -0.0047262 | -0.0047179 | 0 | -165.2018 | 74.9622 | 0 | 14.7982 | -105.0378 | 0.94905 | 0.94473 | 0.94392 | 0.94843 | 0.94136 | 0.94053 | -0.028434 | -120.1653 | 119.934 | -0.029162 | -120.2018 | 119.9622
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9847e-11 | -3.0514e-11 | 3.3265e-11 | 1.1776e-12 | 6.5908e-12 | 9.3278e-12 | -3.6921e-11 | 4.2849e-11 | 8.4477e-12 | -1.5996e-12 | -7.4361e-12 | -5.4127e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5878e-10 | -2.4411e-10 | 2.6612e-10 | 1.4011e-10 | 2.2019e-10 | -2.2352e-10 | -2.9537e-10 | 3.4279e-10 | 6.7582e-11 | 2.5685e-10 | -3.0738e-10 | -6.4547e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line2_1_4 | 0 | 0.030745 | 0.030718 | 0 | 0.030745 | 0.030718 | 0 | 0.0071002 | 0.007094 | 0 | 0.0071002 | 0.007094 | -4.805e-11 | 0.004754 | 0.0047566 | 2.8884e-11 | -0.0047401 | -0.0047372 | -1.7178e-10 | 0.0047661 | 0.0047472 | 1.0867e-10 | -0.0047461 | -0.0047326 | 0 | -165.2018 | 74.9622 | 0 | 14.7982 | -105.0378 | 0.94966 | 0.9481 | 0.94731 | 0.94905 | 0.94473 | 0.94392 | -0.027706 | -120.129 | 119.906 | -0.028434 | -120.1653 | 119.934
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9694e-11 | -6.1027e-11 | 6.6529e-11 | 2.1025e-11 | 3.7104e-11 | -2.3937e-11 | -7.3842e-11 | 8.5697e-11 | 1.6895e-11 | 3.5321e-11 | -5.0285e-11 | -1.386e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.9235e-11 | -1.5257e-10 | 1.6632e-10 | 8.0566e-11 | 1.2865e-10 | -1.2373e-10 | -1.846e-10 | 2.1424e-10 | 4.2238e-11 | 1.4608e-10 | -1.7883e-10 | -3.9203e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9388e-11 | -1.2205e-10 | 1.3306e-10 | 6.0719e-11 | 9.8132e-11 | -9.0466e-11 | -1.4768e-10 | 1.7139e-10 | 3.3791e-11 | 1.0916e-10 | -1.3598e-10 | -3.0756e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9541e-11 | -9.1541e-11 | 9.9794e-11 | 4.0872e-11 | 6.7618e-11 | -5.7201e-11 | -1.1076e-10 | 1.2855e-10 | 2.5343e-11 | 7.2242e-11 | -9.3134e-11 | -2.2308e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9847e-11 | -3.0514e-11 | 3.3265e-11 | 1.1776e-12 | 6.5908e-12 | 9.3278e-12 | -3.6921e-11 | 4.2849e-11 | 8.4477e-12 | -1.5996e-12 | -7.4361e-12 | -5.4127e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9847e-11 | -3.0514e-11 | 3.3265e-11 | 1.1776e-12 | 6.5908e-12 | 9.3278e-12 | -3.6921e-11 | 4.2849e-11 | 8.4477e-12 | -1.5996e-12 | -7.4361e-12 | -5.4127e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3893e-10 | -2.136e-10 | 2.3285e-10 | 1.2026e-10 | 1.8967e-10 | -1.9026e-10 | -2.5845e-10 | 2.9994e-10 | 5.9134e-11 | 2.1993e-10 | -2.6453e-10 | -5.6099e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94966 | 0.9481 | 0.94731 | 0.94966 | 0.9481 | 0.94731 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0688e-10 | -1.6432e-10 | 1.7913e-10 | 9.0121e-11 | 1.4285e-10 | -1.409e-10 | -1.9882e-10 | 2.3074e-10 | 4.5491e-11 | 1.6425e-10 | -1.9896e-10 | -4.2767e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line10_11_12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0688e-10 | -1.6432e-10 | 1.7913e-10 | 9.0121e-11 | 1.4285e-10 | -1.409e-10 | -1.9882e-10 | 2.3074e-10 | 4.5491e-11 | 1.6425e-10 | -1.9896e-10 | -4.2767e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line11_12_13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.9064e-11 | -1.3693e-10 | 1.4928e-10 | 7.2308e-11 | 1.1546e-10 | -1.1105e-10 | -1.6568e-10 | 1.9229e-10 | 3.7909e-11 | 1.3111e-10 | -1.605e-10 | -3.5185e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3439e-11 | -8.2159e-11 | 8.9565e-11 | 3.6683e-11 | 6.0688e-11 | -5.1339e-11 | -9.941e-11 | 1.1537e-10 | 2.2746e-11 | 6.4838e-11 | -8.3588e-11 | -2.0022e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line13_13_14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7813e-11 | -2.7386e-11 | 2.9855e-11 | 1.0569e-12 | 5.9153e-12 | 8.3718e-12 | -3.3137e-11 | 3.8457e-11 | 7.5819e-12 | -1.4357e-12 | -6.674e-12 | -4.8579e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5626e-11 | -5.4772e-11 | 5.971e-11 | 1.887e-11 | 3.3302e-11 | -2.1483e-11 | -6.6273e-11 | 7.6914e-11 | 1.5164e-11 | 3.1701e-11 | -4.5131e-11 | -1.244e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7813e-11 | -2.7386e-11 | 2.9855e-11 | 1.0569e-12 | 5.9153e-12 | 8.3718e-12 | -3.3137e-11 | 3.8457e-11 | 7.5819e-12 | -1.4357e-12 | -6.674e-12 | -4.8579e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line16_4_18 | 0 | 0.029127 | 0.029101 | 0 | 0.029127 | 0.029101 | 0 | 0.0067265 | 0.0067206 | 0 | 0.0067265 | 0.0067206 | -2.2942e-11 | 0.0042543 | 0.0042517 | 4.9025e-12 | -0.0042418 | -0.0042343 | -9.9005e-11 | 0.0042597 | 0.0042475 | -1.5092e-12 | -0.0042418 | -0.0042343 | 0 | -165.2018 | 74.9622 | 0 | 14.7982 | -105.0378 | 0.8991 | 0.89501 | 0.89424 | 0.89851 | 0.89182 | 0.89103 | -0.028434 | -120.1653 | 119.934 | -0.029162 | -120.2018 | 119.9622
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7813e-11 | -2.7386e-11 | 2.9855e-11 | 1.0569e-12 | 5.9153e-12 | 8.3718e-12 | -3.3137e-11 | 3.8457e-11 | 7.5819e-12 | -1.4357e-12 | -6.674e-12 | -4.8579e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line1_1_3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.425e-10 | -2.1909e-10 | 2.3884e-10 | 1.2575e-10 | 1.9762e-10 | -2.0061e-10 | -2.6509e-10 | 3.0766e-10 | 6.0655e-11 | 2.3052e-10 | -2.7587e-10 | -5.7931e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line2_1_4 | 0 | 0.029127 | 0.029101 | 0 | 0.029127 | 0.029101 | 0 | 0.0067265 | 0.0067206 | 0 | 0.0067265 | 0.0067206 | -4.3125e-11 | 0.0042667 | 0.004269 | 2.5923e-11 | -0.0042543 | -0.0042517 | -1.5417e-10 | 0.0042776 | 0.0042607 | 9.7533e-11 | -0.0042597 | -0.0042475 | 0 | -165.2018 | 74.9622 | 0 | 14.7982 | -105.0378 | 0.89968 | 0.8982 | 0.89745 | 0.8991 | 0.89501 | 0.89424 | -0.027706 | -120.129 | 119.906 | -0.028434 | -120.1653 | 119.934
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5626e-11 | -5.4772e-11 | 5.971e-11 | 1.887e-11 | 3.3302e-11 | -2.1483e-11 | -6.6273e-11 | 7.6914e-11 | 1.5164e-11 | 3.1701e-11 | -4.5131e-11 | -1.244e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line4_2_6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.9064e-11 | -1.3693e-10 | 1.4928e-10 | 7.2308e-11 | 1.1546e-10 | -1.1105e-10 | -1.6568e-10 | 1.9229e-10 | 3.7909e-11 | 1.3111e-10 | -1.605e-10 | -3.5185e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line5_6_7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.1251e-11 | -1.0954e-10 | 1.1942e-10 | 5.4495e-11 | 8.8074e-11 | -8.1194e-11 | -1.3255e-10 | 1.5383e-10 | 3.0327e-11 | 9.7974e-11 | -1.2205e-10 | -2.7604e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3439e-11 | -8.2159e-11 | 8.9565e-11 | 3.6683e-11 | 6.0688e-11 | -5.1338e-11 | -9.941e-11 | 1.1537e-10 | 2.2746e-11 | 6.4838e-11 | -8.3588e-11 | -2.0022e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7813e-11 | -2.7386e-11 | 2.9855e-11 | 1.0569e-12 | 5.9153e-12 | 8.3718e-12 | -3.3137e-11 | 3.8457e-11 | 7.5819e-12 | -1.4357e-12 | -6.674e-12 | -4.8579e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7813e-11 | -2.7386e-11 | 2.9855e-11 | 1.0569e-12 | 5.9153e-12 | 8.3718e-12 | -3.3137e-11 | 3.8457e-11 | 7.5819e-12 | -1.4357e-12 | -6.674e-12 | -4.8579e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906
Line9_3_11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2469e-10 | -1.917e-10 | 2.0899e-10 | 1.0793e-10 | 1.7023e-10 | -1.7076e-10 | -2.3196e-10 | 2.692e-10 | 5.3073e-11 | 1.9738e-10 | -2.3742e-10 | -5.0349e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89968 | 0.8982 | 0.89745 | 0.89968 | 0.8982 | 0.89745 | -0.027706 | -120.129 | 119.906 | -0.027706 | -120.129 | 119.906