## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3036 | 3.3036 | 0 | 0 | 114.4404 | 114.4404 | 37.7713 | -20.7457 | 43.3355 | -24.018 | -70.8485 | 109.1515 | 0.50232 | 0.27733 | -21.9239 | -21.6675
Line_1 | 4.0718 | 4.0718 | 7.8074 | 0 | 141.0522 | 141.0522 | -1e-07 | 25.8644 | -1e-07 | 29.3462 | 109.7241 | -70.2759 | 0 | 0.27733 | 0 | -21.6675
Line_2 | 0.76909 | 0.76909 | 0 | 0 | 26.6421 | 26.6421 | 6.0414 | -5.1187 | 6.3751 | -5.3281 | -67.816 | 112.184 | 0.32967 | 0.27733 | -21.2767 | -21.6675

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3036 | 3.3036 | 0 | 0 | 114.4404 | 114.4404 | 37.7713 | -20.7457 | 43.3355 | -24.018 | -70.8485 | 109.1515 | 0.50232 | 0.27733 | -21.9239 | -21.6675
Line_1 | 4.0718 | 4.0718 | 7.8074 | 0 | 141.0522 | 141.0522 | -1e-07 | 25.8644 | -1e-07 | 29.3462 | 109.7241 | -70.2759 | 0 | 0.27733 | 0 | -21.6675
Line_2 | 0.76909 | 0.76909 | 0 | 0 | 26.6421 | 26.6421 | 6.0414 | -5.1187 | 6.3751 | -5.3281 | -67.816 | 112.184 | 0.32967 | 0.27733 | -21.2767 | -21.6675

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.77289 | 0.77289 | 0 | 0 | 26.7736 | 26.7736 | 20.4887 | -19.5569 | 16.8303 | -15.773 | -45.3926 | 134.6074 | 0.99034 | 0.93842 | -5.9915 | -6.5057
Line_1 | 1.057 | 1.057 | 2.0668 | 0 | 36.615 | 36.615 | -23.4304 | 25.1732 | -21.4091 | 23.3865 | 130.6015 | -49.3985 | 0.86682 | 0.93842 | -6.9796 | -6.5057
Line_2 | 0.29104 | 0.29104 | 0 | 0 | 10.0818 | 10.0818 | 5.7485 | -5.6164 | 7.7635 | -7.6135 | -60.0901 | 119.9099 | 0.95817 | 0.93842 | -6.6085 | -6.5057

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.77289 | 0.77289 | 0 | 0 | 26.7736 | 26.7736 | 20.4887 | -19.5569 | 16.8303 | -15.773 | -45.3926 | 134.6074 | 0.99034 | 0.93842 | -5.9915 | -6.5057
Line_1 | 1.057 | 1.057 | 2.0668 | 0 | 36.615 | 36.615 | -23.4304 | 25.1732 | -21.4091 | 23.3865 | 130.6015 | -49.3985 | 0.86682 | 0.93842 | -6.9796 | -6.5057
Line_2 | 0.29104 | 0.29104 | 0 | 0 | 10.0818 | 10.0818 | 5.7485 | -5.6164 | 7.7635 | -7.6135 | -60.0901 | 119.9099 | 0.95817 | 0.93842 | -6.6085 | -6.5057

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34465 | 2.8163 | 2.9394 | 0.34465 | 2.8163 | 2.9394 | 3.9797 | 32.5201 | 33.9408 | 3.9797 | 32.5201 | 33.9408 | -2.8467 | 27.5894 | -9.8021 | 2.9085 | -23.4649 | 14.2948 | -3.6108 | 3.3833 | 16.3211 | 3.6809 | 1.2964 | -11.2236 | 130.3426 | -157.3314 | 16.2542 | -49.6574 | 22.6686 | -163.7458 | 1.1554 | 0.85474 | 0.56093 | 1.1788 | 0.72265 | 0.53548 | 2.0909 | -150.3401 | 137.2424 | 2.0284 | -160.4937 | 158.117
Line_1 | 0.19448 | 3.4668 | 3.5514 | 0.19448 | 3.4668 | 3.5514 | 2.2456 | 40.0309 | 41.0075 | 2.2456 | 40.0309 | 41.0075 | 1.8069 | -22.6769 | 23.5803 | -1.7872 | 28.9265 | -17.0221 | 1.975 | 7.4181 | -6.4306 | -1.9527 | -0.32717 | 13.8717 | -45.5053 | 20.1544 | -162.7055 | 134.4947 | -159.8456 | 17.2945 | 1.192 | 0.59602 | 0.59602 | 1.1788 | 0.72265 | 0.53548 | 2.0403 | -177.9597 | -177.9597 | 2.0284 | -160.4937 | 158.117
Line_2 | 0.15134 | 0.66475 | 0.6148 | 0.15134 | 0.66475 | 0.6148 | 1.7476 | 7.6758 | 7.0991 | 1.7476 | 7.6758 | 7.0991 | 1.1332 | 5.6914 | -2.5307 | -1.1212 | -5.4616 | 2.7272 | 1.7417 | 1.2299 | 2.8712 | -1.7282 | -0.96922 | -2.6482 | -54.9959 | -170.5566 | 22.2743 | 125.0041 | 9.4434 | -157.7257 | 1.189 | 0.75859 | 0.53912 | 1.1788 | 0.72265 | 0.53548 | 1.9557 | -158.3623 | 153.6676 | 2.0284 | -160.4937 | 158.117

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34465 | 2.8163 | 2.9394 | 0.34465 | 2.8163 | 2.9394 | 3.9797 | 32.5201 | 33.9408 | 3.9797 | 32.5201 | 33.9408 | -2.8467 | 27.5894 | -9.8021 | 2.9085 | -23.4649 | 14.2948 | -3.6108 | 3.3833 | 16.3211 | 3.6809 | 1.2964 | -11.2236 | 130.3426 | -157.3314 | 16.2542 | -49.6574 | 22.6686 | -163.7458 | 1.1554 | 0.85474 | 0.56093 | 1.1788 | 0.72265 | 0.53548 | 2.0909 | -150.3401 | 137.2424 | 2.0284 | -160.4937 | 158.117
Line_1 | 0.19448 | 3.4668 | 3.5514 | 0.19448 | 3.4668 | 3.5514 | 2.2456 | 40.0309 | 41.0075 | 2.2456 | 40.0309 | 41.0075 | 1.8069 | -22.6769 | 23.5803 | -1.7872 | 28.9265 | -17.0221 | 1.975 | 7.4181 | -6.4306 | -1.9527 | -0.32717 | 13.8717 | -45.5053 | 20.1544 | -162.7055 | 134.4947 | -159.8456 | 17.2945 | 1.192 | 0.59602 | 0.59602 | 1.1788 | 0.72265 | 0.53548 | 2.0403 | -177.9597 | -177.9597 | 2.0284 | -160.4937 | 158.117
Line_2 | 0.15134 | 0.66475 | 0.6148 | 0.15134 | 0.66475 | 0.6148 | 1.7476 | 7.6758 | 7.0991 | 1.7476 | 7.6758 | 7.0991 | 1.1332 | 5.6914 | -2.5307 | -1.1212 | -5.4616 | 2.7272 | 1.7417 | 1.2299 | 2.8712 | -1.7282 | -0.96922 | -2.6482 | -54.9959 | -170.5566 | 22.2743 | 125.0041 | 9.4434 | -157.7257 | 1.189 | 0.75859 | 0.53912 | 1.1788 | 0.72265 | 0.53548 | 1.9557 | -158.3623 | 153.6676 | 2.0284 | -160.4937 | 158.117

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26375 | 1.2082 | 1.1737 | 0.26375 | 1.2082 | 1.1737 | 3.0455 | 13.9508 | 13.5526 | 3.0455 | 13.9508 | 13.5526 | -1.7236 | 14.6366 | 0.36638 | 1.7598 | -13.8776 | 0.34995 | -3.0377 | 0.70931 | 11.719 | 3.0787 | 0.15191 | -10.9062 | 120.8148 | -135.4144 | 31.9789 | -59.1852 | 44.5856 | -148.0211 | 1.1468 | 1.0504 | 0.86513 | 1.1644 | 0.99481 | 0.80515 | 1.244 | -132.6399 | 120.1882 | 1.0629 | -136.0415 | 123.8167
Line_1 | 0.14172 | 1.5139 | 1.518 | 0.14172 | 1.5139 | 1.518 | 1.6364 | 17.4815 | 17.5279 | 1.6364 | 17.4815 | 17.5279 | 1.1337 | -16.1122 | 1.4292 | -1.1232 | 17.3041 | -0.23098 | 1.5511 | -0.38203 | -12.7512 | -1.5392 | 1.7343 | 14.1107 | -52.8182 | 38.235 | -147.1211 | 127.1818 | -141.765 | 32.8789 | 1.174 | 0.92193 | 0.73203 | 1.1644 | 0.99481 | 0.80515 | 1.0196 | -140.4067 | 129.274 | 1.0629 | -136.0415 | 123.8167
Line_2 | 0.1239 | 0.3405 | 0.34491 | 0.1239 | 0.3405 | 0.34491 | 1.4307 | 3.9318 | 3.9827 | 1.4307 | 3.9318 | 3.9827 | 0.64456 | 3.4868 | 0.18083 | -0.63657 | -3.4265 | -0.11897 | 1.5486 | 1.9546 | 3.2746 | -1.5395 | -1.8862 | -3.2044 | -66.4724 | -164.8737 | 35.9428 | 113.5276 | 15.1263 | -144.0572 | 1.1724 | 1.0167 | 0.82347 | 1.1644 | 0.99481 | 0.80515 | 0.92914 | -135.5993 | 122.7821 | 1.0629 | -136.0415 | 123.8167

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26375 | 1.2082 | 1.1737 | 0.26375 | 1.2082 | 1.1737 | 3.0455 | 13.9508 | 13.5526 | 3.0455 | 13.9508 | 13.5526 | -1.7236 | 14.6366 | 0.36638 | 1.7598 | -13.8776 | 0.34995 | -3.0377 | 0.70931 | 11.719 | 3.0787 | 0.15191 | -10.9062 | 120.8148 | -135.4144 | 31.9789 | -59.1852 | 44.5856 | -148.0211 | 1.1468 | 1.0504 | 0.86513 | 1.1644 | 0.99481 | 0.80515 | 1.244 | -132.6399 | 120.1882 | 1.0629 | -136.0415 | 123.8167
Line_1 | 0.14172 | 1.5139 | 1.518 | 0.14172 | 1.5139 | 1.518 | 1.6364 | 17.4815 | 17.5279 | 1.6364 | 17.4815 | 17.5279 | 1.1337 | -16.1122 | 1.4292 | -1.1232 | 17.3041 | -0.23098 | 1.5511 | -0.38203 | -12.7512 | -1.5392 | 1.7343 | 14.1107 | -52.8182 | 38.235 | -147.1211 | 127.1818 | -141.765 | 32.8789 | 1.174 | 0.92193 | 0.73203 | 1.1644 | 0.99481 | 0.80515 | 1.0196 | -140.4067 | 129.274 | 1.0629 | -136.0415 | 123.8167
Line_2 | 0.1239 | 0.3405 | 0.34491 | 0.1239 | 0.3405 | 0.34491 | 1.4307 | 3.9318 | 3.9827 | 1.4307 | 3.9318 | 3.9827 | 0.64456 | 3.4868 | 0.18083 | -0.63657 | -3.4265 | -0.11897 | 1.5486 | 1.9546 | 3.2746 | -1.5395 | -1.8862 | -3.2044 | -66.4724 | -164.8737 | 35.9428 | 113.5276 | 15.1263 | -144.0572 | 1.1724 | 1.0167 | 0.82347 | 1.1644 | 0.99481 | 0.80515 | 0.92914 | -135.5993 | 122.7821 | 1.0629 | -136.0415 | 123.8167

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7105 | 0.77395 | 0.61112 | 1.7087 | 0.77567 | 0.61289 | 19.7512 | 8.9368 | 7.0566 | 19.7301 | 8.9567 | 7.077 | 7.2803 | -10.1154 | 8.4951 | -5.1115 | 10.3947 | -8.5919 | 6.8944 | 5.031 | 0.95763 | -4.346 | -5.1659 | -1.0059 | -65.6699 | 82.299 | 122.1456 | 114.3409 | -97.6495 | -57.9075 |  | 0.50765 | 1.2641 | 1.2115 | 0.34005 | 1.296 | 1.2224 | -22.2297 | -124.1451 | 128.5772 | -25.2866 | -124.0756 | 128.7701
Line_1 | 2.555 | 0.59767 | 0.41994 | 2.5573 | 0.59543 | 0.41753 | 29.5029 | 6.9013 | 4.8491 | 29.5292 | 6.8754 | 4.8212 | 9.2992e-11 | 8.3703 | -5.4544 | 7.6277 | -8.4993 | 4.9879 | -9.627e-11 | -3.6054 | -3.6821 | 6.5308 | 2.6749 | 3.1387 | 114.1613 | -106.5212 | -83.4204 | -65.8565 | 73.394 | 96.5893 |  | 0 | 1.3206 | 1.3571 | 0.34005 | 1.296 | 1.2224 | 0 | -129.8242 | 130.6016 | -25.2866 | -124.0756 | 128.7701
Line_2 | 0.85044 | 0.21095 | 0.2979 | 0.84866 | 0.20917 | 0.2967 | 9.82 | 2.4358 | 3.4398 | 9.7994 | 2.4153 | 3.426 | 3.9896 | 2.1928 | -3.1911 | -2.5162 | -1.8954 | 3.604 | 3.1058 | -2.3419 | 2.0257 | -2.1848 | 2.491 | -2.1328 | -66.2586 | -71.3194 | -20.8679 | 113.7461 | 108.6569 | 159.3866 |  | 0.51487 | 1.3171 | 1.0988 | 0.34005 | 1.296 | 1.2224 | -28.359 | -118.2025 | 126.7248 | -25.2866 | -124.0756 | 128.7701

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7105 | 0.77395 | 0.61112 | 1.7087 | 0.77567 | 0.61289 | 19.7512 | 8.9368 | 7.0566 | 19.7301 | 8.9567 | 7.077 | 7.2803 | -10.1154 | 8.4951 | -5.1115 | 10.3947 | -8.5919 | 6.8944 | 5.031 | 0.95763 | -4.346 | -5.1659 | -1.0059 | -65.6699 | 82.299 | 122.1456 | 114.3409 | -97.6495 | -57.9075 |  | 0.50765 | 1.2641 | 1.2115 | 0.34005 | 1.296 | 1.2224 | -22.2297 | -124.1451 | 128.5772 | -25.2866 | -124.0756 | 128.7701
Line_1 | 2.555 | 0.59767 | 0.41994 | 2.5573 | 0.59543 | 0.41753 | 29.5029 | 6.9013 | 4.8491 | 29.5292 | 6.8754 | 4.8212 | 9.2992e-11 | 8.3703 | -5.4544 | 7.6277 | -8.4993 | 4.9879 | -9.627e-11 | -3.6054 | -3.6821 | 6.5308 | 2.6749 | 3.1387 | 114.1613 | -106.5212 | -83.4204 | -65.8565 | 73.394 | 96.5893 |  | 0 | 1.3206 | 1.3571 | 0.34005 | 1.296 | 1.2224 | 0 | -129.8242 | 130.6016 | -25.2866 | -124.0756 | 128.7701
Line_2 | 0.85044 | 0.21095 | 0.2979 | 0.84866 | 0.20917 | 0.2967 | 9.82 | 2.4358 | 3.4398 | 9.7994 | 2.4153 | 3.426 | 3.9896 | 2.1928 | -3.1911 | -2.5162 | -1.8954 | 3.604 | 3.1058 | -2.3419 | 2.0257 | -2.1848 | 2.491 | -2.1328 | -66.2586 | -71.3194 | -20.8679 | 113.7461 | 108.6569 | 159.3866 |  | 0.51487 | 1.3171 | 1.0988 | 0.34005 | 1.296 | 1.2224 | -28.359 | -118.2025 | 126.7248 | -25.2866 | -124.0756 | 128.7701

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.46677 | 0.21921 | 0.298 | 0.46618 | 0.21953 | 0.29841 | 5.3898 | 2.5312 | 3.441 | 5.3829 | 2.5349 | 3.4458 | 4.5755 | -3.0219 | 2.5785 | -4.3826 | 3.0752 | -2.6019 | 2.3765 | 0.15303 | -2.9912 | -2.1807 | -0.17152 | 3.0309 | -35.1885 | 62.3881 | 172.8047 | 144.8412 | -117.4673 | -7.2894 |  | 0.9566 | 1.1954 | 1.1477 | 0.90939 | 1.215 | 1.1593 | -7.7419 | -120.5108 | 123.5674 | -8.7048 | -120.6596 | 123.3546
Line_1 | 0.80933 | 0.19276 | 0.14482 | 0.8101 | 0.19217 | 0.14414 | 9.3454 | 2.2258 | 1.6723 | 9.3542 | 2.219 | 1.6644 | -6.0751 | 2.7071 | -1.8439 | 6.8957 | -2.666 | 1.7505 | -4.3211 | -0.51901 | 0.79408 | 4.9812 | 0.40262 | -0.81165 | 135.4747 | -111.8966 | -31.9581 | -44.5475 | 67.9283 | 148.2305 |  | 0.79773 | 1.2384 | 1.2005 | 0.90939 | 1.215 | 1.1593 | -9.1016 | -122.7495 | 124.7429 | -8.7048 | -120.6596 | 123.3546
Line_2 | 0.35894 | 0.033398 | 0.17786 | 0.35833 | 0.033498 | 0.17757 | 4.1447 | 0.38565 | 2.0537 | 4.1376 | 0.3868 | 2.0504 | 2.7307 | 0.40337 | -0.77347 | -2.5131 | -0.40923 | 0.85139 | 2.9753 | 0.23686 | 2.1882 | -2.8005 | -0.2311 | -2.2193 | -56.7893 | -149.0778 | 12.1908 | 123.1995 | 29.8861 | -167.6338 |  | 0.97437 | 1.2129 | 1.1301 | 0.90939 | 1.215 | 1.1593 | -9.3353 | -118.6558 | 121.6577 | -8.7048 | -120.6596 | 123.3546

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.46677 | 0.21921 | 0.298 | 0.46618 | 0.21953 | 0.29841 | 5.3898 | 2.5312 | 3.441 | 5.3829 | 2.5349 | 3.4458 | 4.5755 | -3.0219 | 2.5785 | -4.3826 | 3.0752 | -2.6019 | 2.3765 | 0.15303 | -2.9912 | -2.1807 | -0.17152 | 3.0309 | -35.1885 | 62.3881 | 172.8047 | 144.8412 | -117.4673 | -7.2894 |  | 0.9566 | 1.1954 | 1.1477 | 0.90939 | 1.215 | 1.1593 | -7.7419 | -120.5108 | 123.5674 | -8.7048 | -120.6596 | 123.3546
Line_1 | 0.80933 | 0.19276 | 0.14482 | 0.8101 | 0.19217 | 0.14414 | 9.3454 | 2.2258 | 1.6723 | 9.3542 | 2.219 | 1.6644 | -6.0751 | 2.7071 | -1.8439 | 6.8957 | -2.666 | 1.7505 | -4.3211 | -0.51901 | 0.79408 | 4.9812 | 0.40262 | -0.81165 | 135.4747 | -111.8966 | -31.9581 | -44.5475 | 67.9283 | 148.2305 |  | 0.79773 | 1.2384 | 1.2005 | 0.90939 | 1.215 | 1.1593 | -9.1016 | -122.7495 | 124.7429 | -8.7048 | -120.6596 | 123.3546
Line_2 | 0.35894 | 0.033398 | 0.17786 | 0.35833 | 0.033498 | 0.17757 | 4.1447 | 0.38565 | 2.0537 | 4.1376 | 0.3868 | 2.0504 | 2.7307 | 0.40337 | -0.77347 | -2.5131 | -0.40923 | 0.85139 | 2.9753 | 0.23686 | 2.1882 | -2.8005 | -0.2311 | -2.2193 | -56.7893 | -149.0778 | 12.1908 | 123.1995 | 29.8861 | -167.6338 |  | 0.97437 | 1.2129 | 1.1301 | 0.90939 | 1.215 | 1.1593 | -9.3353 | -118.6558 | 121.6577 | -8.7048 | -120.6596 | 123.3546

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.4171 | 0.64071 | 0.533 | 1.4159 | 0.64195 | 0.53424 | 16.3632 | 7.3983 | 6.1546 | 16.349 | 7.4126 | 6.1689 | 8.0185 | -5.11 | 6.0895 | -5.3402 | 5.3183 | -6.0281 | 5.7368 | 6.0178 | 1.189 | -3.7791 | -6.1984 | -1.3465 | -57.8044 | 108.3584 | 114.0539 | 122.2028 | -71.6308 | -65.9463 |  | 0.60254 | 1.0671 | 1.0081 | 0.40015 | 1.1018 | 1.0013 | -22.223 | -121.3053 | 125.1023 | -22.5116 | -121.0011 | 126.6453
Line_1 | 1.9283 | 0.56517 | 0.49233 | 1.9301 | 0.56327 | 0.49042 | 22.2664 | 6.526 | 5.6849 | 22.2865 | 6.5041 | 5.6629 | -4.3062e-11 | 5.8892 | -5.0432 | 7.4367 | -6.0433 | 4.7861 | 7.8915e-12 | -4.9371 | -3.9817 | 4.9221 | 3.8517 | 3.0401 | 124.0131 | -88.4625 | -85.7578 | -56.0105 | 91.5105 | 94.2216 |  | 0 | 1.1776 | 1.1303 | 0.40015 | 1.1018 | 1.0013 | 0 | -128.4369 | 132.5338 | -22.5116 | -121.0011 | 126.6453
Line_2 | 0.51789 | 0.1939 | 0.18229 | 0.51678 | 0.19305 | 0.18166 | 5.9801 | 2.2389 | 2.1049 | 5.9673 | 2.2292 | 2.0976 | 3.1557 | -0.35828 | -0.94088 | -2.0965 | 0.72499 | 1.242 | 1.6952 | -2.3983 | 1.5831 | -1.143 | 2.3467 | -1.6936 | -51.1185 | -14.0501 | 0.10157 | 128.8898 | 166.1667 | -179.61 |  | 0.59902 | 1.0831 | 0.8749 | 0.40015 | 1.1018 | 1.0013 | -22.875 | -112.5467 | 120.8259 | -22.5116 | -121.0011 | 126.6453

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.4171 | 0.64071 | 0.533 | 1.4159 | 0.64195 | 0.53424 | 16.3632 | 7.3983 | 6.1546 | 16.349 | 7.4126 | 6.1689 | 8.0185 | -5.11 | 6.0895 | -5.3402 | 5.3183 | -6.0281 | 5.7368 | 6.0178 | 1.189 | -3.7791 | -6.1984 | -1.3465 | -57.8044 | 108.3584 | 114.0539 | 122.2028 | -71.6308 | -65.9463 |  | 0.60254 | 1.0671 | 1.0081 | 0.40015 | 1.1018 | 1.0013 | -22.223 | -121.3053 | 125.1023 | -22.5116 | -121.0011 | 126.6453
Line_1 | 1.9283 | 0.56517 | 0.49233 | 1.9301 | 0.56327 | 0.49042 | 22.2664 | 6.526 | 5.6849 | 22.2865 | 6.5041 | 5.6629 | -4.3062e-11 | 5.8892 | -5.0432 | 7.4367 | -6.0433 | 4.7861 | 7.8915e-12 | -4.9371 | -3.9817 | 4.9221 | 3.8517 | 3.0401 | 124.0131 | -88.4625 | -85.7578 | -56.0105 | 91.5105 | 94.2216 |  | 0 | 1.1776 | 1.1303 | 0.40015 | 1.1018 | 1.0013 | 0 | -128.4369 | 132.5338 | -22.5116 | -121.0011 | 126.6453
Line_2 | 0.51789 | 0.1939 | 0.18229 | 0.51678 | 0.19305 | 0.18166 | 5.9801 | 2.2389 | 2.1049 | 5.9673 | 2.2292 | 2.0976 | 3.1557 | -0.35828 | -0.94088 | -2.0965 | 0.72499 | 1.242 | 1.6952 | -2.3983 | 1.5831 | -1.143 | 2.3467 | -1.6936 | -51.1185 | -14.0501 | 0.10157 | 128.8898 | 166.1667 | -179.61 |  | 0.59902 | 1.0831 | 0.8749 | 0.40015 | 1.1018 | 1.0013 | -22.875 | -112.5467 | 120.8259 | -22.5116 | -121.0011 | 126.6453

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.5147 | 0.23271 | 0.19359 | 0.51425 | 0.23316 | 0.19404 | 5.9432 | 2.6871 | 2.2354 | 5.9381 | 2.6923 | 2.2406 | 4.2019 | -1.2694 | 2.2087 | -3.8461 | 1.2977 | -2.2039 | 3.0388 | 2.4464 | -0.24311 | -2.7782 | -2.4736 | 0.22326 | -43.7352 | 122.4276 | 128.1231 | 136.272 | -57.5616 | -51.8771 |  | 0.87252 | 1.0257 | 0.99405 | 0.79901 | 1.0375 | 0.98867 | -7.8608 | -120.1489 | 121.8419 | -7.8864 | -119.8789 | 122.3384
Line_1 | 0.70038 | 0.20527 | 0.17882 | 0.70101 | 0.20458 | 0.17812 | 8.0873 | 2.3703 | 2.0648 | 8.0946 | 2.3623 | 2.0568 | -4.3747 | 1.7014 | -2.0118 | 5.3585 | -1.7192 | 1.9727 | -2.968 | -1.8947 | -0.61767 | 3.6218 | 1.7469 | 0.49358 | 138.0823 | -74.3933 | -71.6886 | -41.9413 | 105.5796 | 108.2908 |  | 0.65368 | 1.0743 | 1.0192 | 0.79901 | 1.0375 | 0.98867 | -7.7627 | -122.4709 | 125.3788 | -7.8864 | -119.8789 | 122.3384
Line_2 | 0.1881 | 0.070424 | 0.06621 | 0.1877 | 0.070119 | 0.065978 | 2.172 | 0.81319 | 0.76452 | 2.1674 | 0.80966 | 0.76185 | 1.6546 | -0.37293 | -0.19425 | -1.5123 | 0.42147 | 0.23125 | 0.91816 | -0.7365 | 0.70365 | -0.84365 | 0.72665 | -0.71684 | -37.0493 | 0.019072 | 14.1708 | 142.959 | -179.7641 | -165.5408 |  | 0.87122 | 1.0152 | 0.9548 | 0.79901 | 1.0375 | 0.98867 | -8.0232 | -116.8365 | 119.6033 | -7.8864 | -119.8789 | 122.3384

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.5147 | 0.23271 | 0.19359 | 0.51425 | 0.23316 | 0.19404 | 5.9432 | 2.6871 | 2.2354 | 5.9381 | 2.6923 | 2.2406 | 4.2019 | -1.2694 | 2.2087 | -3.8461 | 1.2977 | -2.2039 | 3.0388 | 2.4464 | -0.24311 | -2.7782 | -2.4736 | 0.22326 | -43.7352 | 122.4276 | 128.1231 | 136.272 | -57.5616 | -51.8771 |  | 0.87252 | 1.0257 | 0.99405 | 0.79901 | 1.0375 | 0.98867 | -7.8608 | -120.1489 | 121.8419 | -7.8864 | -119.8789 | 122.3384
Line_1 | 0.70038 | 0.20527 | 0.17882 | 0.70101 | 0.20458 | 0.17812 | 8.0873 | 2.3703 | 2.0648 | 8.0946 | 2.3623 | 2.0568 | -4.3747 | 1.7014 | -2.0118 | 5.3585 | -1.7192 | 1.9727 | -2.968 | -1.8947 | -0.61767 | 3.6218 | 1.7469 | 0.49358 | 138.0823 | -74.3933 | -71.6886 | -41.9413 | 105.5796 | 108.2908 |  | 0.65368 | 1.0743 | 1.0192 | 0.79901 | 1.0375 | 0.98867 | -7.7627 | -122.4709 | 125.3788 | -7.8864 | -119.8789 | 122.3384
Line_2 | 0.1881 | 0.070424 | 0.06621 | 0.1877 | 0.070119 | 0.065978 | 2.172 | 0.81319 | 0.76452 | 2.1674 | 0.80966 | 0.76185 | 1.6546 | -0.37293 | -0.19425 | -1.5123 | 0.42147 | 0.23125 | 0.91816 | -0.7365 | 0.70365 | -0.84365 | 0.72665 | -0.71684 | -37.0493 | 0.019072 | 14.1708 | 142.959 | -179.7641 | -165.5408 |  | 0.87122 | 1.0152 | 0.9548 | 0.79901 | 1.0375 | 0.98867 | -8.0232 | -116.8365 | 119.6033 | -7.8864 | -119.8789 | 122.3384

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36636 | 2.9479 | 2.8295 | 0.36769 | 2.9478 | 2.8293 | 4.2304 | 34.0398 | 32.6723 | 4.2457 | 34.0387 | 32.6695 | -1.5539 | 15.725 | 4.9285 | 1.623 | -9.868 | -1.8834 | 5.2142 | 7.098 | 15.6446 | -5.3406 | -2.5786 | -10.0634 | -102.8399 | -166.9054 | 25.8537 | 77.2773 | 13.1242 | -154.1768 |  | 1.2861 | 0.50684 | 0.50203 | 1.3147 | 0.29964 | 0.31339 | 3.755 | -142.6118 | 98.3677 | 4.1808 | -152.2315 | 105.2227
Line_1 | 0.35077 | 3.7757 | 3.4234 | 0.34911 | 3.7757 | 3.4243 | 4.0504 | 43.5982 | 39.5304 | 4.0311 | 43.5984 | 39.5401 | 2.6413 | 9.0295e-11 | 1.0323e-10 | -2.6353 | 12.1988 | 3.6387 | -5.1173 | -7.4342e-11 | -1.0058e-11 | 4.598 | 4.6748 | 11.845 | 64.5385 | 6.8309 | -147.731 | -115.6375 | -173.1992 | 32.2991 |  | 1.4218 | 0 | 0 | 1.3147 | 0.29964 | 0.31339 | 1.8395 | 0 | 0 | 4.1808 | -152.2315 | 105.2227
Line_2 | 0.08392 | 0.9069 | 0.692 | 0.082702 | 0.906 | 0.69114 | 0.96902 | 10.472 | 7.9905 | 0.95496 | 10.4616 | 7.9806 | -0.91975 | 3.7056 | 2.1436 | 1.0123 | -2.3308 | -1.7553 | -0.77139 | 2.1352 | 2.8529 | 0.74259 | -2.0962 | -1.7816 | 147.3577 | 165.7284 | 59.8943 | -32.0815 | -14.1987 | -120.2039 |  | 1.2388 | 0.4084 | 0.44658 | 1.3147 | 0.29964 | 0.31339 | 7.3441 | -164.3215 | 112.9742 | 4.1808 | -152.2315 | 105.2227

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36636 | 2.9479 | 2.8295 | 0.36769 | 2.9478 | 2.8293 | 4.2304 | 34.0398 | 32.6723 | 4.2457 | 34.0387 | 32.6695 | -1.5539 | 15.725 | 4.9285 | 1.623 | -9.868 | -1.8834 | 5.2142 | 7.098 | 15.6446 | -5.3406 | -2.5786 | -10.0634 | -102.8399 | -166.9054 | 25.8537 | 77.2773 | 13.1242 | -154.1768 |  | 1.2861 | 0.50684 | 0.50203 | 1.3147 | 0.29964 | 0.31339 | 3.755 | -142.6118 | 98.3677 | 4.1808 | -152.2315 | 105.2227
Line_1 | 0.35077 | 3.7757 | 3.4234 | 0.34911 | 3.7757 | 3.4243 | 4.0504 | 43.5982 | 39.5304 | 4.0311 | 43.5984 | 39.5401 | 2.6413 | 9.0295e-11 | 1.0323e-10 | -2.6353 | 12.1988 | 3.6387 | -5.1173 | -7.4342e-11 | -1.0058e-11 | 4.598 | 4.6748 | 11.845 | 64.5385 | 6.8309 | -147.731 | -115.6375 | -173.1992 | 32.2991 |  | 1.4218 | 0 | 0 | 1.3147 | 0.29964 | 0.31339 | 1.8395 | 0 | 0 | 4.1808 | -152.2315 | 105.2227
Line_2 | 0.08392 | 0.9069 | 0.692 | 0.082702 | 0.906 | 0.69114 | 0.96902 | 10.472 | 7.9905 | 0.95496 | 10.4616 | 7.9806 | -0.91975 | 3.7056 | 2.1436 | 1.0123 | -2.3308 | -1.7553 | -0.77139 | 2.1352 | 2.8529 | 0.74259 | -2.0962 | -1.7816 | 147.3577 | 165.7284 | 59.8943 | -32.0815 | -14.1987 | -120.2039 |  | 1.2388 | 0.4084 | 0.44658 | 1.3147 | 0.29964 | 0.31339 | 7.3441 | -164.3215 | 112.9742 | 4.1808 | -152.2315 | 105.2227

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.012024 | 0.74085 | 0.63527 | 0.011916 | 0.74093 | 0.63506 | 0.13884 | 8.5546 | 7.3355 | 0.1376 | 8.5555 | 7.3331 | 0.12379 | 7.9389 | 3.7753 | -0.12959 | -7.5402 | -3.6399 | -0.10964 | 2.0813 | 6.2095 | 0.10405 | -1.837 | -5.8796 | 43.8609 | -139.803 | 52.8482 | -138.9274 | 40.2423 | -127.2017 |  | 1.1911 | 0.95939 | 0.99068 | 1.2078 | 0.9071 | 0.943 | 2.3299 | -125.1127 | 111.549 | 2.3116 | -126.0658 | 111.0378
Line_1 | 0.067013 | 1.0202 | 0.91318 | 0.066495 | 1.0202 | 0.91364 | 0.7738 | 11.7807 | 10.5445 | 0.76782 | 11.7804 | 10.5498 | 0.43659 | -8.3103 | -5.8424 | -0.43139 | 9.3308 | 6.1363 | -0.86974 | -5.0027 | -6.7879 | 0.82097 | 5.2082 | 7.8306 | 65.0804 | 24.8081 | -120.918 | -115.4087 | -155.2351 | 59.1208 |  | 1.2576 | 0.82337 | 0.84934 | 1.2078 | 0.9071 | 0.943 | 1.736 | -124.1444 | 108.3632 | 2.3116 | -126.0658 | 111.0378
Line_2 | 0.077357 | 0.36487 | 0.29129 | 0.077568 | 0.36445 | 0.29097 | 0.89324 | 4.2131 | 3.3635 | 0.89567 | 4.2083 | 3.3598 | -0.55967 | 2.0157 | 2.5636 | 0.56098 | -1.7906 | -2.4964 | 0.88757 | 3.4096 | 2.1289 | -0.92502 | -3.3713 | -1.951 | -119.3142 | 171.8483 | 73.1215 | 61.0766 | -8.0911 | -106.9714 |  | 1.1747 | 0.94014 | 0.99071 | 1.2078 | 0.9071 | 0.943 | 2.9197 | -128.7421 | 112.8288 | 2.3116 | -126.0658 | 111.0378

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.012024 | 0.74085 | 0.63527 | 0.011916 | 0.74093 | 0.63506 | 0.13884 | 8.5546 | 7.3355 | 0.1376 | 8.5555 | 7.3331 | 0.12379 | 7.9389 | 3.7753 | -0.12959 | -7.5402 | -3.6399 | -0.10964 | 2.0813 | 6.2095 | 0.10405 | -1.837 | -5.8796 | 43.8609 | -139.803 | 52.8482 | -138.9274 | 40.2423 | -127.2017 |  | 1.1911 | 0.95939 | 0.99068 | 1.2078 | 0.9071 | 0.943 | 2.3299 | -125.1127 | 111.549 | 2.3116 | -126.0658 | 111.0378
Line_1 | 0.067013 | 1.0202 | 0.91318 | 0.066495 | 1.0202 | 0.91364 | 0.7738 | 11.7807 | 10.5445 | 0.76782 | 11.7804 | 10.5498 | 0.43659 | -8.3103 | -5.8424 | -0.43139 | 9.3308 | 6.1363 | -0.86974 | -5.0027 | -6.7879 | 0.82097 | 5.2082 | 7.8306 | 65.0804 | 24.8081 | -120.918 | -115.4087 | -155.2351 | 59.1208 |  | 1.2576 | 0.82337 | 0.84934 | 1.2078 | 0.9071 | 0.943 | 1.736 | -124.1444 | 108.3632 | 2.3116 | -126.0658 | 111.0378
Line_2 | 0.077357 | 0.36487 | 0.29129 | 0.077568 | 0.36445 | 0.29097 | 0.89324 | 4.2131 | 3.3635 | 0.89567 | 4.2083 | 3.3598 | -0.55967 | 2.0157 | 2.5636 | 0.56098 | -1.7906 | -2.4964 | 0.88757 | 3.4096 | 2.1289 | -0.92502 | -3.3713 | -1.951 | -119.3142 | 171.8483 | 73.1215 | 61.0766 | -8.0911 | -106.9714 |  | 1.1747 | 0.94014 | 0.99071 | 1.2078 | 0.9071 | 0.943 | 2.9197 | -128.7421 | 112.8288 | 2.3116 | -126.0658 | 111.0378

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44166 | 2.3005 | 2.3209 | 0.44262 | 2.3005 | 2.3206 | 5.0999 | 26.5642 | 26.7992 | 5.1109 | 26.5643 | 26.796 | 0.054817 | 16.675 | 8.201 | 0.077836 | -10.2571 | -3.7268 | 5.4065 | 2.6158 | 12.1969 | -5.5577 | -0.23625 | -7.9928 | -85.8896 | -155.3346 | 39.8023 | 94.1552 | 24.6907 | -140.2218 |  | 1.0602 | 0.6354 | 0.54844 | 1.0875 | 0.38623 | 0.32912 | 3.5294 | -146.4193 | 95.8863 | 4.9576 | -153.9899 | 104.78
Line_1 | 0.41957 | 2.9264 | 2.7066 | 0.41808 | 2.9261 | 2.7074 | 4.8448 | 33.7912 | 31.2528 | 4.8275 | 33.788 | 31.2629 | 1.2843 | -1.0308e-10 | -4.2184e-11 | -1.2641 | 12.9741 | 4.8995 | -5.8199 | -6.6234e-11 | -1.0629e-10 | 5.0956 | 1.4042 | 9.0477 | 81.0937 | 19.8632 | -136.8115 | -98.9748 | -160.1671 | 43.2163 |  | 1.2302 | 0 | 0 | 1.0875 | 0.38623 | 0.32912 | 3.5378 | 0 | 0 | 4.9576 | -153.9899 | 104.78
Line_2 | 0.1021 | 0.66361 | 0.41547 | 0.10138 | 0.66312 | 0.41505 | 1.1789 | 7.6627 | 4.7975 | 1.1706 | 7.657 | 4.7926 | -1.0408 | 3.979 | 1.323 | 1.1863 | -2.7169 | -1.1727 | -0.48551 | 1.0084 | 1.7337 | 0.46209 | -1.168 | -1.0549 | 163.3548 | -177.3187 | 62.9188 | -16.3251 | 2.748 | -117.1931 |  | 0.97416 | 0.53568 | 0.45458 | 1.0875 | 0.38623 | 0.32912 | 8.3631 | -163.0969 | 115.5714 | 4.9576 | -153.9899 | 104.78

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44166 | 2.3005 | 2.3209 | 0.44262 | 2.3005 | 2.3206 | 5.0999 | 26.5642 | 26.7992 | 5.1109 | 26.5643 | 26.796 | 0.054817 | 16.675 | 8.201 | 0.077836 | -10.2571 | -3.7268 | 5.4065 | 2.6158 | 12.1969 | -5.5577 | -0.23625 | -7.9928 | -85.8896 | -155.3346 | 39.8023 | 94.1552 | 24.6907 | -140.2218 |  | 1.0602 | 0.6354 | 0.54844 | 1.0875 | 0.38623 | 0.32912 | 3.5294 | -146.4193 | 95.8863 | 4.9576 | -153.9899 | 104.78
Line_1 | 0.41957 | 2.9264 | 2.7066 | 0.41808 | 2.9261 | 2.7074 | 4.8448 | 33.7912 | 31.2528 | 4.8275 | 33.788 | 31.2629 | 1.2843 | -1.0308e-10 | -4.2184e-11 | -1.2641 | 12.9741 | 4.8995 | -5.8199 | -6.6234e-11 | -1.0629e-10 | 5.0956 | 1.4042 | 9.0477 | 81.0937 | 19.8632 | -136.8115 | -98.9748 | -160.1671 | 43.2163 |  | 1.2302 | 0 | 0 | 1.0875 | 0.38623 | 0.32912 | 3.5378 | 0 | 0 | 4.9576 | -153.9899 | 104.78
Line_2 | 0.1021 | 0.66361 | 0.41547 | 0.10138 | 0.66312 | 0.41505 | 1.1789 | 7.6627 | 4.7975 | 1.1706 | 7.657 | 4.7926 | -1.0408 | 3.979 | 1.323 | 1.1863 | -2.7169 | -1.1727 | -0.48551 | 1.0084 | 1.7337 | 0.46209 | -1.168 | -1.0549 | 163.3548 | -177.3187 | 62.9188 | -16.3251 | 2.748 | -117.1931 |  | 0.97416 | 0.53568 | 0.45458 | 1.0875 | 0.38623 | 0.32912 | 8.3631 | -163.0969 | 115.5714 | 4.9576 | -153.9899 | 104.78

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.18395 | 0.6933 | 0.68844 | 0.18435 | 0.69328 | 0.6883 | 2.1241 | 8.0056 | 7.9494 | 2.1287 | 8.0053 | 7.9478 | 0.74561 | 6.605 | 3.903 | -0.72822 | -5.981 | -3.5292 | 2.03 | 2.309 | 5.843 | -2.0565 | -2.106 | -5.4335 | -68.2547 | -145.8951 | 55.7096 | 111.7788 | 34.1393 | -124.3232 |  | 1.0181 | 0.87401 | 0.88393 | 1.0249 | 0.79209 | 0.8152 | 1.5771 | -126.6261 | 111.9674 | 2.2796 | -126.4624 | 112.6715
Line_1 | 0.17296 | 0.89942 | 0.80405 | 0.17233 | 0.89935 | 0.80445 | 1.9971 | 10.3857 | 9.2844 | 1.9899 | 10.3849 | 9.289 | -0.17662 | -6.0578 | -4.2791 | 0.16996 | 7.4513 | 4.687 | -2.1568 | -3.4224 | -4.967 | 2.0323 | 3.4845 | 5.9475 | 97.1162 | 28.5156 | -119.124 | -82.94 | -151.5253 | 60.9119 |  | 1.0835 | 0.66993 | 0.70614 | 1.0249 | 0.79209 | 0.8152 | 2.4346 | -122.0197 | 110.1306 | 2.2796 | -126.4624 | 112.6715
Line_2 | 0.047498 | 0.22058 | 0.13482 | 0.047218 | 0.22035 | 0.13458 | 0.54846 | 2.5471 | 1.5568 | 0.54523 | 2.5444 | 1.554 | -0.53258 | 1.6352 | 1.1935 | 0.55826 | -1.4703 | -1.1578 | -0.031327 | 1.363 | 0.59895 | 0.024195 | -1.3785 | -0.51406 | 179.4951 | -169.6948 | 88.851 | -0.20212 | 10.3826 | -91.2696 |  | 0.97272 | 0.83577 | 0.85775 | 1.0249 | 0.79209 | 0.8152 | 2.8614 | -129.8809 | 115.5005 | 2.2796 | -126.4624 | 112.6715

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.18395 | 0.6933 | 0.68844 | 0.18435 | 0.69328 | 0.6883 | 2.1241 | 8.0056 | 7.9494 | 2.1287 | 8.0053 | 7.9478 | 0.74561 | 6.605 | 3.903 | -0.72822 | -5.981 | -3.5292 | 2.03 | 2.309 | 5.843 | -2.0565 | -2.106 | -5.4335 | -68.2547 | -145.8951 | 55.7096 | 111.7788 | 34.1393 | -124.3232 |  | 1.0181 | 0.87401 | 0.88393 | 1.0249 | 0.79209 | 0.8152 | 1.5771 | -126.6261 | 111.9674 | 2.2796 | -126.4624 | 112.6715
Line_1 | 0.17296 | 0.89942 | 0.80405 | 0.17233 | 0.89935 | 0.80445 | 1.9971 | 10.3857 | 9.2844 | 1.9899 | 10.3849 | 9.289 | -0.17662 | -6.0578 | -4.2791 | 0.16996 | 7.4513 | 4.687 | -2.1568 | -3.4224 | -4.967 | 2.0323 | 3.4845 | 5.9475 | 97.1162 | 28.5156 | -119.124 | -82.94 | -151.5253 | 60.9119 |  | 1.0835 | 0.66993 | 0.70614 | 1.0249 | 0.79209 | 0.8152 | 2.4346 | -122.0197 | 110.1306 | 2.2796 | -126.4624 | 112.6715
Line_2 | 0.047498 | 0.22058 | 0.13482 | 0.047218 | 0.22035 | 0.13458 | 0.54846 | 2.5471 | 1.5568 | 0.54523 | 2.5444 | 1.554 | -0.53258 | 1.6352 | 1.1935 | 0.55826 | -1.4703 | -1.1578 | -0.031327 | 1.363 | 0.59895 | 0.024195 | -1.3785 | -0.51406 | 179.4951 | -169.6948 | 88.851 | -0.20212 | 10.3826 | -91.2696 |  | 0.97272 | 0.83577 | 0.85775 | 1.0249 | 0.79209 | 0.8152 | 2.8614 | -129.8809 | 115.5005 | 2.2796 | -126.4624 | 112.6715