## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3036 | 3.3036 | 0 | 0 | 114.4404 | 114.4404 | 37.7713 | -20.7457 | 43.3355 | -24.018 | -70.8485 | 109.1515 | 0.50232 | 0.27733 | -21.9239 | -21.6675
Line_1 | 4.0718 | 4.0718 | 7.8074 | 0 | 141.0522 | 141.0522 | -1e-07 | 25.8644 | -1e-07 | 29.3462 | 109.7241 | -70.2759 | 0 | 0.27733 | 0 | -21.6675
Line_2 | 0.76909 | 0.76909 | 0 | 0 | 26.6421 | 26.6421 | 6.0414 | -5.1187 | 6.3751 | -5.3281 | -67.816 | 112.184 | 0.32967 | 0.27733 | -21.2767 | -21.6675

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3036 | 3.3036 | 0 | 0 | 114.4404 | 114.4404 | 37.7713 | -20.7457 | 43.3355 | -24.018 | -70.8485 | 109.1515 | 0.50232 | 0.27733 | -21.9239 | -21.6675
Line_1 | 4.0718 | 4.0718 | 7.8074 | 0 | 141.0522 | 141.0522 | -1e-07 | 25.8644 | -1e-07 | 29.3462 | 109.7241 | -70.2759 | 0 | 0.27733 | 0 | -21.6675
Line_2 | 0.76909 | 0.76909 | 0 | 0 | 26.6421 | 26.6421 | 6.0414 | -5.1187 | 6.3751 | -5.3281 | -67.816 | 112.184 | 0.32967 | 0.27733 | -21.2767 | -21.6675

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.77289 | 0.77289 | 0 | 0 | 26.7736 | 26.7736 | 20.4887 | -19.5569 | 16.8303 | -15.773 | -45.3926 | 134.6074 | 0.99034 | 0.93842 | -5.9915 | -6.5057
Line_1 | 1.057 | 1.057 | 2.0668 | 0 | 36.615 | 36.615 | -23.4304 | 25.1732 | -21.4091 | 23.3865 | 130.6015 | -49.3985 | 0.86682 | 0.93842 | -6.9796 | -6.5057
Line_2 | 0.29104 | 0.29104 | 0 | 0 | 10.0818 | 10.0818 | 5.7485 | -5.6164 | 7.7635 | -7.6135 | -60.0901 | 119.9099 | 0.95817 | 0.93842 | -6.6085 | -6.5057

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.77289 | 0.77289 | 0 | 0 | 26.7736 | 26.7736 | 20.4887 | -19.5569 | 16.8303 | -15.773 | -45.3926 | 134.6074 | 0.99034 | 0.93842 | -5.9915 | -6.5057
Line_1 | 1.057 | 1.057 | 2.0668 | 0 | 36.615 | 36.615 | -23.4304 | 25.1732 | -21.4091 | 23.3865 | 130.6015 | -49.3985 | 0.86682 | 0.93842 | -6.9796 | -6.5057
Line_2 | 0.29104 | 0.29104 | 0 | 0 | 10.0818 | 10.0818 | 5.7485 | -5.6164 | 7.7635 | -7.6135 | -60.0901 | 119.9099 | 0.95817 | 0.93842 | -6.6085 | -6.5057

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34465 | 2.8163 | 2.9394 | 0.34465 | 2.8163 | 2.9394 | 3.9797 | 32.5201 | 33.9408 | 3.9797 | 32.5201 | 33.9408 | -2.8467 | 27.5894 | -9.8021 | 2.9085 | -23.4649 | 14.2948 | -3.6108 | 3.3833 | 16.3211 | 3.6809 | 1.2964 | -11.2236 | 130.3426 | -157.3314 | 16.2542 | -49.6574 | 22.6686 | -163.7458 | 1.1554 | 0.85474 | 0.56093 | 1.1788 | 0.72265 | 0.53548 | 2.0909 | -150.3401 | 137.2424 | 2.0284 | -160.4937 | 158.117
Line_1 | 0.19448 | 3.4668 | 3.5514 | 0.19448 | 3.4668 | 3.5514 | 2.2456 | 40.0309 | 41.0075 | 2.2456 | 40.0309 | 41.0075 | 1.8069 | -22.6769 | 23.5803 | -1.7872 | 28.9265 | -17.0221 | 1.975 | 7.4181 | -6.4306 | -1.9527 | -0.32717 | 13.8717 | -45.5053 | 20.1544 | -162.7055 | 134.4947 | -159.8456 | 17.2945 | 1.192 | 0.59602 | 0.59602 | 1.1788 | 0.72265 | 0.53548 | 2.0403 | -177.9597 | -177.9597 | 2.0284 | -160.4937 | 158.117
Line_2 | 0.15134 | 0.66475 | 0.6148 | 0.15134 | 0.66475 | 0.6148 | 1.7476 | 7.6758 | 7.0991 | 1.7476 | 7.6758 | 7.0991 | 1.1332 | 5.6914 | -2.5307 | -1.1212 | -5.4616 | 2.7272 | 1.7417 | 1.2299 | 2.8712 | -1.7282 | -0.96922 | -2.6482 | -54.9959 | -170.5566 | 22.2743 | 125.0041 | 9.4434 | -157.7257 | 1.189 | 0.75859 | 0.53912 | 1.1788 | 0.72265 | 0.53548 | 1.9557 | -158.3623 | 153.6676 | 2.0284 | -160.4937 | 158.117

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34465 | 2.8163 | 2.9394 | 0.34465 | 2.8163 | 2.9394 | 3.9797 | 32.5201 | 33.9408 | 3.9797 | 32.5201 | 33.9408 | -2.8467 | 27.5894 | -9.8021 | 2.9085 | -23.4649 | 14.2948 | -3.6108 | 3.3833 | 16.3211 | 3.6809 | 1.2964 | -11.2236 | 130.3426 | -157.3314 | 16.2542 | -49.6574 | 22.6686 | -163.7458 | 1.1554 | 0.85474 | 0.56093 | 1.1788 | 0.72265 | 0.53548 | 2.0909 | -150.3401 | 137.2424 | 2.0284 | -160.4937 | 158.117
Line_1 | 0.19448 | 3.4668 | 3.5514 | 0.19448 | 3.4668 | 3.5514 | 2.2456 | 40.0309 | 41.0075 | 2.2456 | 40.0309 | 41.0075 | 1.8069 | -22.6769 | 23.5803 | -1.7872 | 28.9265 | -17.0221 | 1.975 | 7.4181 | -6.4306 | -1.9527 | -0.32717 | 13.8717 | -45.5053 | 20.1544 | -162.7055 | 134.4947 | -159.8456 | 17.2945 | 1.192 | 0.59602 | 0.59602 | 1.1788 | 0.72265 | 0.53548 | 2.0403 | -177.9597 | -177.9597 | 2.0284 | -160.4937 | 158.117
Line_2 | 0.15134 | 0.66475 | 0.6148 | 0.15134 | 0.66475 | 0.6148 | 1.7476 | 7.6758 | 7.0991 | 1.7476 | 7.6758 | 7.0991 | 1.1332 | 5.6914 | -2.5307 | -1.1212 | -5.4616 | 2.7272 | 1.7417 | 1.2299 | 2.8712 | -1.7282 | -0.96922 | -2.6482 | -54.9959 | -170.5566 | 22.2743 | 125.0041 | 9.4434 | -157.7257 | 1.189 | 0.75859 | 0.53912 | 1.1788 | 0.72265 | 0.53548 | 1.9557 | -158.3623 | 153.6676 | 2.0284 | -160.4937 | 158.117

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26375 | 1.2082 | 1.1737 | 0.26375 | 1.2082 | 1.1737 | 3.0455 | 13.9508 | 13.5526 | 3.0455 | 13.9508 | 13.5526 | -1.7236 | 14.6366 | 0.36638 | 1.7598 | -13.8776 | 0.34995 | -3.0377 | 0.70931 | 11.719 | 3.0787 | 0.15191 | -10.9062 | 120.8148 | -135.4144 | 31.9789 | -59.1852 | 44.5856 | -148.0211 | 1.1468 | 1.0504 | 0.86513 | 1.1644 | 0.99481 | 0.80515 | 1.244 | -132.6399 | 120.1882 | 1.0629 | -136.0415 | 123.8167
Line_1 | 0.14172 | 1.5139 | 1.518 | 0.14172 | 1.5139 | 1.518 | 1.6364 | 17.4815 | 17.5279 | 1.6364 | 17.4815 | 17.5279 | 1.1337 | -16.1122 | 1.4292 | -1.1232 | 17.3041 | -0.23098 | 1.5511 | -0.38203 | -12.7512 | -1.5392 | 1.7343 | 14.1107 | -52.8182 | 38.235 | -147.1211 | 127.1818 | -141.765 | 32.8789 | 1.174 | 0.92193 | 0.73203 | 1.1644 | 0.99481 | 0.80515 | 1.0196 | -140.4067 | 129.274 | 1.0629 | -136.0415 | 123.8167
Line_2 | 0.1239 | 0.3405 | 0.34491 | 0.1239 | 0.3405 | 0.34491 | 1.4307 | 3.9318 | 3.9827 | 1.4307 | 3.9318 | 3.9827 | 0.64456 | 3.4868 | 0.18083 | -0.63657 | -3.4265 | -0.11897 | 1.5486 | 1.9546 | 3.2746 | -1.5395 | -1.8862 | -3.2044 | -66.4724 | -164.8737 | 35.9428 | 113.5276 | 15.1263 | -144.0572 | 1.1724 | 1.0167 | 0.82347 | 1.1644 | 0.99481 | 0.80515 | 0.92914 | -135.5993 | 122.7821 | 1.0629 | -136.0415 | 123.8167

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26375 | 1.2082 | 1.1737 | 0.26375 | 1.2082 | 1.1737 | 3.0455 | 13.9508 | 13.5526 | 3.0455 | 13.9508 | 13.5526 | -1.7236 | 14.6366 | 0.36638 | 1.7598 | -13.8776 | 0.34995 | -3.0377 | 0.70931 | 11.719 | 3.0787 | 0.15191 | -10.9062 | 120.8148 | -135.4144 | 31.9789 | -59.1852 | 44.5856 | -148.0211 | 1.1468 | 1.0504 | 0.86513 | 1.1644 | 0.99481 | 0.80515 | 1.244 | -132.6399 | 120.1882 | 1.0629 | -136.0415 | 123.8167
Line_1 | 0.14172 | 1.5139 | 1.518 | 0.14172 | 1.5139 | 1.518 | 1.6364 | 17.4815 | 17.5279 | 1.6364 | 17.4815 | 17.5279 | 1.1337 | -16.1122 | 1.4292 | -1.1232 | 17.3041 | -0.23098 | 1.5511 | -0.38203 | -12.7512 | -1.5392 | 1.7343 | 14.1107 | -52.8182 | 38.235 | -147.1211 | 127.1818 | -141.765 | 32.8789 | 1.174 | 0.92193 | 0.73203 | 1.1644 | 0.99481 | 0.80515 | 1.0196 | -140.4067 | 129.274 | 1.0629 | -136.0415 | 123.8167
Line_2 | 0.1239 | 0.3405 | 0.34491 | 0.1239 | 0.3405 | 0.34491 | 1.4307 | 3.9318 | 3.9827 | 1.4307 | 3.9318 | 3.9827 | 0.64456 | 3.4868 | 0.18083 | -0.63657 | -3.4265 | -0.11897 | 1.5486 | 1.9546 | 3.2746 | -1.5395 | -1.8862 | -3.2044 | -66.4724 | -164.8737 | 35.9428 | 113.5276 | 15.1263 | -144.0572 | 1.1724 | 1.0167 | 0.82347 | 1.1644 | 0.99481 | 0.80515 | 0.92914 | -135.5993 | 122.7821 | 1.0629 | -136.0415 | 123.8167

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5124 | 0.84192 | 0.74083 | 1.5101 | 0.84417 | 0.74299 | 17.4642 | 9.7217 | 8.5544 | 17.4374 | 9.7476 | 8.5793 | 5.0362 | -10.4664 | 10.762 | -3.8364 | 10.8561 | -10.5081 | 4.9265 | 8.1393 | 1.4457 | -3.5708 | -7.7501 | -1.1366 | -73.0345 | 90.1514 | 126.1805 | 106.9691 | -89.8091 | -53.8851 |  | 0.4034 | 1.3638 | 1.2694 | 0.30056 | 1.3684 | 1.232 | -28.6653 | -127.7193 | 133.8315 | -30.0839 | -125.3318 | 132.2883
Line_1 | 2.4039 | 0.61197 | 0.45849 | 2.4065 | 0.6095 | 0.45588 | 27.7583 | 7.0664 | 5.2942 | 27.7879 | 7.0378 | 5.2641 | 9.223e-11 | 8.564 | -6.146 | 6.3882 | -8.8139 | 5.633 | -8.2147e-11 | -4.5623 | -3.5636 | 5.3802 | 3.8811 | 3.2136 | 109.8249 | -101.4848 | -77.4438 | -70.1882 | 78.4341 | 102.5837 |  | 0 | 1.3732 | 1.3419 | 0.30056 | 1.3684 | 1.232 | 0 | -129.5304 | 132.6628 | -30.0839 | -125.3318 | 132.2883
Line_2 | 0.90342 | 0.27893 | 0.37405 | 0.90136 | 0.27687 | 0.37251 | 10.4318 | 3.2208 | 4.3191 | 10.408 | 3.197 | 4.3013 | 4.3137 | 2.518 | -4.2418 | -2.5519 | -2.0422 | 4.8751 | 2.925 | -3.6727 | 1.9895 | -1.8094 | 3.8689 | -2.077 | -65.4244 | -63.1839 | -24.8471 | 114.5781 | 116.8411 | 155.3641 |  | 0.49962 | 1.3825 | 1.0847 | 0.30056 | 1.3684 | 1.232 | -31.2842 | -118.7493 | 130.0253 | -30.0839 | -125.3318 | 132.2883

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5124 | 0.84192 | 0.74083 | 1.5101 | 0.84417 | 0.74299 | 17.4642 | 9.7217 | 8.5544 | 17.4374 | 9.7476 | 8.5793 | 5.0362 | -10.4664 | 10.762 | -3.8364 | 10.8561 | -10.5081 | 4.9265 | 8.1393 | 1.4457 | -3.5708 | -7.7501 | -1.1366 | -73.0345 | 90.1514 | 126.1805 | 106.9691 | -89.8091 | -53.8851 |  | 0.4034 | 1.3638 | 1.2694 | 0.30056 | 1.3684 | 1.232 | -28.6653 | -127.7193 | 133.8315 | -30.0839 | -125.3318 | 132.2883
Line_1 | 2.4039 | 0.61197 | 0.45849 | 2.4065 | 0.6095 | 0.45588 | 27.7583 | 7.0664 | 5.2942 | 27.7879 | 7.0378 | 5.2641 | 9.223e-11 | 8.564 | -6.146 | 6.3882 | -8.8139 | 5.633 | -8.2147e-11 | -4.5623 | -3.5636 | 5.3802 | 3.8811 | 3.2136 | 109.8249 | -101.4848 | -77.4438 | -70.1882 | 78.4341 | 102.5837 |  | 0 | 1.3732 | 1.3419 | 0.30056 | 1.3684 | 1.232 | 0 | -129.5304 | 132.6628 | -30.0839 | -125.3318 | 132.2883
Line_2 | 0.90342 | 0.27893 | 0.37405 | 0.90136 | 0.27687 | 0.37251 | 10.4318 | 3.2208 | 4.3191 | 10.408 | 3.197 | 4.3013 | 4.3137 | 2.518 | -4.2418 | -2.5519 | -2.0422 | 4.8751 | 2.925 | -3.6727 | 1.9895 | -1.8094 | 3.8689 | -2.077 | -65.4244 | -63.1839 | -24.8471 | 114.5781 | 116.8411 | 155.3641 |  | 0.49962 | 1.3825 | 1.0847 | 0.30056 | 1.3684 | 1.232 | -31.2842 | -118.7493 | 130.0253 | -30.0839 | -125.3318 | 132.2883

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.40481 | 0.21378 | 0.35622 | 0.40402 | 0.21433 | 0.35678 | 4.6744 | 2.4685 | 4.1132 | 4.6652 | 2.4749 | 4.1197 | 3.6967 | -2.8919 | 3.2918 | -3.605 | 2.9204 | -3.237 | 2.2124 | 0.99356 | -3.3749 | -2.1097 | -0.97749 | 3.45 | -40.4729 | 77.6114 | 171.6156 | 139.5568 | -102.2282 | -8.4804 |  | 0.92165 | 1.2388 | 1.1462 | 0.89535 | 1.2444 | 1.1484 | -9.5734 | -121.3494 | 125.9019 | -10.1063 | -120.7339 | 124.6951
Line_1 | 0.77844 | 0.19099 | 0.17182 | 0.77933 | 0.1903 | 0.17104 | 8.9886 | 2.2054 | 1.984 | 8.9989 | 2.1974 | 1.975 | -5.7135 | 2.6306 | -2.1254 | 6.4319 | -2.6167 | 2.0313 | -4.2837 | -0.89212 | 1.0093 | 4.8527 | 0.79339 | -1.0089 | 132.8781 | -103.6822 | -29.061 | -47.1396 | 76.1335 | 151.1083 |  | 0.79446 | 1.2595 | 1.186 | 0.89535 | 1.2444 | 1.1484 | -10.2611 | -122.4156 | 125.5381 | -10.1063 | -120.7339 | 124.6951
Line_2 | 0.38171 | 0.025257 | 0.20575 | 0.38099 | 0.024719 | 0.20533 | 4.4077 | 0.29164 | 2.3758 | 4.3993 | 0.28543 | 2.3709 | 3.0906 | 0.31229 | -1.089 | -2.8269 | -0.30374 | 1.2057 | 2.9568 | -0.18029 | 2.4114 | -2.7429 | 0.1841 | -2.4411 | -54.228 | -88.3848 | 8.2427 | 125.7573 | 90.4869 | -171.5912 |  | 0.97039 | 1.2364 | 1.1137 | 0.89535 | 1.2444 | 1.1484 | -10.4956 | -118.3841 | 122.5472 | -10.1063 | -120.7339 | 124.6951

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.40481 | 0.21378 | 0.35622 | 0.40402 | 0.21433 | 0.35678 | 4.6744 | 2.4685 | 4.1132 | 4.6652 | 2.4749 | 4.1197 | 3.6967 | -2.8919 | 3.2918 | -3.605 | 2.9204 | -3.237 | 2.2124 | 0.99356 | -3.3749 | -2.1097 | -0.97749 | 3.45 | -40.4729 | 77.6114 | 171.6156 | 139.5568 | -102.2282 | -8.4804 |  | 0.92165 | 1.2388 | 1.1462 | 0.89535 | 1.2444 | 1.1484 | -9.5734 | -121.3494 | 125.9019 | -10.1063 | -120.7339 | 124.6951
Line_1 | 0.77844 | 0.19099 | 0.17182 | 0.77933 | 0.1903 | 0.17104 | 8.9886 | 2.2054 | 1.984 | 8.9989 | 2.1974 | 1.975 | -5.7135 | 2.6306 | -2.1254 | 6.4319 | -2.6167 | 2.0313 | -4.2837 | -0.89212 | 1.0093 | 4.8527 | 0.79339 | -1.0089 | 132.8781 | -103.6822 | -29.061 | -47.1396 | 76.1335 | 151.1083 |  | 0.79446 | 1.2595 | 1.186 | 0.89535 | 1.2444 | 1.1484 | -10.2611 | -122.4156 | 125.5381 | -10.1063 | -120.7339 | 124.6951
Line_2 | 0.38171 | 0.025257 | 0.20575 | 0.38099 | 0.024719 | 0.20533 | 4.4077 | 0.29164 | 2.3758 | 4.3993 | 0.28543 | 2.3709 | 3.0906 | 0.31229 | -1.089 | -2.8269 | -0.30374 | 1.2057 | 2.9568 | -0.18029 | 2.4114 | -2.7429 | 0.1841 | -2.4411 | -54.228 | -88.3848 | 8.2427 | 125.7573 | 90.4869 | -171.5912 |  | 0.97039 | 1.2364 | 1.1137 | 0.89535 | 1.2444 | 1.1484 | -10.4956 | -118.3841 | 122.5472 | -10.1063 | -120.7339 | 124.6951

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3154 | 0.70489 | 0.60748 | 1.3137 | 0.70655 | 0.60913 | 15.1889 | 8.1394 | 7.0146 | 15.1698 | 8.1586 | 7.0336 | 6.1176 | -4.7249 | 7.3456 | -4.3794 | 5.2312 | -6.9981 | 4.3096 | 8.1013 | 1.4233 | -3.2843 | -7.826 | -1.2116 | -63.2908 | 113.8304 | 120.0973 | 116.7165 | -66.1764 | -59.9277 |  | 0.49267 | 1.1522 | 1.0667 | 0.36086 | 1.1538 | 1.0098 | -28.1275 | -125.9178 | 131.0632 | -26.4156 | -122.416 | 129.8949
Line_1 | 1.8601 | 0.57903 | 0.50991 | 1.862 | 0.57697 | 0.50784 | 21.4782 | 6.6861 | 5.8879 | 21.5009 | 6.6623 | 5.864 | -4.213e-11 | 5.9203 | -5.339 | 6.5139 | -6.1259 | 5.0324 | 5.2322e-12 | -5.4874 | -3.8482 | 4.2151 | 4.6436 | 3.12 | 120.6982 | -85.2282 | -81.8892 | -59.3227 | 94.7474 | 98.0966 |  | 0 | 1.2073 | 1.1178 | 0.36086 | 1.1538 | 1.0098 | 0 | -128.0547 | 133.8935 | -26.4156 | -122.416 | 129.8949
Line_2 | 0.56017 | 0.24918 | 0.23585 | 0.55884 | 0.24812 | 0.23497 | 6.4683 | 2.8772 | 2.7234 | 6.453 | 2.8651 | 2.7132 | 3.4705 | -0.3268 | -1.4723 | -2.1345 | 0.89467 | 1.9656 | 1.6124 | -3.2253 | 1.7936 | -0.93084 | 3.1824 | -1.9084 | -49.9882 | -16.9 | -6.1923 | 130.0223 | 163.2865 | 174.0489 |  | 0.59162 | 1.1267 | 0.85204 | 0.36086 | 1.1538 | 1.0098 | -25.0683 | -112.6858 | 123.189 | -26.4156 | -122.416 | 129.8949

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.3154 | 0.70489 | 0.60748 | 1.3137 | 0.70655 | 0.60913 | 15.1889 | 8.1394 | 7.0146 | 15.1698 | 8.1586 | 7.0336 | 6.1176 | -4.7249 | 7.3456 | -4.3794 | 5.2312 | -6.9981 | 4.3096 | 8.1013 | 1.4233 | -3.2843 | -7.826 | -1.2116 | -63.2908 | 113.8304 | 120.0973 | 116.7165 | -66.1764 | -59.9277 |  | 0.49267 | 1.1522 | 1.0667 | 0.36086 | 1.1538 | 1.0098 | -28.1275 | -125.9178 | 131.0632 | -26.4156 | -122.416 | 129.8949
Line_1 | 1.8601 | 0.57903 | 0.50991 | 1.862 | 0.57697 | 0.50784 | 21.4782 | 6.6861 | 5.8879 | 21.5009 | 6.6623 | 5.864 | -4.213e-11 | 5.9203 | -5.339 | 6.5139 | -6.1259 | 5.0324 | 5.2322e-12 | -5.4874 | -3.8482 | 4.2151 | 4.6436 | 3.12 | 120.6982 | -85.2282 | -81.8892 | -59.3227 | 94.7474 | 98.0966 |  | 0 | 1.2073 | 1.1178 | 0.36086 | 1.1538 | 1.0098 | 0 | -128.0547 | 133.8935 | -26.4156 | -122.416 | 129.8949
Line_2 | 0.56017 | 0.24918 | 0.23585 | 0.55884 | 0.24812 | 0.23497 | 6.4683 | 2.8772 | 2.7234 | 6.453 | 2.8651 | 2.7132 | 3.4705 | -0.3268 | -1.4723 | -2.1345 | 0.89467 | 1.9656 | 1.6124 | -3.2253 | 1.7936 | -0.93084 | 3.1824 | -1.9084 | -49.9882 | -16.9 | -6.1923 | 130.0223 | 163.2865 | 174.0489 |  | 0.59162 | 1.1267 | 0.85204 | 0.36086 | 1.1538 | 1.0098 | -25.0683 | -112.6858 | 123.189 | -26.4156 | -122.416 | 129.8949

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48333 | 0.25901 | 0.22322 | 0.48272 | 0.25962 | 0.22382 | 5.581 | 2.9908 | 2.5775 | 5.574 | 2.9978 | 2.5844 | 3.6481 | -1.0489 | 2.5282 | -3.4102 | 1.1184 | -2.4857 | 2.889 | 3.0035 | -0.49584 | -2.7473 | -2.9707 | 0.52561 | -47.8693 | 129.2519 | 135.5187 | 132.138 | -50.7549 | -44.5062 |  | 0.8338 | 1.0637 | 0.99957 | 0.78563 | 1.0589 | 0.98307 | -9.4937 | -121.4978 | 124.4225 | -9.0071 | -120.1245 | 123.5544
Line_1 | 0.68347 | 0.21276 | 0.18736 | 0.68419 | 0.212 | 0.1866 | 7.892 | 2.4568 | 2.1635 | 7.9003 | 2.448 | 2.1547 | -4.2081 | 1.6306 | -2.1329 | 5.0909 | -1.656 | 2.0858 | -2.9769 | -2.1133 | -0.46689 | 3.5507 | 1.9942 | 0.36914 | 136.1196 | -69.8067 | -66.4677 | -43.9012 | 110.1688 | 113.5181 |  | 0.65314 | 1.0865 | 1.0092 | 0.78563 | 1.0589 | 0.98307 | -8.6038 | -122.1535 | 125.8796 | -9.0071 | -120.1245 | 123.5544
Line_2 | 0.20583 | 0.091558 | 0.086663 | 0.20534 | 0.091171 | 0.086338 | 2.3767 | 1.0572 | 1.0007 | 2.3711 | 1.0528 | 0.99695 | 1.8642 | -0.46088 | -0.33653 | -1.6807 | 0.53758 | 0.39994 | 0.89729 | -0.98601 | 0.88107 | -0.80341 | 0.97654 | -0.89476 | -34.5667 | -1.4785 | 9.2291 | 145.4437 | 178.708 | -170.5296 |  | 0.8705 | 1.0295 | 0.94249 | 0.78563 | 1.0589 | 0.98307 | -8.8642 | -116.5311 | 120.134 | -9.0071 | -120.1245 | 123.5544

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.48333 | 0.25901 | 0.22322 | 0.48272 | 0.25962 | 0.22382 | 5.581 | 2.9908 | 2.5775 | 5.574 | 2.9978 | 2.5844 | 3.6481 | -1.0489 | 2.5282 | -3.4102 | 1.1184 | -2.4857 | 2.889 | 3.0035 | -0.49584 | -2.7473 | -2.9707 | 0.52561 | -47.8693 | 129.2519 | 135.5187 | 132.138 | -50.7549 | -44.5062 |  | 0.8338 | 1.0637 | 0.99957 | 0.78563 | 1.0589 | 0.98307 | -9.4937 | -121.4978 | 124.4225 | -9.0071 | -120.1245 | 123.5544
Line_1 | 0.68347 | 0.21276 | 0.18736 | 0.68419 | 0.212 | 0.1866 | 7.892 | 2.4568 | 2.1635 | 7.9003 | 2.448 | 2.1547 | -4.2081 | 1.6306 | -2.1329 | 5.0909 | -1.656 | 2.0858 | -2.9769 | -2.1133 | -0.46689 | 3.5507 | 1.9942 | 0.36914 | 136.1196 | -69.8067 | -66.4677 | -43.9012 | 110.1688 | 113.5181 |  | 0.65314 | 1.0865 | 1.0092 | 0.78563 | 1.0589 | 0.98307 | -8.6038 | -122.1535 | 125.8796 | -9.0071 | -120.1245 | 123.5544
Line_2 | 0.20583 | 0.091558 | 0.086663 | 0.20534 | 0.091171 | 0.086338 | 2.3767 | 1.0572 | 1.0007 | 2.3711 | 1.0528 | 0.99695 | 1.8642 | -0.46088 | -0.33653 | -1.6807 | 0.53758 | 0.39994 | 0.89729 | -0.98601 | 0.88107 | -0.80341 | 0.97654 | -0.89476 | -34.5667 | -1.4785 | 9.2291 | 145.4437 | 178.708 | -170.5296 |  | 0.8705 | 1.0295 | 0.94249 | 0.78563 | 1.0589 | 0.98307 | -8.8642 | -116.5311 | 120.134 | -9.0071 | -120.1245 | 123.5544

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4114 | 2.8027 | 2.952 | 0.41319 | 2.8027 | 2.9517 | 4.7505 | 32.3632 | 34.0865 | 4.7711 | 32.3633 | 34.0836 | -0.72523 | 12.2656 | 7.3296 | 0.80713 | -8.1816 | -2.7914 | 6.5452 | 6.8795 | 15.3684 | -6.4748 | -2.2463 | -10.2206 | -91.9131 | -164.6301 | 23.1271 | 88.1638 | 15.4081 | -156.9089 |  | 1.3862 | 0.43454 | 0.49952 | 1.3676 | 0.26216 | 0.31085 | 4.4097 | -135.3431 | 87.6293 | 5.2695 | -149.2391 | 97.8153
Line_1 | 0.35243 | 3.6373 | 3.5283 | 0.35058 | 3.6373 | 3.5291 | 4.0695 | 41.9997 | 40.7411 | 4.0482 | 42 | 40.7502 | 2.3361 | 8.5176e-11 | 1.0508e-10 | -2.4225 | 10.1276 | 4.8845 | -5.3755 | -7.1343e-11 | -6.407e-12 | 4.9781 | 4.3206 | 11.6876 | 69.487 | 7.6905 | -149.5353 | -110.6799 | -172.3428 | 30.4965 |  | 1.4403 | 0 | 0 | 1.3676 | 0.26216 | 0.31085 | 2.9754 | 0 | 0 | 5.2695 | -149.2391 | 97.8153
Line_2 | 0.14092 | 0.94064 | 0.71316 | 0.13945 | 0.93957 | 0.71211 | 1.6272 | 10.8616 | 8.2348 | 1.6103 | 10.8492 | 8.2228 | -1.4282 | 3.5422 | 2.5641 | 1.6154 | -1.946 | -2.0931 | -1.515 | 2.1114 | 2.6821 | 1.4967 | -2.0742 | -1.467 | 142.1321 | 163.8569 | 62.894 | -37.5464 | -16.0656 | -117.2105 |  | 1.2795 | 0.37966 | 0.45059 | 1.3676 | 0.26216 | 0.31085 | 8.8216 | -165.3446 | 109.1823 | 5.2695 | -149.2391 | 97.8153

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4114 | 2.8027 | 2.952 | 0.41319 | 2.8027 | 2.9517 | 4.7505 | 32.3632 | 34.0865 | 4.7711 | 32.3633 | 34.0836 | -0.72523 | 12.2656 | 7.3296 | 0.80713 | -8.1816 | -2.7914 | 6.5452 | 6.8795 | 15.3684 | -6.4748 | -2.2463 | -10.2206 | -91.9131 | -164.6301 | 23.1271 | 88.1638 | 15.4081 | -156.9089 |  | 1.3862 | 0.43454 | 0.49952 | 1.3676 | 0.26216 | 0.31085 | 4.4097 | -135.3431 | 87.6293 | 5.2695 | -149.2391 | 97.8153
Line_1 | 0.35243 | 3.6373 | 3.5283 | 0.35058 | 3.6373 | 3.5291 | 4.0695 | 41.9997 | 40.7411 | 4.0482 | 42 | 40.7502 | 2.3361 | 8.5176e-11 | 1.0508e-10 | -2.4225 | 10.1276 | 4.8845 | -5.3755 | -7.1343e-11 | -6.407e-12 | 4.9781 | 4.3206 | 11.6876 | 69.487 | 7.6905 | -149.5353 | -110.6799 | -172.3428 | 30.4965 |  | 1.4403 | 0 | 0 | 1.3676 | 0.26216 | 0.31085 | 2.9754 | 0 | 0 | 5.2695 | -149.2391 | 97.8153
Line_2 | 0.14092 | 0.94064 | 0.71316 | 0.13945 | 0.93957 | 0.71211 | 1.6272 | 10.8616 | 8.2348 | 1.6103 | 10.8492 | 8.2228 | -1.4282 | 3.5422 | 2.5641 | 1.6154 | -1.946 | -2.0931 | -1.515 | 2.1114 | 2.6821 | 1.4967 | -2.0742 | -1.467 | 142.1321 | 163.8569 | 62.894 | -37.5464 | -16.0656 | -117.2105 |  | 1.2795 | 0.37966 | 0.45059 | 1.3676 | 0.26216 | 0.31085 | 8.8216 | -165.3446 | 109.1823 | 5.2695 | -149.2391 | 97.8153

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.056514 | 0.70062 | 0.66767 | 0.057011 | 0.70076 | 0.66747 | 0.65257 | 8.0901 | 7.7095 | 0.65831 | 8.0917 | 7.7073 | 0.78657 | 7.2936 | 3.7249 | -0.79028 | -7.0411 | -3.4849 | 0.15279 | 1.5379 | 6.7282 | -0.16014 | -1.2418 | -6.4665 | -7.6123 | -135.8929 | 48.1086 | 171.812 | 44.1678 | -131.9541 |  | 1.2279 | 0.92137 | 0.99753 | 1.2249 | 0.88359 | 0.95309 | 3.3805 | -123.9863 | 109.1386 | 3.2673 | -125.8304 | 109.7248
Line_1 | 0.067893 | 0.98422 | 0.93459 | 0.067169 | 0.98422 | 0.93502 | 0.78397 | 11.3647 | 10.7917 | 0.7756 | 11.3648 | 10.7967 | 0.13959 | -7.9737 | -5.8784 | -0.15181 | 8.8273 | 6.2437 | -0.9808 | -4.5913 | -7.1798 | 0.93781 | 4.7873 | 8.1796 | 84.4557 | 25.7469 | -122.9645 | -95.9277 | -154.3028 | 57.0805 |  | 1.2637 | 0.80962 | 0.85986 | 1.2249 | 0.88359 | 0.95309 | 2.5556 | -124.3196 | 107.7267 | 3.2673 | -125.8304 | 109.7248
Line_2 | 0.086363 | 0.38964 | 0.29547 | 0.086371 | 0.38911 | 0.29508 | 0.99724 | 4.4991 | 3.4118 | 0.99732 | 4.4931 | 3.4072 | -0.92402 | 2.066 | 2.8373 | 0.94209 | -1.7862 | -2.7588 | 0.73336 | 3.5971 | 1.9167 | -0.77767 | -3.5456 | -1.7131 | -137.6406 | 170.8451 | 77.9923 | 42.8061 | -9.0927 | -102.1134 |  | 1.1829 | 0.92199 | 1.0036 | 1.2249 | 0.88359 | 0.95309 | 3.9218 | -129.0255 | 112.0324 | 3.2673 | -125.8304 | 109.7248

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.056514 | 0.70062 | 0.66767 | 0.057011 | 0.70076 | 0.66747 | 0.65257 | 8.0901 | 7.7095 | 0.65831 | 8.0917 | 7.7073 | 0.78657 | 7.2936 | 3.7249 | -0.79028 | -7.0411 | -3.4849 | 0.15279 | 1.5379 | 6.7282 | -0.16014 | -1.2418 | -6.4665 | -7.6123 | -135.8929 | 48.1086 | 171.812 | 44.1678 | -131.9541 |  | 1.2279 | 0.92137 | 0.99753 | 1.2249 | 0.88359 | 0.95309 | 3.3805 | -123.9863 | 109.1386 | 3.2673 | -125.8304 | 109.7248
Line_1 | 0.067893 | 0.98422 | 0.93459 | 0.067169 | 0.98422 | 0.93502 | 0.78397 | 11.3647 | 10.7917 | 0.7756 | 11.3648 | 10.7967 | 0.13959 | -7.9737 | -5.8784 | -0.15181 | 8.8273 | 6.2437 | -0.9808 | -4.5913 | -7.1798 | 0.93781 | 4.7873 | 8.1796 | 84.4557 | 25.7469 | -122.9645 | -95.9277 | -154.3028 | 57.0805 |  | 1.2637 | 0.80962 | 0.85986 | 1.2249 | 0.88359 | 0.95309 | 2.5556 | -124.3196 | 107.7267 | 3.2673 | -125.8304 | 109.7248
Line_2 | 0.086363 | 0.38964 | 0.29547 | 0.086371 | 0.38911 | 0.29508 | 0.99724 | 4.4991 | 3.4118 | 0.99732 | 4.4931 | 3.4072 | -0.92402 | 2.066 | 2.8373 | 0.94209 | -1.7862 | -2.7588 | 0.73336 | 3.5971 | 1.9167 | -0.77767 | -3.5456 | -1.7131 | -137.6406 | 170.8451 | 77.9923 | 42.8061 | -9.0927 | -102.1134 |  | 1.1829 | 0.92199 | 1.0036 | 1.2249 | 0.88359 | 0.95309 | 3.9218 | -129.0255 | 112.0324 | 3.2673 | -125.8304 | 109.7248

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.47985 | 2.2132 | 2.39 | 0.48119 | 2.2134 | 2.3896 | 5.5409 | 25.5558 | 27.597 | 5.5563 | 25.5576 | 27.5922 | 0.75699 | 13.8005 | 10.1987 | -0.53299 | -8.9113 | -4.4888 | 6.3819 | 3.093 | 11.2408 | -6.2635 | -0.20524 | -7.8638 | -79.3394 | -153.5625 | 37.6765 | 100.6862 | 26.4723 | -142.3544 |  | 1.1599 | 0.55341 | 0.54999 | 1.1314 | 0.34877 | 0.32816 | 3.896 | -140.9301 | 85.4594 | 5.8224 | -152.2083 | 97.9273
Line_1 | 0.42411 | 2.8522 | 2.765 | 0.42249 | 2.8519 | 2.7659 | 4.8972 | 32.9345 | 31.9278 | 4.8786 | 32.9312 | 31.938 | 1.1249 | -1.0075e-10 | -4.063e-11 | -1.1699 | 11.3898 | 5.8792 | -5.9668 | -6.3644e-11 | -1.0947e-10 | 5.394 | 1.4783 | 8.6767 | 83.6516 | 20.43 | -137.9813 | -96.4145 | -159.6033 | 42.0484 |  | 1.2399 | 0 | 0 | 1.1314 | 0.34877 | 0.32816 | 4.3283 | 0 | 0 | 5.8224 | -152.2083 | 97.9273
Line_2 | 0.14725 | 0.69247 | 0.42563 | 0.14636 | 0.69187 | 0.42504 | 1.7003 | 7.9959 | 4.9147 | 1.69 | 7.989 | 4.9079 | -1.4469 | 3.981 | 1.6112 | 1.7029 | -2.4785 | -1.3904 | -0.88499 | 1.0663 | 1.6154 | 0.86952 | -1.273 | -0.81285 | 158.536 | -179.4686 | 67.7384 | -21.2276 | 0.60543 | -112.3831 |  | 0.99751 | 0.51543 | 0.46422 | 1.1314 | 0.34877 | 0.32816 | 9.9883 | -164.4744 | 112.8119 | 5.8224 | -152.2083 | 97.9273

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.47985 | 2.2132 | 2.39 | 0.48119 | 2.2134 | 2.3896 | 5.5409 | 25.5558 | 27.597 | 5.5563 | 25.5576 | 27.5922 | 0.75699 | 13.8005 | 10.1987 | -0.53299 | -8.9113 | -4.4888 | 6.3819 | 3.093 | 11.2408 | -6.2635 | -0.20524 | -7.8638 | -79.3394 | -153.5625 | 37.6765 | 100.6862 | 26.4723 | -142.3544 |  | 1.1599 | 0.55341 | 0.54999 | 1.1314 | 0.34877 | 0.32816 | 3.896 | -140.9301 | 85.4594 | 5.8224 | -152.2083 | 97.9273
Line_1 | 0.42411 | 2.8522 | 2.765 | 0.42249 | 2.8519 | 2.7659 | 4.8972 | 32.9345 | 31.9278 | 4.8786 | 32.9312 | 31.938 | 1.1249 | -1.0075e-10 | -4.063e-11 | -1.1699 | 11.3898 | 5.8792 | -5.9668 | -6.3644e-11 | -1.0947e-10 | 5.394 | 1.4783 | 8.6767 | 83.6516 | 20.43 | -137.9813 | -96.4145 | -159.6033 | 42.0484 |  | 1.2399 | 0 | 0 | 1.1314 | 0.34877 | 0.32816 | 4.3283 | 0 | 0 | 5.8224 | -152.2083 | 97.9273
Line_2 | 0.14725 | 0.69247 | 0.42563 | 0.14636 | 0.69187 | 0.42504 | 1.7003 | 7.9959 | 4.9147 | 1.69 | 7.989 | 4.9079 | -1.4469 | 3.981 | 1.6112 | 1.7029 | -2.4785 | -1.3904 | -0.88499 | 1.0663 | 1.6154 | 0.86952 | -1.273 | -0.81285 | 158.536 | -179.4686 | 67.7384 | -21.2276 | 0.60543 | -112.3831 |  | 0.99751 | 0.51543 | 0.46422 | 1.1314 | 0.34877 | 0.32816 | 9.9883 | -164.4744 | 112.8119 | 5.8224 | -152.2083 | 97.9273

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.20437 | 0.65969 | 0.71187 | 0.20493 | 0.6597 | 0.71169 | 2.3599 | 7.6174 | 8.2199 | 2.3664 | 7.6176 | 8.2178 | 1.155 | 6.0499 | 4.0336 | -1.1171 | -5.6171 | -3.5222 | 2.2111 | 2.0493 | 6.0484 | -2.1923 | -1.7887 | -5.7497 | -59.9828 | -143.8011 | 52.9255 | 120.0293 | 36.248 | -127.1177 |  | 1.0571 | 0.83855 | 0.88445 | 1.0398 | 0.77387 | 0.8205 | 2.4368 | -125.0884 | 109.2266 | 3.0278 | -126.0884 | 111.3909
Line_1 | 0.17804 | 0.87685 | 0.81883 | 0.17735 | 0.8768 | 0.81923 | 2.0558 | 10.125 | 9.4551 | 2.0479 | 10.1244 | 9.4597 | -0.33787 | -5.8802 | -4.3143 | 0.32027 | 7.1074 | 4.799 | -2.207 | -3.2202 | -5.1785 | 2.1051 | 3.2973 | 6.1003 | 101.731 | 29.0701 | -120.4581 | -78.3215 | -150.9759 | 59.5825 |  | 1.0861 | 0.66215 | 0.71286 | 1.0398 | 0.77387 | 0.8205 | 3.0273 | -122.2232 | 109.7438 | 3.0278 | -126.0884 | 111.3909
Line_2 | 0.06712 | 0.2376 | 0.14008 | 0.066763 | 0.23731 | 0.13975 | 0.77504 | 2.7436 | 1.6175 | 0.77091 | 2.7402 | 1.6137 | -0.75051 | 1.7004 | 1.328 | 0.79682 | -1.4903 | -1.2768 | -0.094042 | 1.4924 | 0.45226 | 0.087168 | -1.5085 | -0.35062 | 176.5492 | -171.5198 | 96.1613 | -3.2152 | 8.5629 | -83.9647 |  | 0.97593 | 0.82464 | 0.8673 | 1.0398 | 0.77387 | 0.8205 | 3.6914 | -130.2468 | 114.9683 | 3.0278 | -126.0884 | 111.3909

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.20437 | 0.65969 | 0.71187 | 0.20493 | 0.6597 | 0.71169 | 2.3599 | 7.6174 | 8.2199 | 2.3664 | 7.6176 | 8.2178 | 1.155 | 6.0499 | 4.0336 | -1.1171 | -5.6171 | -3.5222 | 2.2111 | 2.0493 | 6.0484 | -2.1923 | -1.7887 | -5.7497 | -59.9828 | -143.8011 | 52.9255 | 120.0293 | 36.248 | -127.1177 |  | 1.0571 | 0.83855 | 0.88445 | 1.0398 | 0.77387 | 0.8205 | 2.4368 | -125.0884 | 109.2266 | 3.0278 | -126.0884 | 111.3909
Line_1 | 0.17804 | 0.87685 | 0.81883 | 0.17735 | 0.8768 | 0.81923 | 2.0558 | 10.125 | 9.4551 | 2.0479 | 10.1244 | 9.4597 | -0.33787 | -5.8802 | -4.3143 | 0.32027 | 7.1074 | 4.799 | -2.207 | -3.2202 | -5.1785 | 2.1051 | 3.2973 | 6.1003 | 101.731 | 29.0701 | -120.4581 | -78.3215 | -150.9759 | 59.5825 |  | 1.0861 | 0.66215 | 0.71286 | 1.0398 | 0.77387 | 0.8205 | 3.0273 | -122.2232 | 109.7438 | 3.0278 | -126.0884 | 111.3909
Line_2 | 0.06712 | 0.2376 | 0.14008 | 0.066763 | 0.23731 | 0.13975 | 0.77504 | 2.7436 | 1.6175 | 0.77091 | 2.7402 | 1.6137 | -0.75051 | 1.7004 | 1.328 | 0.79682 | -1.4903 | -1.2768 | -0.094042 | 1.4924 | 0.45226 | 0.087168 | -1.5085 | -0.35062 | 176.5492 | -171.5198 | 96.1613 | -3.2152 | 8.5629 | -83.9647 |  | 0.97593 | 0.82464 | 0.8673 | 1.0398 | 0.77387 | 0.8205 | 3.6914 | -130.2468 | 114.9683 | 3.0278 | -126.0884 | 111.3909