## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.2445 | 0.85559 | 0.71656 | 2.2421 | 0.85833 | 0.71878 | 25.9178 | 9.8795 | 8.2741 | 25.8896 | 9.9111 | 8.2998 | 4.2585 | -9.5583 | 11.4499 | 1.1964e-10 | 9.5936 | -11.7886 | 4.0942 | 7.78 | 1.7038 | -9.9317e-11 | -8.03 | -1.7037 | -67.8937 | 86.3168 | 121.155 | 112.1378 | -93.6862 | -58.9726 |  | 0.22793 | 1.2475 | 1.3991 | 0 | 1.2623 | 1.4351 | -24.0203 | -132.8272 | 129.6186 | 0 | -133.6163 | 129.2508
Line_1 | 1.1365 | 0.43178 | 0.3617 | 1.134 | 0.42916 | 0.35939 | 13.1236 | 4.9857 | 4.1766 | 13.0939 | 4.9556 | 4.1499 | 2.9552 | 5.6757 | -5.1108 | 6.6732e-11 | -4.7968 | 5.8943 | 1.3544 | -3.4504 | -0.82597 | -4.1612e-11 | 4.015 | 0.85184 | -75.6392 | -93.6488 | -59.1716 | 104.3881 | 86.3138 | 121.0274 |  | 0.2477 | 1.3322 | 1.2396 | 0 | 1.2623 | 1.4351 | -51.0166 | -124.9452 | 130.0087 | 0 | -133.6163 | 129.2508
Line_2 | 1.1365 | 0.43178 | 0.3617 | 1.134 | 0.42916 | 0.35939 | 13.1236 | 4.9857 | 4.1766 | 13.0939 | 4.9556 | 4.1499 | 2.9552 | 5.6757 | -5.1108 | 6.6732e-11 | -4.7968 | 5.8943 | 1.3544 | -3.4504 | -0.82597 | -4.1612e-11 | 4.015 | 0.85184 | -75.6392 | -93.6488 | -59.1716 | 104.3881 | 86.3138 | 121.0274 |  | 0.2477 | 1.3322 | 1.2396 | 0 | 1.2623 | 1.4351 | -51.0166 | -124.9452 | 130.0087 | 0 | -133.6163 | 129.2508

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.2445 | 0.85559 | 0.71656 | 2.2421 | 0.85833 | 0.71878 | 25.9178 | 9.8795 | 8.2741 | 25.8896 | 9.9111 | 8.2998 | 4.2585 | -9.5583 | 11.4499 | 1.1964e-10 | 9.5936 | -11.7886 | 4.0942 | 7.78 | 1.7038 | -9.9317e-11 | -8.03 | -1.7037 | -67.8937 | 86.3168 | 121.155 | 112.1378 | -93.6862 | -58.9726 |  | 0.22793 | 1.2475 | 1.3991 | 0 | 1.2623 | 1.4351 | -24.0203 | -132.8272 | 129.6186 | 0 | -133.6163 | 129.2508
Line_1 | 1.1365 | 0.43178 | 0.3617 | 1.134 | 0.42916 | 0.35939 | 13.1236 | 4.9857 | 4.1766 | 13.0939 | 4.9556 | 4.1499 | 2.9552 | 5.6757 | -5.1108 | 6.6732e-11 | -4.7968 | 5.8943 | 1.3544 | -3.4504 | -0.82597 | -4.1612e-11 | 4.015 | 0.85184 | -75.6392 | -93.6488 | -59.1716 | 104.3881 | 86.3138 | 121.0274 |  | 0.2477 | 1.3322 | 1.2396 | 0 | 1.2623 | 1.4351 | -51.0166 | -124.9452 | 130.0087 | 0 | -133.6163 | 129.2508
Line_2 | 1.1365 | 0.43178 | 0.3617 | 1.134 | 0.42916 | 0.35939 | 13.1236 | 4.9857 | 4.1766 | 13.0939 | 4.9556 | 4.1499 | 2.9552 | 5.6757 | -5.1108 | 6.6732e-11 | -4.7968 | 5.8943 | 1.3544 | -3.4504 | -0.82597 | -4.1612e-11 | 4.015 | 0.85184 | -75.6392 | -93.6488 | -59.1716 | 104.3881 | 86.3138 | 121.0274 |  | 0.2477 | 1.3322 | 1.2396 | 0 | 1.2623 | 1.4351 | -51.0166 | -124.9452 | 130.0087 | 0 | -133.6163 | 129.2508

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.55126 | 0.19647 | 0.31342 | 0.5506 | 0.1971 | 0.31373 | 6.3654 | 2.2686 | 3.6191 | 6.3578 | 2.2759 | 3.6227 | 4.8926 | -2.7003 | 2.9039 | -4.5958 | 2.7394 | -2.9473 | 2.9204 | 0.29619 | -3.2096 | -2.6746 | -0.33361 | 3.2738 | -38.1053 | 63.0495 | 172.4488 | 141.9476 | -116.7911 | -7.6922 |  | 0.89513 | 1.1974 | 1.196 | 0.83635 | 1.2126 | 1.216 | -7.2723 | -123.2102 | 124.5865 | -7.8545 | -123.7346 | 124.3034
Line_1 | 0.4234 | 0.099082 | 0.15726 | 0.42261 | 0.098548 | 0.15687 | 4.889 | 1.1441 | 1.8158 | 4.8798 | 1.1379 | 1.8113 | 2.7126 | 1.3981 | -1.3898 | -2.3653 | -1.3697 | 1.4737 | 3.5308 | -0.1101 | 1.5933 | -3.3259 | 0.16681 | -1.6369 | -62.4464 | -116.4474 | -7.9462 | 117.5652 | 63.2089 | 172.3078 |  | 0.91071 | 1.2258 | 1.1643 | 0.83635 | 1.2126 | 1.216 | -9.9804 | -120.9499 | 123.1526 | -7.8545 | -123.7346 | 124.3034
Line_2 | 0.4234 | 0.099082 | 0.15726 | 0.42261 | 0.098548 | 0.15687 | 4.889 | 1.1441 | 1.8158 | 4.8798 | 1.1379 | 1.8113 | 2.7126 | 1.3981 | -1.3898 | -2.3653 | -1.3697 | 1.4737 | 3.5308 | -0.1101 | 1.5933 | -3.3259 | 0.16681 | -1.6369 | -62.4464 | -116.4474 | -7.9462 | 117.5652 | 63.2089 | 172.3078 |  | 0.91071 | 1.2258 | 1.1643 | 0.83635 | 1.2126 | 1.216 | -9.9804 | -120.9499 | 123.1526 | -7.8545 | -123.7346 | 124.3034

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.55126 | 0.19647 | 0.31342 | 0.5506 | 0.1971 | 0.31373 | 6.3654 | 2.2686 | 3.6191 | 6.3578 | 2.2759 | 3.6227 | 4.8926 | -2.7003 | 2.9039 | -4.5958 | 2.7394 | -2.9473 | 2.9204 | 0.29619 | -3.2096 | -2.6746 | -0.33361 | 3.2738 | -38.1053 | 63.0495 | 172.4488 | 141.9476 | -116.7911 | -7.6922 |  | 0.89513 | 1.1974 | 1.196 | 0.83635 | 1.2126 | 1.216 | -7.2723 | -123.2102 | 124.5865 | -7.8545 | -123.7346 | 124.3034
Line_1 | 0.4234 | 0.099082 | 0.15726 | 0.42261 | 0.098548 | 0.15687 | 4.889 | 1.1441 | 1.8158 | 4.8798 | 1.1379 | 1.8113 | 2.7126 | 1.3981 | -1.3898 | -2.3653 | -1.3697 | 1.4737 | 3.5308 | -0.1101 | 1.5933 | -3.3259 | 0.16681 | -1.6369 | -62.4464 | -116.4474 | -7.9462 | 117.5652 | 63.2089 | 172.3078 |  | 0.91071 | 1.2258 | 1.1643 | 0.83635 | 1.2126 | 1.216 | -9.9804 | -120.9499 | 123.1526 | -7.8545 | -123.7346 | 124.3034
Line_2 | 0.4234 | 0.099082 | 0.15726 | 0.42261 | 0.098548 | 0.15687 | 4.889 | 1.1441 | 1.8158 | 4.8798 | 1.1379 | 1.8113 | 2.7126 | 1.3981 | -1.3898 | -2.3653 | -1.3697 | 1.4737 | 3.5308 | -0.1101 | 1.5933 | -3.3259 | 0.16681 | -1.6369 | -62.4464 | -116.4474 | -7.9462 | 117.5652 | 63.2089 | 172.3078 |  | 0.91071 | 1.2258 | 1.1643 | 0.83635 | 1.2126 | 1.216 | -9.9804 | -120.9499 | 123.1526 | -7.8545 | -123.7346 | 124.3034

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.9777 | 0.73153 | 0.60853 | 1.9759 | 0.73348 | 0.61037 | 22.8364 | 8.447 | 7.0267 | 22.8157 | 8.4695 | 7.0479 | 6.4161 | -3.0212 | 8.6007 | -5.5207e-11 | 2.6857 | -9.0212 | 3.0798 | 8.4192 | 1.0872 | -1.5755e-13 | -8.508 | -1.1523 | -57.3639 | 116.2868 | 121.026 | 122.6788 | -63.812 | -59.1073 |  | 0.31165 | 1.0589 | 1.2337 | 0 | 1.0534 | 1.2904 | -31.7225 | -133.9728 | 128.2303 | 0 | -136.2928 | 128.1718
Line_1 | 0.87347 | 0.36867 | 0.30705 | 0.87152 | 0.36674 | 0.30518 | 10.086 | 4.2571 | 3.5455 | 10.0635 | 4.2347 | 3.5239 | 3.4935 | 2.6511 | -3.4706 | -2.4125e-11 | -1.3428 | 4.5106 | 0.91202 | -4.0201 | -0.47207 | -3.3049e-12 | 4.254 | 0.57615 | -65.0065 | -63.9327 | -59.2814 | 115.0419 | 116.188 | 120.8927 |  | 0.35798 | 1.1312 | 0.98788 | 0 | 1.0534 | 1.2904 | -50.3752 | -120.5294 | 128.4646 | 0 | -136.2928 | 128.1718
Line_2 | 0.87347 | 0.36867 | 0.30705 | 0.87152 | 0.36674 | 0.30518 | 10.086 | 4.2571 | 3.5455 | 10.0635 | 4.2347 | 3.5239 | 3.4935 | 2.6511 | -3.4706 | -2.4125e-11 | -1.3428 | 4.5106 | 0.91202 | -4.0201 | -0.47207 | -3.3049e-12 | 4.254 | 0.57615 | -65.0065 | -63.9327 | -59.2814 | 115.0419 | 116.188 | 120.8927 |  | 0.35798 | 1.1312 | 0.98788 | 0 | 1.0534 | 1.2904 | -50.3752 | -120.5294 | 128.4646 | 0 | -136.2928 | 128.1718

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.9777 | 0.73153 | 0.60853 | 1.9759 | 0.73348 | 0.61037 | 22.8364 | 8.447 | 7.0267 | 22.8157 | 8.4695 | 7.0479 | 6.4161 | -3.0212 | 8.6007 | -5.5207e-11 | 2.6857 | -9.0212 | 3.0798 | 8.4192 | 1.0872 | -1.5755e-13 | -8.508 | -1.1523 | -57.3639 | 116.2868 | 121.026 | 122.6788 | -63.812 | -59.1073 |  | 0.31165 | 1.0589 | 1.2337 | 0 | 1.0534 | 1.2904 | -31.7225 | -133.9728 | 128.2303 | 0 | -136.2928 | 128.1718
Line_1 | 0.87347 | 0.36867 | 0.30705 | 0.87152 | 0.36674 | 0.30518 | 10.086 | 4.2571 | 3.5455 | 10.0635 | 4.2347 | 3.5239 | 3.4935 | 2.6511 | -3.4706 | -2.4125e-11 | -1.3428 | 4.5106 | 0.91202 | -4.0201 | -0.47207 | -3.3049e-12 | 4.254 | 0.57615 | -65.0065 | -63.9327 | -59.2814 | 115.0419 | 116.188 | 120.8927 |  | 0.35798 | 1.1312 | 0.98788 | 0 | 1.0534 | 1.2904 | -50.3752 | -120.5294 | 128.4646 | 0 | -136.2928 | 128.1718
Line_2 | 0.87347 | 0.36867 | 0.30705 | 0.87152 | 0.36674 | 0.30518 | 10.086 | 4.2571 | 3.5455 | 10.0635 | 4.2347 | 3.5239 | 3.4935 | 2.6511 | -3.4706 | -2.4125e-11 | -1.3428 | 4.5106 | 0.91202 | -4.0201 | -0.47207 | -3.3049e-12 | 4.254 | 0.57615 | -65.0065 | -63.9327 | -59.2814 | 115.0419 | 116.188 | 120.8927 |  | 0.35798 | 1.1312 | 0.98788 | 0 | 1.0534 | 1.2904 | -50.3752 | -120.5294 | 128.4646 | 0 | -136.2928 | 128.1718

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.60933 | 0.22539 | 0.18749 | 0.60878 | 0.22599 | 0.18806 | 7.036 | 2.6025 | 2.1649 | 7.0296 | 2.6095 | 2.1715 | 4.3005 | -0.84419 | 2.2665 | -3.6905 | 0.81682 | -2.3118 | 3.5541 | 2.5339 | -0.33808 | -3.256 | -2.546 | 0.32985 | -46.3057 | 127.345 | 132.0842 | 133.737 | -52.7538 | -48.0491 |  | 0.79293 | 1.0263 | 1.0585 | 0.70012 | 1.0247 | 1.0754 | -6.7341 | -124.2294 | 123.6002 | -4.842 | -124.9664 | 123.8308
Line_1 | 0.26912 | 0.11359 | 0.094603 | 0.26852 | 0.11299 | 0.094028 | 3.1075 | 1.3116 | 1.0924 | 3.1006 | 1.3047 | 1.0857 | 1.7559 | 0.53592 | -1.0623 | -1.4225 | -0.40841 | 1.1559 | 1.7312 | -1.2548 | 0.17392 | -1.6397 | 1.273 | -0.16492 | -53.9483 | -52.8745 | -48.2232 | 126.1001 | 127.2462 | 131.9509 |  | 0.7935 | 1.0403 | 0.98541 | 0.70012 | 1.0247 | 1.0754 | -9.3547 | -119.7472 | 122.4788 | -4.842 | -124.9664 | 123.8308
Line_2 | 0.26912 | 0.11359 | 0.094603 | 0.26852 | 0.11299 | 0.094028 | 3.1075 | 1.3116 | 1.0924 | 3.1006 | 1.3047 | 1.0857 | 1.7559 | 0.53592 | -1.0623 | -1.4225 | -0.40841 | 1.1559 | 1.7312 | -1.2548 | 0.17392 | -1.6397 | 1.273 | -0.16492 | -53.9483 | -52.8745 | -48.2232 | 126.1001 | 127.2462 | 131.9509 |  | 0.7935 | 1.0403 | 0.98541 | 0.70012 | 1.0247 | 1.0754 | -9.3547 | -119.7472 | 122.4788 | -4.842 | -124.9664 | 123.8308

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.60933 | 0.22539 | 0.18749 | 0.60878 | 0.22599 | 0.18806 | 7.036 | 2.6025 | 2.1649 | 7.0296 | 2.6095 | 2.1715 | 4.3005 | -0.84419 | 2.2665 | -3.6905 | 0.81682 | -2.3118 | 3.5541 | 2.5339 | -0.33808 | -3.256 | -2.546 | 0.32985 | -46.3057 | 127.345 | 132.0842 | 133.737 | -52.7538 | -48.0491 |  | 0.79293 | 1.0263 | 1.0585 | 0.70012 | 1.0247 | 1.0754 | -6.7341 | -124.2294 | 123.6002 | -4.842 | -124.9664 | 123.8308
Line_1 | 0.26912 | 0.11359 | 0.094603 | 0.26852 | 0.11299 | 0.094028 | 3.1075 | 1.3116 | 1.0924 | 3.1006 | 1.3047 | 1.0857 | 1.7559 | 0.53592 | -1.0623 | -1.4225 | -0.40841 | 1.1559 | 1.7312 | -1.2548 | 0.17392 | -1.6397 | 1.273 | -0.16492 | -53.9483 | -52.8745 | -48.2232 | 126.1001 | 127.2462 | 131.9509 |  | 0.7935 | 1.0403 | 0.98541 | 0.70012 | 1.0247 | 1.0754 | -9.3547 | -119.7472 | 122.4788 | -4.842 | -124.9664 | 123.8308
Line_2 | 0.26912 | 0.11359 | 0.094603 | 0.26852 | 0.11299 | 0.094028 | 3.1075 | 1.3116 | 1.0924 | 3.1006 | 1.3047 | 1.0857 | 1.7559 | 0.53592 | -1.0623 | -1.4225 | -0.40841 | 1.1559 | 1.7312 | -1.2548 | 0.17392 | -1.6397 | 1.273 | -0.16492 | -53.9483 | -52.8745 | -48.2232 | 126.1001 | 127.2462 | 131.9509 |  | 0.7935 | 1.0403 | 0.98541 | 0.70012 | 1.0247 | 1.0754 | -9.3547 | -119.7472 | 122.4788 | -4.842 | -124.9664 | 123.8308

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.39068 | 3.8736 | 3.6009 | 0.39288 | 3.8738 | 3.6002 | 4.5112 | 44.7289 | 41.5798 | 4.5365 | 44.7307 | 41.5719 | -0.15677 | 10.1058 | 5.0049 | 0.11285 | 9.1349e-11 | 1.2029e-10 | 6.3143 | 7.3535 | 9.5231 | -6.5094 | -9.4216e-11 | -1.6344e-12 | -91.4692 | -174.5598 | 19.5163 | 88.546 | 5.4726 | -160.5169 |  | 1.4001 | 0.27942 | 0.25874 | 1.4351 | 0 | 0 | -0.047021 | -138.5182 | 81.7918 | -0.46075 | 0 | 0
Line_1 | 0.19852 | 1.1189 | 0.93207 | 0.19644 | 1.1178 | 0.9305 | 2.2923 | 12.92 | 10.7626 | 2.2683 | 12.9069 | 10.7445 | 0.33845 | 2.2461 | 1.0263 | -0.056427 | 3.6335e-11 | 2.4595e-11 | -3.0712 | -0.22252 | 1.9536 | 3.2547 | -1.066e-11 | -1.9023e-11 | 88.6496 | 155.8474 | 56.5112 | -91.454 | -24.0615 | -123.5754 |  | 1.3479 | 0.1747 | 0.20504 | 1.4351 | 0 | 0 | 4.9383 | 150.1896 | 118.7975 | -0.46075 | 0 | 0
Line_2 | 0.19852 | 1.1189 | 0.93207 | 0.19644 | 1.1178 | 0.9305 | 2.2923 | 12.92 | 10.7626 | 2.2683 | 12.9069 | 10.7445 | 0.33845 | 2.2461 | 1.0263 | -0.056427 | 3.6335e-11 | 2.4595e-11 | -3.0712 | -0.22252 | 1.9536 | 3.2547 | -1.066e-11 | -1.9023e-11 | 88.6496 | 155.8474 | 56.5112 | -91.454 | -24.0615 | -123.5754 |  | 1.3479 | 0.1747 | 0.20504 | 1.4351 | 0 | 0 | 4.9383 | 150.1896 | 118.7975 | -0.46075 | 0 | 0

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.39068 | 3.8736 | 3.6009 | 0.39288 | 3.8738 | 3.6002 | 4.5112 | 44.7289 | 41.5798 | 4.5365 | 44.7307 | 41.5719 | -0.15677 | 10.1058 | 5.0049 | 0.11285 | 9.1349e-11 | 1.2029e-10 | 6.3143 | 7.3535 | 9.5231 | -6.5094 | -9.4216e-11 | -1.6344e-12 | -91.4692 | -174.5598 | 19.5163 | 88.546 | 5.4726 | -160.5169 |  | 1.4001 | 0.27942 | 0.25874 | 1.4351 | 0 | 0 | -0.047021 | -138.5182 | 81.7918 | -0.46075 | 0 | 0
Line_1 | 0.19852 | 1.1189 | 0.93207 | 0.19644 | 1.1178 | 0.9305 | 2.2923 | 12.92 | 10.7626 | 2.2683 | 12.9069 | 10.7445 | 0.33845 | 2.2461 | 1.0263 | -0.056427 | 3.6335e-11 | 2.4595e-11 | -3.0712 | -0.22252 | 1.9536 | 3.2547 | -1.066e-11 | -1.9023e-11 | 88.6496 | 155.8474 | 56.5112 | -91.454 | -24.0615 | -123.5754 |  | 1.3479 | 0.1747 | 0.20504 | 1.4351 | 0 | 0 | 4.9383 | 150.1896 | 118.7975 | -0.46075 | 0 | 0
Line_2 | 0.19852 | 1.1189 | 0.93207 | 0.19644 | 1.1178 | 0.9305 | 2.2923 | 12.92 | 10.7626 | 2.2683 | 12.9069 | 10.7445 | 0.33845 | 2.2461 | 1.0263 | -0.056427 | 3.6335e-11 | 2.4595e-11 | -3.0712 | -0.22252 | 1.9536 | 3.2547 | -1.066e-11 | -1.9023e-11 | 88.6496 | 155.8474 | 56.5112 | -91.454 | -24.0615 | -123.5754 |  | 1.3479 | 0.1747 | 0.20504 | 1.4351 | 0 | 0 | 4.9383 | 150.1896 | 118.7975 | -0.46075 | 0 | 0

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.03854 | 0.82982 | 0.73067 | 0.038354 | 0.8301 | 0.73019 | 0.44502 | 9.5819 | 8.437 | 0.44287 | 9.5851 | 8.4315 | 0.48292 | 8.4094 | 4.4139 | -0.49178 | -7.9253 | -4.1988 | -0.26005 | 3.1773 | 6.5875 | 0.25673 | -2.9233 | -6.1054 | 29.3057 | -143.831 | 52.992 | -151.8031 | 36.2183 | -127.0552 |  | 1.2325 | 0.93819 | 0.93986 | 1.2526 | 0.88129 | 0.87883 | 1.0039 | -123.1328 | 109.1685 | 0.63092 | -123.5347 | 108.4274
Line_1 | 0.01911 | 0.38465 | 0.36524 | 0.019177 | 0.3842 | 0.36466 | 0.22066 | 4.4416 | 4.2174 | 0.22144 | 4.4364 | 4.2107 | -0.24535 | 1.4883 | 3.2184 | 0.24589 | -1.2151 | -3.0495 | 0.10839 | 3.7109 | 2.3656 | -0.12836 | -3.7161 | -2.0962 | -153.9952 | 164.4854 | 73.9936 | 28.1969 | -15.4274 | -106.0773 |  | 1.2155 | 0.90018 | 0.94709 | 1.2526 | 0.88129 | 0.87883 | 2.1696 | -127.3679 | 110.3106 | 0.63092 | -123.5347 | 108.4274
Line_2 | 0.01911 | 0.38465 | 0.36524 | 0.019177 | 0.3842 | 0.36466 | 0.22066 | 4.4416 | 4.2174 | 0.22144 | 4.4364 | 4.2107 | -0.24535 | 1.4883 | 3.2184 | 0.24589 | -1.2151 | -3.0495 | 0.10839 | 3.7109 | 2.3656 | -0.12836 | -3.7161 | -2.0962 | -153.9952 | 164.4854 | 73.9936 | 28.1969 | -15.4274 | -106.0773 |  | 1.2155 | 0.90018 | 0.94709 | 1.2526 | 0.88129 | 0.87883 | 2.1696 | -127.3679 | 110.3106 | 0.63092 | -123.5347 | 108.4274

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.03854 | 0.82982 | 0.73067 | 0.038354 | 0.8301 | 0.73019 | 0.44502 | 9.5819 | 8.437 | 0.44287 | 9.5851 | 8.4315 | 0.48292 | 8.4094 | 4.4139 | -0.49178 | -7.9253 | -4.1988 | -0.26005 | 3.1773 | 6.5875 | 0.25673 | -2.9233 | -6.1054 | 29.3057 | -143.831 | 52.992 | -151.8031 | 36.2183 | -127.0552 |  | 1.2325 | 0.93819 | 0.93986 | 1.2526 | 0.88129 | 0.87883 | 1.0039 | -123.1328 | 109.1685 | 0.63092 | -123.5347 | 108.4274
Line_1 | 0.01911 | 0.38465 | 0.36524 | 0.019177 | 0.3842 | 0.36466 | 0.22066 | 4.4416 | 4.2174 | 0.22144 | 4.4364 | 4.2107 | -0.24535 | 1.4883 | 3.2184 | 0.24589 | -1.2151 | -3.0495 | 0.10839 | 3.7109 | 2.3656 | -0.12836 | -3.7161 | -2.0962 | -153.9952 | 164.4854 | 73.9936 | 28.1969 | -15.4274 | -106.0773 |  | 1.2155 | 0.90018 | 0.94709 | 1.2526 | 0.88129 | 0.87883 | 2.1696 | -127.3679 | 110.3106 | 0.63092 | -123.5347 | 108.4274
Line_2 | 0.01911 | 0.38465 | 0.36524 | 0.019177 | 0.3842 | 0.36466 | 0.22066 | 4.4416 | 4.2174 | 0.22144 | 4.4364 | 4.2107 | -0.24535 | 1.4883 | 3.2184 | 0.24589 | -1.2151 | -3.0495 | 0.10839 | 3.7109 | 2.3656 | -0.12836 | -3.7161 | -2.0962 | -153.9952 | 164.4854 | 73.9936 | 28.1969 | -15.4274 | -106.0773 |  | 1.2155 | 0.90018 | 0.94709 | 1.2526 | 0.88129 | 0.87883 | 2.1696 | -127.3679 | 110.3106 | 0.63092 | -123.5347 | 108.4274

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4369 | 3.2815 | 3.0192 | 0.43863 | 3.2818 | 3.0184 | 5.0449 | 37.8911 | 34.8632 | 5.0649 | 37.895 | 34.8536 | 2.3508 | 13.2261 | 7.5317 | -2.5311 | -1.1635e-10 | -2.5871e-11 | 5.6508 | 3.942 | 8.1433 | -5.8393 | -8.28e-11 | -1.3004e-10 | -68.2935 | -167.4196 | 28.7525 | 111.625 | 12.612 | -151.2786 |  | 1.2131 | 0.36423 | 0.31817 | 1.2565 | 0 | 0 | -0.88103 | -150.8229 | 75.987 | -1.81 | 0 | 0
Line_1 | 0.22095 | 0.96115 | 0.62632 | 0.21932 | 0.96037 | 0.6251 | 2.5513 | 11.0984 | 7.2322 | 2.5325 | 11.0894 | 7.218 | -0.7065 | 2.9816 | 0.86989 | 1.2656 | -1.8836e-11 | -1.8833e-11 | -2.7092 | -0.71975 | 1.7319 | 2.9196 | -3.7304e-11 | -1.9983e-11 | 111.5602 | 164.7537 | 60.8748 | -68.375 | -15.1593 | -119.2267 |  | 1.0974 | 0.27637 | 0.26798 | 1.2565 | 0 | 0 | 6.9442 | 151.1825 | 124.2052 | -1.81 | 0 | 0
Line_2 | 0.22095 | 0.96115 | 0.62632 | 0.21932 | 0.96037 | 0.6251 | 2.5513 | 11.0984 | 7.2322 | 2.5325 | 11.0894 | 7.218 | -0.7065 | 2.9816 | 0.86989 | 1.2656 | -1.8836e-11 | -1.8833e-11 | -2.7092 | -0.71975 | 1.7319 | 2.9196 | -3.7304e-11 | -1.9983e-11 | 111.5602 | 164.7537 | 60.8748 | -68.375 | -15.1593 | -119.2267 |  | 1.0974 | 0.27637 | 0.26798 | 1.2565 | 0 | 0 | 6.9442 | 151.1825 | 124.2052 | -1.81 | 0 | 0

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4369 | 3.2815 | 3.0192 | 0.43863 | 3.2818 | 3.0184 | 5.0449 | 37.8911 | 34.8632 | 5.0649 | 37.895 | 34.8536 | 2.3508 | 13.2261 | 7.5317 | -2.5311 | -1.1635e-10 | -2.5871e-11 | 5.6508 | 3.942 | 8.1433 | -5.8393 | -8.28e-11 | -1.3004e-10 | -68.2935 | -167.4196 | 28.7525 | 111.625 | 12.612 | -151.2786 |  | 1.2131 | 0.36423 | 0.31817 | 1.2565 | 0 | 0 | -0.88103 | -150.8229 | 75.987 | -1.81 | 0 | 0
Line_1 | 0.22095 | 0.96115 | 0.62632 | 0.21932 | 0.96037 | 0.6251 | 2.5513 | 11.0984 | 7.2322 | 2.5325 | 11.0894 | 7.218 | -0.7065 | 2.9816 | 0.86989 | 1.2656 | -1.8836e-11 | -1.8833e-11 | -2.7092 | -0.71975 | 1.7319 | 2.9196 | -3.7304e-11 | -1.9983e-11 | 111.5602 | 164.7537 | 60.8748 | -68.375 | -15.1593 | -119.2267 |  | 1.0974 | 0.27637 | 0.26798 | 1.2565 | 0 | 0 | 6.9442 | 151.1825 | 124.2052 | -1.81 | 0 | 0
Line_2 | 0.22095 | 0.96115 | 0.62632 | 0.21932 | 0.96037 | 0.6251 | 2.5513 | 11.0984 | 7.2322 | 2.5325 | 11.0894 | 7.218 | -0.7065 | 2.9816 | 0.86989 | 1.2656 | -1.8836e-11 | -1.8833e-11 | -2.7092 | -0.71975 | 1.7319 | 2.9196 | -3.7304e-11 | -1.9983e-11 | 111.5602 | 164.7537 | 60.8748 | -68.375 | -15.1593 | -119.2267 |  | 1.0974 | 0.27637 | 0.26798 | 1.2565 | 0 | 0 | 6.9442 | 151.1825 | 124.2052 | -1.81 | 0 | 0

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.17412 | 0.79972 | 0.78786 | 0.17472 | 0.79996 | 0.78738 | 2.0105 | 9.2344 | 9.0974 | 2.0175 | 9.2371 | 9.0919 | 1.0831 | 6.8273 | 4.1887 | -1.1086 | -6.0216 | -3.6127 | 1.867 | 3.7241 | 6.1514 | -1.8927 | -3.5889 | -5.4926 | -60.1135 | -152.1377 | 53.2705 | 119.8008 | 27.9059 | -126.762 |  | 1.0735 | 0.84218 | 0.81805 | 1.0872 | 0.75889 | 0.72309 | -0.23327 | -123.5268 | 109.018 | -0.55757 | -121.2988 | 109.904
Line_1 | 0.087933 | 0.25206 | 0.22031 | 0.087358 | 0.2518 | 0.21977 | 1.0154 | 2.9106 | 2.544 | 1.0087 | 2.9075 | 2.5376 | -0.47399 | 1.078 | 1.8555 | 0.5543 | -0.82864 | -1.6794 | -0.92455 | 1.9636 | 0.92251 | 0.94635 | -2.045 | -0.73938 | 119.7185 | 170.6398 | 86.1969 | -60.1992 | -9.2407 | -93.8586 |  | 1.0233 | 0.76962 | 0.81456 | 1.0872 | 0.75889 | 0.72309 | 2.5755 | -128.1257 | 112.632 | -0.55757 | -121.2988 | 109.904
Line_2 | 0.087933 | 0.25206 | 0.22031 | 0.087358 | 0.2518 | 0.21977 | 1.0154 | 2.9106 | 2.544 | 1.0087 | 2.9075 | 2.5376 | -0.47399 | 1.078 | 1.8555 | 0.5543 | -0.82864 | -1.6794 | -0.92455 | 1.9636 | 0.92251 | 0.94635 | -2.045 | -0.73938 | 119.7185 | 170.6398 | 86.1969 | -60.1992 | -9.2407 | -93.8586 |  | 1.0233 | 0.76962 | 0.81456 | 1.0872 | 0.75889 | 0.72309 | 2.5755 | -128.1257 | 112.632 | -0.55757 | -121.2988 | 109.904

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.17412 | 0.79972 | 0.78786 | 0.17472 | 0.79996 | 0.78738 | 2.0105 | 9.2344 | 9.0974 | 2.0175 | 9.2371 | 9.0919 | 1.0831 | 6.8273 | 4.1887 | -1.1086 | -6.0216 | -3.6127 | 1.867 | 3.7241 | 6.1514 | -1.8927 | -3.5889 | -5.4926 | -60.1135 | -152.1377 | 53.2705 | 119.8008 | 27.9059 | -126.762 |  | 1.0735 | 0.84218 | 0.81805 | 1.0872 | 0.75889 | 0.72309 | -0.23327 | -123.5268 | 109.018 | -0.55757 | -121.2988 | 109.904
Line_1 | 0.087933 | 0.25206 | 0.22031 | 0.087358 | 0.2518 | 0.21977 | 1.0154 | 2.9106 | 2.544 | 1.0087 | 2.9075 | 2.5376 | -0.47399 | 1.078 | 1.8555 | 0.5543 | -0.82864 | -1.6794 | -0.92455 | 1.9636 | 0.92251 | 0.94635 | -2.045 | -0.73938 | 119.7185 | 170.6398 | 86.1969 | -60.1992 | -9.2407 | -93.8586 |  | 1.0233 | 0.76962 | 0.81456 | 1.0872 | 0.75889 | 0.72309 | 2.5755 | -128.1257 | 112.632 | -0.55757 | -121.2988 | 109.904
Line_2 | 0.087933 | 0.25206 | 0.22031 | 0.087358 | 0.2518 | 0.21977 | 1.0154 | 2.9106 | 2.544 | 1.0087 | 2.9075 | 2.5376 | -0.47399 | 1.078 | 1.8555 | 0.5543 | -0.82864 | -1.6794 | -0.92455 | 1.9636 | 0.92251 | 0.94635 | -2.045 | -0.73938 | 119.7185 | 170.6398 | 86.1969 | -60.1992 | -9.2407 | -93.8586 |  | 1.0233 | 0.76962 | 0.81456 | 1.0872 | 0.75889 | 0.72309 | 2.5755 | -128.1257 | 112.632 | -0.55757 | -121.2988 | 109.904