## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7855 | 0.96185 | 0.87784 | 1.7825 | 0.96502 | 0.8804 | 20.6175 | 11.1065 | 10.1364 | 20.5831 | 11.1431 | 10.166 | 1.6652 | -9.5088 | 14.9618 | 8.7022e-11 | 10.023 | -14.6016 | 1.8791 | 11.6394 | 2.831 | -6.8104e-11 | -11.1263 | -2.4131 | -72.6838 | 93.0644 | 123.1973 | 107.3529 | -86.9577 | -56.9272 |  | 0.12178 | 1.3532 | 1.5022 | 0 | 1.3439 | 1.4558 | -24.2306 | -137.6887 | 133.9118 | 0 | -134.9441 | 132.4568
Line_1 | 1.1526 | 0.48535 | 0.44271 | 1.1498 | 0.48251 | 0.4402 | 13.3089 | 5.6044 | 5.112 | 13.2766 | 5.5716 | 5.083 | 3.1737 | 6.1196 | -6.2432 | 5.7709e-11 | -5.0115 | 7.3008 | 1.5135 | -4.9373 | -1.1425 | -4.1834e-11 | 5.5631 | 1.2065 | -74.7804 | -86.9452 | -57.0994 | 105.2444 | 93.0423 | 123.0728 |  | 0.26419 | 1.403 | 1.2416 | 0 | 1.3439 | 1.4558 | -49.2847 | -125.8421 | 133.2708 | 0 | -134.9441 | 132.4568
Line_2 | 1.1526 | 0.48535 | 0.44271 | 1.1498 | 0.48251 | 0.4402 | 13.3089 | 5.6044 | 5.112 | 13.2766 | 5.5716 | 5.083 | 3.1737 | 6.1196 | -6.2432 | 5.7709e-11 | -5.0115 | 7.3008 | 1.5135 | -4.9373 | -1.1425 | -4.1834e-11 | 5.5631 | 1.2065 | -74.7804 | -86.9452 | -57.0994 | 105.2444 | 93.0423 | 123.0728 |  | 0.26419 | 1.403 | 1.2416 | 0 | 1.3439 | 1.4558 | -49.2847 | -125.8421 | 133.2708 | 0 | -134.9441 | 132.4568

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7855 | 0.96185 | 0.87784 | 1.7825 | 0.96502 | 0.8804 | 20.6175 | 11.1065 | 10.1364 | 20.5831 | 11.1431 | 10.166 | 1.6652 | -9.5088 | 14.9618 | 8.7022e-11 | 10.023 | -14.6016 | 1.8791 | 11.6394 | 2.831 | -6.8104e-11 | -11.1263 | -2.4131 | -72.6838 | 93.0644 | 123.1973 | 107.3529 | -86.9577 | -56.9272 |  | 0.12178 | 1.3532 | 1.5022 | 0 | 1.3439 | 1.4558 | -24.2306 | -137.6887 | 133.9118 | 0 | -134.9441 | 132.4568
Line_1 | 1.1526 | 0.48535 | 0.44271 | 1.1498 | 0.48251 | 0.4402 | 13.3089 | 5.6044 | 5.112 | 13.2766 | 5.5716 | 5.083 | 3.1737 | 6.1196 | -6.2432 | 5.7709e-11 | -5.0115 | 7.3008 | 1.5135 | -4.9373 | -1.1425 | -4.1834e-11 | 5.5631 | 1.2065 | -74.7804 | -86.9452 | -57.0994 | 105.2444 | 93.0423 | 123.0728 |  | 0.26419 | 1.403 | 1.2416 | 0 | 1.3439 | 1.4558 | -49.2847 | -125.8421 | 133.2708 | 0 | -134.9441 | 132.4568
Line_2 | 1.1526 | 0.48535 | 0.44271 | 1.1498 | 0.48251 | 0.4402 | 13.3089 | 5.6044 | 5.112 | 13.2766 | 5.5716 | 5.083 | 3.1737 | 6.1196 | -6.2432 | 5.7709e-11 | -5.0115 | 7.3008 | 1.5135 | -4.9373 | -1.1425 | -4.1834e-11 | 5.5631 | 1.2065 | -74.7804 | -86.9452 | -57.0994 | 105.2444 | 93.0423 | 123.0728 |  | 0.26419 | 1.403 | 1.2416 | 0 | 1.3439 | 1.4558 | -49.2847 | -125.8421 | 133.2708 | 0 | -134.9441 | 132.4568

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45161 | 0.21456 | 0.37945 | 0.45074 | 0.21551 | 0.37995 | 5.2148 | 2.4775 | 4.3815 | 5.2047 | 2.4885 | 4.3872 | 3.7244 | -2.7455 | 4.0263 | -3.6136 | 2.7787 | -3.9654 | 2.3558 | 1.3895 | -3.4728 | -2.2269 | -1.3741 | 3.5533 | -40.77 | 81.9922 | 167.9151 | 139.3022 | -97.8944 | -12.2233 |  | 0.84508 | 1.242 | 1.2135 | 0.81554 | 1.2457 | 1.2136 | -8.4553 | -124.8523 | 127.1357 | -9.0543 | -124.2063 | 125.9142
Line_1 | 0.45056 | 0.10854 | 0.19053 | 0.44964 | 0.10776 | 0.18997 | 5.2026 | 1.2533 | 2.2001 | 5.192 | 1.2443 | 2.1936 | 3.0436 | 1.4433 | -1.8513 | -2.6273 | -1.3894 | 1.9827 | 3.5718 | -0.62337 | 1.734 | -3.3206 | 0.68703 | -1.7766 | -60.7123 | -97.6288 | -12.4456 | 119.2966 | 82.1056 | 167.7767 |  | 0.90197 | 1.2544 | 1.1529 | 0.81554 | 1.2457 | 1.2136 | -11.1473 | -120.9889 | 124.4284 | -9.0543 | -124.2063 | 125.9142
Line_2 | 0.45056 | 0.10854 | 0.19053 | 0.44964 | 0.10776 | 0.18997 | 5.2026 | 1.2533 | 2.2001 | 5.192 | 1.2443 | 2.1936 | 3.0436 | 1.4433 | -1.8513 | -2.6273 | -1.3894 | 1.9827 | 3.5718 | -0.62337 | 1.734 | -3.3206 | 0.68703 | -1.7766 | -60.7123 | -97.6288 | -12.4456 | 119.2966 | 82.1056 | 167.7767 |  | 0.90197 | 1.2544 | 1.1529 | 0.81554 | 1.2457 | 1.2136 | -11.1473 | -120.9889 | 124.4284 | -9.0543 | -124.2063 | 125.9142

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.45161 | 0.21456 | 0.37945 | 0.45074 | 0.21551 | 0.37995 | 5.2148 | 2.4775 | 4.3815 | 5.2047 | 2.4885 | 4.3872 | 3.7244 | -2.7455 | 4.0263 | -3.6136 | 2.7787 | -3.9654 | 2.3558 | 1.3895 | -3.4728 | -2.2269 | -1.3741 | 3.5533 | -40.77 | 81.9922 | 167.9151 | 139.3022 | -97.8944 | -12.2233 |  | 0.84508 | 1.242 | 1.2135 | 0.81554 | 1.2457 | 1.2136 | -8.4553 | -124.8523 | 127.1357 | -9.0543 | -124.2063 | 125.9142
Line_1 | 0.45056 | 0.10854 | 0.19053 | 0.44964 | 0.10776 | 0.18997 | 5.2026 | 1.2533 | 2.2001 | 5.192 | 1.2443 | 2.1936 | 3.0436 | 1.4433 | -1.8513 | -2.6273 | -1.3894 | 1.9827 | 3.5718 | -0.62337 | 1.734 | -3.3206 | 0.68703 | -1.7766 | -60.7123 | -97.6288 | -12.4456 | 119.2966 | 82.1056 | 167.7767 |  | 0.90197 | 1.2544 | 1.1529 | 0.81554 | 1.2457 | 1.2136 | -11.1473 | -120.9889 | 124.4284 | -9.0543 | -124.2063 | 125.9142
Line_2 | 0.45056 | 0.10854 | 0.19053 | 0.44964 | 0.10776 | 0.18997 | 5.2026 | 1.2533 | 2.2001 | 5.192 | 1.2443 | 2.1936 | 3.0436 | 1.4433 | -1.8513 | -2.6273 | -1.3894 | 1.9827 | 3.5718 | -0.62337 | 1.734 | -3.3206 | 0.68703 | -1.7766 | -60.7123 | -97.6288 | -12.4456 | 119.2966 | 82.1056 | 167.7767 |  | 0.90197 | 1.2544 | 1.1529 | 0.81554 | 1.2457 | 1.2136 | -11.1473 | -120.9889 | 124.4284 | -9.0543 | -124.2063 | 125.9142

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5911 | 0.84664 | 0.73882 | 1.5889 | 0.84889 | 0.74094 | 18.3719 | 9.7762 | 8.5311 | 18.3466 | 9.8021 | 8.5556 | 2.5367 | -1.6649 | 11.6896 | -4.3525e-11 | 2.4036 | -11.1769 | 1.4868 | 11.1108 | 1.8279 | 7.1838e-13 | -10.7079 | -1.5352 | -58.9752 | 119.3333 | 123.3804 | 121.0895 | -60.7833 | -56.7651 |  | 0.16005 | 1.1492 | 1.3869 | 0 | 1.1196 | 1.3186 | -28.6003 | -142.1447 | 132.2676 | 0 | -138.132 | 131.0558
Line_1 | 0.88037 | 0.42653 | 0.37249 | 0.87825 | 0.42444 | 0.37047 | 10.1657 | 4.9251 | 4.3011 | 10.1411 | 4.9011 | 4.2778 | 3.75 | 2.8534 | -4.2006 | -2.401e-11 | -1.2018 | 5.5885 | 1.004 | -5.0756 | -0.62364 | -1.5815e-12 | 5.3539 | 0.7676 | -63.6747 | -60.9007 | -56.9216 | 116.3753 | 119.2167 | 123.2349 |  | 0.38188 | 1.1822 | 0.98732 | 0 | 1.1196 | 1.3186 | -48.6864 | -121.5571 | 131.5231 | 0 | -138.132 | 131.0558
Line_2 | 0.88037 | 0.42653 | 0.37249 | 0.87825 | 0.42444 | 0.37047 | 10.1657 | 4.9251 | 4.3011 | 10.1411 | 4.9011 | 4.2778 | 3.75 | 2.8534 | -4.2006 | -2.401e-11 | -1.2018 | 5.5885 | 1.004 | -5.0756 | -0.62364 | -1.5815e-12 | 5.3539 | 0.7676 | -63.6747 | -60.9007 | -56.9216 | 116.3753 | 119.2167 | 123.2349 |  | 0.38188 | 1.1822 | 0.98732 | 0 | 1.1196 | 1.3186 | -48.6864 | -121.5571 | 131.5231 | 0 | -138.132 | 131.0558

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5911 | 0.84664 | 0.73882 | 1.5889 | 0.84889 | 0.74094 | 18.3719 | 9.7762 | 8.5311 | 18.3466 | 9.8021 | 8.5556 | 2.5367 | -1.6649 | 11.6896 | -4.3525e-11 | 2.4036 | -11.1769 | 1.4868 | 11.1108 | 1.8279 | 7.1838e-13 | -10.7079 | -1.5352 | -58.9752 | 119.3333 | 123.3804 | 121.0895 | -60.7833 | -56.7651 |  | 0.16005 | 1.1492 | 1.3869 | 0 | 1.1196 | 1.3186 | -28.6003 | -142.1447 | 132.2676 | 0 | -138.132 | 131.0558
Line_1 | 0.88037 | 0.42653 | 0.37249 | 0.87825 | 0.42444 | 0.37047 | 10.1657 | 4.9251 | 4.3011 | 10.1411 | 4.9011 | 4.2778 | 3.75 | 2.8534 | -4.2006 | -2.401e-11 | -1.2018 | 5.5885 | 1.004 | -5.0756 | -0.62364 | -1.5815e-12 | 5.3539 | 0.7676 | -63.6747 | -60.9007 | -56.9216 | 116.3753 | 119.2167 | 123.2349 |  | 0.38188 | 1.1822 | 0.98732 | 0 | 1.1196 | 1.3186 | -48.6864 | -121.5571 | 131.5231 | 0 | -138.132 | 131.0558
Line_2 | 0.88037 | 0.42653 | 0.37249 | 0.87825 | 0.42444 | 0.37047 | 10.1657 | 4.9251 | 4.3011 | 10.1411 | 4.9011 | 4.2778 | 3.75 | 2.8534 | -4.2006 | -2.401e-11 | -1.2018 | 5.5885 | 1.004 | -5.0756 | -0.62364 | -1.5815e-12 | 5.3539 | 0.7676 | -63.6747 | -60.9007 | -56.9216 | 116.3753 | 119.2167 | 123.2349 |  | 0.38188 | 1.1822 | 0.98732 | 0 | 1.1196 | 1.3186 | -48.6864 | -121.5571 | 131.5231 | 0 | -138.132 | 131.0558

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.52693 | 0.28039 | 0.24469 | 0.52621 | 0.28114 | 0.24539 | 6.0845 | 3.2377 | 2.8254 | 6.0761 | 3.2463 | 2.8335 | 3.3149 | -0.72402 | 3.0846 | -3.0356 | 0.81082 | -3.0352 | 2.9544 | 3.3457 | -0.44724 | -2.784 | -3.306 | 0.4766 | -47.9503 | 130.3582 | 134.4053 | 132.1144 | -49.7584 | -45.7402 |  | 0.72978 | 1.0573 | 1.1032 | 0.67789 | 1.0486 | 1.0843 | -6.2413 | -127.431 | 126.1555 | -5.3609 | -125.9783 | 125.3358
Line_1 | 0.29157 | 0.14126 | 0.12336 | 0.29086 | 0.14057 | 0.12269 | 3.3667 | 1.6311 | 1.4245 | 3.3586 | 1.6232 | 1.4167 | 1.9594 | 0.5901 | -1.3712 | -1.5458 | -0.40541 | 1.5176 | 1.7871 | -1.6271 | 0.25336 | -1.6716 | 1.653 | -0.2383 | -52.6498 | -49.8758 | -45.8967 | 127.4003 | 130.2416 | 134.2598 |  | 0.7877 | 1.0611 | 0.97889 | 0.67789 | 1.0486 | 1.0843 | -10.2827 | -119.9421 | 123.6344 | -5.3609 | -125.9783 | 125.3358
Line_2 | 0.29157 | 0.14126 | 0.12336 | 0.29086 | 0.14057 | 0.12269 | 3.3667 | 1.6311 | 1.4245 | 3.3586 | 1.6232 | 1.4167 | 1.9594 | 0.5901 | -1.3712 | -1.5458 | -0.40541 | 1.5176 | 1.7871 | -1.6271 | 0.25336 | -1.6716 | 1.653 | -0.2383 | -52.6498 | -49.8758 | -45.8967 | 127.4003 | 130.2416 | 134.2598 |  | 0.7877 | 1.0611 | 0.97889 | 0.67789 | 1.0486 | 1.0843 | -10.2827 | -119.9421 | 123.6344 | -5.3609 | -125.9783 | 125.3358

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.52693 | 0.28039 | 0.24469 | 0.52621 | 0.28114 | 0.24539 | 6.0845 | 3.2377 | 2.8254 | 6.0761 | 3.2463 | 2.8335 | 3.3149 | -0.72402 | 3.0846 | -3.0356 | 0.81082 | -3.0352 | 2.9544 | 3.3457 | -0.44724 | -2.784 | -3.306 | 0.4766 | -47.9503 | 130.3582 | 134.4053 | 132.1144 | -49.7584 | -45.7402 |  | 0.72978 | 1.0573 | 1.1032 | 0.67789 | 1.0486 | 1.0843 | -6.2413 | -127.431 | 126.1555 | -5.3609 | -125.9783 | 125.3358
Line_1 | 0.29157 | 0.14126 | 0.12336 | 0.29086 | 0.14057 | 0.12269 | 3.3667 | 1.6311 | 1.4245 | 3.3586 | 1.6232 | 1.4167 | 1.9594 | 0.5901 | -1.3712 | -1.5458 | -0.40541 | 1.5176 | 1.7871 | -1.6271 | 0.25336 | -1.6716 | 1.653 | -0.2383 | -52.6498 | -49.8758 | -45.8967 | 127.4003 | 130.2416 | 134.2598 |  | 0.7877 | 1.0611 | 0.97889 | 0.67789 | 1.0486 | 1.0843 | -10.2827 | -119.9421 | 123.6344 | -5.3609 | -125.9783 | 125.3358
Line_2 | 0.29157 | 0.14126 | 0.12336 | 0.29086 | 0.14057 | 0.12269 | 3.3667 | 1.6311 | 1.4245 | 3.3586 | 1.6232 | 1.4167 | 1.9594 | 0.5901 | -1.3712 | -1.5458 | -0.40541 | 1.5176 | 1.7871 | -1.6271 | 0.25336 | -1.6716 | 1.653 | -0.2383 | -52.6498 | -49.8758 | -45.8967 | 127.4003 | 130.2416 | 134.2598 |  | 0.7877 | 1.0611 | 0.97889 | 0.67789 | 1.0486 | 1.0843 | -10.2827 | -119.9421 | 123.6344 | -5.3609 | -125.9783 | 125.3358

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44727 | 3.6933 | 3.7388 | 0.4497 | 3.6936 | 3.7382 | 5.1647 | 42.6463 | 43.172 | 5.1927 | 42.6502 | 43.1647 | 0.88546 | 7.0926 | 7.2708 | -0.7829 | 8.707e-11 | 1.1431e-10 | 7.7096 | 8.0357 | 8.2595 | -7.6332 | -7.7988e-11 | 1.9472e-11 | -83.4453 | -171.2901 | 15.6876 | 96.5229 | 8.7474 | -164.3485 |  | 1.5026 | 0.25133 | 0.25488 | 1.4777 | 0 | 0 | 0.0029076 | -122.7226 | 64.3303 | 0.66684 | 0 | 0
Line_1 | 0.22702 | 1.1282 | 0.92874 | 0.22485 | 1.127 | 0.92715 | 2.6214 | 13.0269 | 10.7242 | 2.5963 | 13.013 | 10.7058 | -0.031207 | 2.3387 | 1.0159 | 0.39145 | 3.523e-11 | 2.4555e-11 | -3.6321 | -0.21161 | 1.9961 | 3.8166 | -5.5509e-12 | -1.4974e-11 | 96.5512 | 155.7594 | 56.7844 | -83.4771 | -24.1488 | -123.3066 |  | 1.3856 | 0.18026 | 0.20885 | 1.4777 | 0 | 0 | 6.0589 | 150.5891 | 119.811 | 0.66684 | 0 | 0
Line_2 | 0.22702 | 1.1282 | 0.92874 | 0.22485 | 1.127 | 0.92715 | 2.6214 | 13.0269 | 10.7242 | 2.5963 | 13.013 | 10.7058 | -0.031207 | 2.3387 | 1.0159 | 0.39145 | 3.523e-11 | 2.4555e-11 | -3.6321 | -0.21161 | 1.9961 | 3.8166 | -5.5509e-12 | -1.4974e-11 | 96.5512 | 155.7594 | 56.7844 | -83.4771 | -24.1488 | -123.3066 |  | 1.3856 | 0.18026 | 0.20885 | 1.4777 | 0 | 0 | 6.0589 | 150.5891 | 119.811 | 0.66684 | 0 | 0

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.44727 | 3.6933 | 3.7388 | 0.4497 | 3.6936 | 3.7382 | 5.1647 | 42.6463 | 43.172 | 5.1927 | 42.6502 | 43.1647 | 0.88546 | 7.0926 | 7.2708 | -0.7829 | 8.707e-11 | 1.1431e-10 | 7.7096 | 8.0357 | 8.2595 | -7.6332 | -7.7988e-11 | 1.9472e-11 | -83.4453 | -171.2901 | 15.6876 | 96.5229 | 8.7474 | -164.3485 |  | 1.5026 | 0.25133 | 0.25488 | 1.4777 | 0 | 0 | 0.0029076 | -122.7226 | 64.3303 | 0.66684 | 0 | 0
Line_1 | 0.22702 | 1.1282 | 0.92874 | 0.22485 | 1.127 | 0.92715 | 2.6214 | 13.0269 | 10.7242 | 2.5963 | 13.013 | 10.7058 | -0.031207 | 2.3387 | 1.0159 | 0.39145 | 3.523e-11 | 2.4555e-11 | -3.6321 | -0.21161 | 1.9961 | 3.8166 | -5.5509e-12 | -1.4974e-11 | 96.5512 | 155.7594 | 56.7844 | -83.4771 | -24.1488 | -123.3066 |  | 1.3856 | 0.18026 | 0.20885 | 1.4777 | 0 | 0 | 6.0589 | 150.5891 | 119.811 | 0.66684 | 0 | 0
Line_2 | 0.22702 | 1.1282 | 0.92874 | 0.22485 | 1.127 | 0.92715 | 2.6214 | 13.0269 | 10.7242 | 2.5963 | 13.013 | 10.7058 | -0.031207 | 2.3387 | 1.0159 | 0.39145 | 3.523e-11 | 2.4555e-11 | -3.6321 | -0.21161 | 1.9961 | 3.8166 | -5.5509e-12 | -1.4974e-11 | 96.5512 | 155.7594 | 56.7844 | -83.4771 | -24.1488 | -123.3066 |  | 1.3856 | 0.18026 | 0.20885 | 1.4777 | 0 | 0 | 6.0589 | 150.5891 | 119.811 | 0.66684 | 0 | 0

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.082229 | 0.79642 | 0.74887 | 0.082632 | 0.79683 | 0.74839 | 0.9495 | 9.1963 | 8.6472 | 0.95415 | 9.201 | 8.6416 | 1.1929 | 7.961 | 4.0801 | -1.1929 | -7.6377 | -3.7785 | 0.23142 | 2.49 | 6.9704 | -0.24077 | -2.1097 | -6.6385 | -9.4006 | -138.3885 | 46.7025 | 170.0086 | 41.6723 | -133.3592 |  | 1.2798 | 0.90703 | 0.93403 | 1.2754 | 0.86118 | 0.88392 | 1.5782 | -121.0204 | 106.3599 | 1.42 | -122.8867 | 106.9928
Line_1 | 0.041795 | 0.40772 | 0.37489 | 0.041316 | 0.40717 | 0.37422 | 0.48261 | 4.7079 | 4.3289 | 0.47707 | 4.7016 | 4.3212 | -0.57598 | 1.4568 | 3.5118 | 0.59643 | -1.1253 | -3.3195 | -0.14376 | 3.8922 | 2.1931 | 0.12039 | -3.8894 | -1.8895 | 169.0619 | 163.162 | 77.4208 | -9.9914 | -16.7495 | -102.6564 |  | 1.2301 | 0.88274 | 0.95644 | 1.2754 | 0.86118 | 0.88392 | 3.0757 | -127.3579 | 109.4053 | 1.42 | -122.8867 | 106.9928
Line_2 | 0.041795 | 0.40772 | 0.37489 | 0.041316 | 0.40717 | 0.37422 | 0.48261 | 4.7079 | 4.3289 | 0.47707 | 4.7016 | 4.3212 | -0.57598 | 1.4568 | 3.5118 | 0.59643 | -1.1253 | -3.3195 | -0.14376 | 3.8922 | 2.1931 | 0.12039 | -3.8894 | -1.8895 | 169.0619 | 163.162 | 77.4208 | -9.9914 | -16.7495 | -102.6564 |  | 1.2301 | 0.88274 | 0.95644 | 1.2754 | 0.86118 | 0.88392 | 3.0757 | -127.3579 | 109.4053 | 1.42 | -122.8867 | 106.9928

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.082229 | 0.79642 | 0.74887 | 0.082632 | 0.79683 | 0.74839 | 0.9495 | 9.1963 | 8.6472 | 0.95415 | 9.201 | 8.6416 | 1.1929 | 7.961 | 4.0801 | -1.1929 | -7.6377 | -3.7785 | 0.23142 | 2.49 | 6.9704 | -0.24077 | -2.1097 | -6.6385 | -9.4006 | -138.3885 | 46.7025 | 170.0086 | 41.6723 | -133.3592 |  | 1.2798 | 0.90703 | 0.93403 | 1.2754 | 0.86118 | 0.88392 | 1.5782 | -121.0204 | 106.3599 | 1.42 | -122.8867 | 106.9928
Line_1 | 0.041795 | 0.40772 | 0.37489 | 0.041316 | 0.40717 | 0.37422 | 0.48261 | 4.7079 | 4.3289 | 0.47707 | 4.7016 | 4.3212 | -0.57598 | 1.4568 | 3.5118 | 0.59643 | -1.1253 | -3.3195 | -0.14376 | 3.8922 | 2.1931 | 0.12039 | -3.8894 | -1.8895 | 169.0619 | 163.162 | 77.4208 | -9.9914 | -16.7495 | -102.6564 |  | 1.2301 | 0.88274 | 0.95644 | 1.2754 | 0.86118 | 0.88392 | 3.0757 | -127.3579 | 109.4053 | 1.42 | -122.8867 | 106.9928
Line_2 | 0.041795 | 0.40772 | 0.37489 | 0.041316 | 0.40717 | 0.37422 | 0.48261 | 4.7079 | 4.3289 | 0.47707 | 4.7016 | 4.3212 | -0.57598 | 1.4568 | 3.5118 | 0.59643 | -1.1253 | -3.3195 | -0.14376 | 3.8922 | 2.1931 | 0.12039 | -3.8894 | -1.8895 | 169.0619 | 163.162 | 77.4208 | -9.9914 | -16.7495 | -102.6564 |  | 1.2301 | 0.88274 | 0.95644 | 1.2754 | 0.86118 | 0.88392 | 3.0757 | -127.3579 | 109.4053 | 1.42 | -122.8867 | 106.9928

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.49666 | 3.1507 | 3.1075 | 0.49857 | 3.1513 | 3.1066 | 5.7349 | 36.3811 | 35.8826 | 5.757 | 36.3881 | 35.872 | 3.5444 | 9.907 | 9.6477 | -3.3007 | -1.0718e-10 | -6.2672e-12 | 6.7889 | 5.8401 | 5.7131 | -6.6741 | -7.9793e-11 | -1.3356e-10 | -64.4038 | -164.2283 | 24.947 | 115.4873 | 15.8089 | -155.0884 |  | 1.3354 | 0.31611 | 0.31248 | 1.2933 | 0 | 0 | -1.9726 | -133.7092 | 55.5799 | -0.82731 | 0 | 0
Line_1 | 0.25095 | 0.96786 | 0.61978 | 0.24929 | 0.96703 | 0.61854 | 2.8977 | 11.1758 | 7.1567 | 2.8785 | 11.1663 | 7.1423 | -0.97899 | 3.09 | 0.84931 | 1.6503 | -1.5658e-11 | -1.6655e-11 | -3.1155 | -0.72453 | 1.7615 | 3.3371 | -3.7897e-11 | -2.0768e-11 | 115.4093 | 164.8358 | 61.0599 | -64.5127 | -15.0761 | -119.0472 |  | 1.127 | 0.28399 | 0.27325 | 1.2933 | 0 | 0 | 7.9649 | 151.6396 | 125.3192 | -0.82731 | 0 | 0
Line_2 | 0.25095 | 0.96786 | 0.61978 | 0.24929 | 0.96703 | 0.61854 | 2.8977 | 11.1758 | 7.1567 | 2.8785 | 11.1663 | 7.1423 | -0.97899 | 3.09 | 0.84931 | 1.6503 | -1.5658e-11 | -1.6655e-11 | -3.1155 | -0.72453 | 1.7615 | 3.3371 | -3.7897e-11 | -2.0768e-11 | 115.4093 | 164.8358 | 61.0599 | -64.5127 | -15.0761 | -119.0472 |  | 1.127 | 0.28399 | 0.27325 | 1.2933 | 0 | 0 | 7.9649 | 151.6396 | 125.3192 | -0.82731 | 0 | 0

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.49666 | 3.1507 | 3.1075 | 0.49857 | 3.1513 | 3.1066 | 5.7349 | 36.3811 | 35.8826 | 5.757 | 36.3881 | 35.872 | 3.5444 | 9.907 | 9.6477 | -3.3007 | -1.0718e-10 | -6.2672e-12 | 6.7889 | 5.8401 | 5.7131 | -6.6741 | -7.9793e-11 | -1.3356e-10 | -64.4038 | -164.2283 | 24.947 | 115.4873 | 15.8089 | -155.0884 |  | 1.3354 | 0.31611 | 0.31248 | 1.2933 | 0 | 0 | -1.9726 | -133.7092 | 55.5799 | -0.82731 | 0 | 0
Line_1 | 0.25095 | 0.96786 | 0.61978 | 0.24929 | 0.96703 | 0.61854 | 2.8977 | 11.1758 | 7.1567 | 2.8785 | 11.1663 | 7.1423 | -0.97899 | 3.09 | 0.84931 | 1.6503 | -1.5658e-11 | -1.6655e-11 | -3.1155 | -0.72453 | 1.7615 | 3.3371 | -3.7897e-11 | -2.0768e-11 | 115.4093 | 164.8358 | 61.0599 | -64.5127 | -15.0761 | -119.0472 |  | 1.127 | 0.28399 | 0.27325 | 1.2933 | 0 | 0 | 7.9649 | 151.6396 | 125.3192 | -0.82731 | 0 | 0
Line_2 | 0.25095 | 0.96786 | 0.61978 | 0.24929 | 0.96703 | 0.61854 | 2.8977 | 11.1758 | 7.1567 | 2.8785 | 11.1663 | 7.1423 | -0.97899 | 3.09 | 0.84931 | 1.6503 | -1.5658e-11 | -1.6655e-11 | -3.1155 | -0.72453 | 1.7615 | 3.3371 | -3.7897e-11 | -2.0768e-11 | 115.4093 | 164.8358 | 61.0599 | -64.5127 | -15.0761 | -119.0472 |  | 1.127 | 0.28399 | 0.27325 | 1.2933 | 0 | 0 | 7.9649 | 151.6396 | 125.3192 | -0.82731 | 0 | 0

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.2172 | 0.77046 | 0.79373 | 0.21792 | 0.77086 | 0.79315 | 2.508 | 8.8965 | 9.1653 | 2.5164 | 8.9011 | 9.1585 | 1.6355 | 6.4849 | 3.9343 | -1.5897 | -5.8989 | -3.2974 | 2.3144 | 3.3977 | 6.098 | -2.2971 | -3.0449 | -5.7233 | -55.3178 | -147.6363 | 48.3981 | 124.5709 | 32.4187 | -131.6453 |  | 1.13 | 0.82292 | 0.7918 | 1.1101 | 0.7458 | 0.72122 | -0.56506 | -119.9842 | 105.5689 | -0.11351 | -120.2793 | 108.4067
Line_1 | 0.1096 | 0.26899 | 0.23085 | 0.10896 | 0.26865 | 0.23022 | 1.2656 | 3.106 | 2.6657 | 1.2582 | 3.1021 | 2.6584 | -0.67798 | 1.0652 | 2.0308 | 0.79483 | -0.75865 | -1.819 | -1.1211 | 2.0984 | 0.81515 | 1.1486 | -2.1856 | -0.60601 | 124.4774 | 168.74 | 90.0346 | -55.4291 | -11.137 | -90.0195 |  | 1.0352 | 0.75764 | 0.82092 | 1.1101 | 0.7458 | 0.72122 | 3.3129 | -128.1735 | 111.905 | -0.11351 | -120.2793 | 108.4067
Line_2 | 0.1096 | 0.26899 | 0.23085 | 0.10896 | 0.26865 | 0.23022 | 1.2656 | 3.106 | 2.6657 | 1.2582 | 3.1021 | 2.6584 | -0.67798 | 1.0652 | 2.0308 | 0.79483 | -0.75865 | -1.819 | -1.1211 | 2.0984 | 0.81515 | 1.1486 | -2.1856 | -0.60601 | 124.4774 | 168.74 | 90.0346 | -55.4291 | -11.137 | -90.0195 |  | 1.0352 | 0.75764 | 0.82092 | 1.1101 | 0.7458 | 0.72122 | 3.3129 | -128.1735 | 111.905 | -0.11351 | -120.2793 | 108.4067

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.2172 | 0.77046 | 0.79373 | 0.21792 | 0.77086 | 0.79315 | 2.508 | 8.8965 | 9.1653 | 2.5164 | 8.9011 | 9.1585 | 1.6355 | 6.4849 | 3.9343 | -1.5897 | -5.8989 | -3.2974 | 2.3144 | 3.3977 | 6.098 | -2.2971 | -3.0449 | -5.7233 | -55.3178 | -147.6363 | 48.3981 | 124.5709 | 32.4187 | -131.6453 |  | 1.13 | 0.82292 | 0.7918 | 1.1101 | 0.7458 | 0.72122 | -0.56506 | -119.9842 | 105.5689 | -0.11351 | -120.2793 | 108.4067
Line_1 | 0.1096 | 0.26899 | 0.23085 | 0.10896 | 0.26865 | 0.23022 | 1.2656 | 3.106 | 2.6657 | 1.2582 | 3.1021 | 2.6584 | -0.67798 | 1.0652 | 2.0308 | 0.79483 | -0.75865 | -1.819 | -1.1211 | 2.0984 | 0.81515 | 1.1486 | -2.1856 | -0.60601 | 124.4774 | 168.74 | 90.0346 | -55.4291 | -11.137 | -90.0195 |  | 1.0352 | 0.75764 | 0.82092 | 1.1101 | 0.7458 | 0.72122 | 3.3129 | -128.1735 | 111.905 | -0.11351 | -120.2793 | 108.4067
Line_2 | 0.1096 | 0.26899 | 0.23085 | 0.10896 | 0.26865 | 0.23022 | 1.2656 | 3.106 | 2.6657 | 1.2582 | 3.1021 | 2.6584 | -0.67798 | 1.0652 | 2.0308 | 0.79483 | -0.75865 | -1.819 | -1.1211 | 2.0984 | 0.81515 | 1.1486 | -2.1856 | -0.60601 | 124.4774 | 168.74 | 90.0346 | -55.4291 | -11.137 | -90.0195 |  | 1.0352 | 0.75764 | 0.82092 | 1.1101 | 0.7458 | 0.72122 | 3.3129 | -128.1735 | 111.905 | -0.11351 | -120.2793 | 108.4067