## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3036 | 3.3036 | 0 | 0 | 114.4404 | 114.4404 | 37.7713 | -20.7457 | 43.3355 | -24.018 | -70.8485 | 109.1515 | 0.50232 | 0.27733 | -21.9239 | -21.6675
Line_1 | 4.0718 | 4.0718 | 7.8074 | 0 | 141.0522 | 141.0522 | -1e-07 | 25.8644 | -1e-07 | 29.3462 | 109.7241 | -70.2759 | 0 | 0.27733 | 0 | -21.6675
Line_2 | 0.76909 | 0.76909 | 0 | 0 | 26.6421 | 26.6421 | 6.0414 | -5.1187 | 6.3751 | -5.3281 | -67.816 | 112.184 | 0.32967 | 0.27733 | -21.2767 | -21.6675

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.3036 | 3.3036 | 0 | 0 | 114.4404 | 114.4404 | 37.7713 | -20.7457 | 43.3355 | -24.018 | -70.8485 | 109.1515 | 0.50232 | 0.27733 | -21.9239 | -21.6675
Line_1 | 4.0718 | 4.0718 | 7.8074 | 0 | 141.0522 | 141.0522 | -1e-07 | 25.8644 | -1e-07 | 29.3462 | 109.7241 | -70.2759 | 0 | 0.27733 | 0 | -21.6675
Line_2 | 0.76909 | 0.76909 | 0 | 0 | 26.6421 | 26.6421 | 6.0414 | -5.1187 | 6.3751 | -5.3281 | -67.816 | 112.184 | 0.32967 | 0.27733 | -21.2767 | -21.6675

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.77289 | 0.77289 | 0 | 0 | 26.7736 | 26.7736 | 20.4887 | -19.5569 | 16.8303 | -15.773 | -45.3926 | 134.6074 | 0.99034 | 0.93842 | -5.9915 | -6.5057
Line_1 | 1.057 | 1.057 | 2.0668 | 0 | 36.615 | 36.615 | -23.4304 | 25.1732 | -21.4091 | 23.3865 | 130.6015 | -49.3985 | 0.86682 | 0.93842 | -6.9796 | -6.5057
Line_2 | 0.29104 | 0.29104 | 0 | 0 | 10.0818 | 10.0818 | 5.7485 | -5.6164 | 7.7635 | -7.6135 | -60.0901 | 119.9099 | 0.95817 | 0.93842 | -6.6085 | -6.5057

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.77289 | 0.77289 | 0 | 0 | 26.7736 | 26.7736 | 20.4887 | -19.5569 | 16.8303 | -15.773 | -45.3926 | 134.6074 | 0.99034 | 0.93842 | -5.9915 | -6.5057
Line_1 | 1.057 | 1.057 | 2.0668 | 0 | 36.615 | 36.615 | -23.4304 | 25.1732 | -21.4091 | 23.3865 | 130.6015 | -49.3985 | 0.86682 | 0.93842 | -6.9796 | -6.5057
Line_2 | 0.29104 | 0.29104 | 0 | 0 | 10.0818 | 10.0818 | 5.7485 | -5.6164 | 7.7635 | -7.6135 | -60.0901 | 119.9099 | 0.95817 | 0.93842 | -6.6085 | -6.5057

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.6307 | 2.6307 | 0 | 0 | 91.1286 | 91.1286 | 45.9418 | -25.214 | 27.0858 | -14.8368 | -57.966 | 122.034 | 0.58524 | 0.32103 | -27.4438 | -27.4919
Line_1 | 3.1965 | 3.1965 | 5.555 | 0 | 110.73 | 110.73 | -1e-07 | 30.6038 | -1e-07 | 18.0852 | 121.9273 | -58.0727 | 0 | 0.32103 | 0 | -27.4919
Line_2 | 0.56587 | 0.56587 | 0 | 0 | 19.6023 | 19.6023 | 6.3489 | -5.3898 | 3.8151 | -3.2484 | -58.5686 | 121.4314 | 0.37786 | 0.32103 | -27.5665 | -27.4919

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.76941 | 0.76941 | 0 | 0 | 26.6531 | 26.6531 | 18.1535 | -16.3803 | 15.0311 | -13.9833 | -46.4658 | 133.5342 | 0.88427 | 0.80805 | -6.841 | -5.9797
Line_1 | 0.93491 | 0.93491 | 1.6247 | 0 | 32.3861 | 32.3861 | -17.2541 | 19.872 | -15.481 | 17.028 | 133.4275 | -46.5725 | 0.71577 | 0.80805 | -4.6729 | -5.9797
Line_2 | 0.1655 | 0.1655 | 0 | 0 | 5.7333 | 5.7333 | 3.5737 | -3.4917 | 3.0933 | -3.0448 | -47.0684 | 132.9316 | 0.8244 | 0.80805 | -6.1904 | -5.9797

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34465 | 2.8163 | 2.9394 | 0.34465 | 2.8163 | 2.9394 | 3.9797 | 32.5201 | 33.9408 | 3.9797 | 32.5201 | 33.9408 | -2.8467 | 27.5894 | -9.8021 | 2.9085 | -23.4649 | 14.2948 | -3.6108 | 3.3833 | 16.3211 | 3.6809 | 1.2964 | -11.2236 | 130.3426 | -157.3314 | 16.2542 | -49.6574 | 22.6686 | -163.7458 | 1.1554 | 0.85474 | 0.56093 | 1.1788 | 0.72265 | 0.53548 | 2.0909 | -150.3401 | 137.2424 | 2.0284 | -160.4937 | 158.117
Line_1 | 0.19448 | 3.4668 | 3.5514 | 0.19448 | 3.4668 | 3.5514 | 2.2456 | 40.0309 | 41.0075 | 2.2456 | 40.0309 | 41.0075 | 1.8069 | -22.6769 | 23.5803 | -1.7872 | 28.9265 | -17.0221 | 1.975 | 7.4181 | -6.4306 | -1.9527 | -0.32717 | 13.8717 | -45.5053 | 20.1544 | -162.7055 | 134.4947 | -159.8456 | 17.2945 | 1.192 | 0.59602 | 0.59602 | 1.1788 | 0.72265 | 0.53548 | 2.0403 | -177.9597 | -177.9597 | 2.0284 | -160.4937 | 158.117
Line_2 | 0.15134 | 0.66475 | 0.6148 | 0.15134 | 0.66475 | 0.6148 | 1.7476 | 7.6758 | 7.0991 | 1.7476 | 7.6758 | 7.0991 | 1.1332 | 5.6914 | -2.5307 | -1.1212 | -5.4616 | 2.7272 | 1.7417 | 1.2299 | 2.8712 | -1.7282 | -0.96922 | -2.6482 | -54.9959 | -170.5566 | 22.2743 | 125.0041 | 9.4434 | -157.7257 | 1.189 | 0.75859 | 0.53912 | 1.1788 | 0.72265 | 0.53548 | 1.9557 | -158.3623 | 153.6676 | 2.0284 | -160.4937 | 158.117

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.34465 | 2.8163 | 2.9394 | 0.34465 | 2.8163 | 2.9394 | 3.9797 | 32.5201 | 33.9408 | 3.9797 | 32.5201 | 33.9408 | -2.8467 | 27.5894 | -9.8021 | 2.9085 | -23.4649 | 14.2948 | -3.6108 | 3.3833 | 16.3211 | 3.6809 | 1.2964 | -11.2236 | 130.3426 | -157.3314 | 16.2542 | -49.6574 | 22.6686 | -163.7458 | 1.1554 | 0.85474 | 0.56093 | 1.1788 | 0.72265 | 0.53548 | 2.0909 | -150.3401 | 137.2424 | 2.0284 | -160.4937 | 158.117
Line_1 | 0.19448 | 3.4668 | 3.5514 | 0.19448 | 3.4668 | 3.5514 | 2.2456 | 40.0309 | 41.0075 | 2.2456 | 40.0309 | 41.0075 | 1.8069 | -22.6769 | 23.5803 | -1.7872 | 28.9265 | -17.0221 | 1.975 | 7.4181 | -6.4306 | -1.9527 | -0.32717 | 13.8717 | -45.5053 | 20.1544 | -162.7055 | 134.4947 | -159.8456 | 17.2945 | 1.192 | 0.59602 | 0.59602 | 1.1788 | 0.72265 | 0.53548 | 2.0403 | -177.9597 | -177.9597 | 2.0284 | -160.4937 | 158.117
Line_2 | 0.15134 | 0.66475 | 0.6148 | 0.15134 | 0.66475 | 0.6148 | 1.7476 | 7.6758 | 7.0991 | 1.7476 | 7.6758 | 7.0991 | 1.1332 | 5.6914 | -2.5307 | -1.1212 | -5.4616 | 2.7272 | 1.7417 | 1.2299 | 2.8712 | -1.7282 | -0.96922 | -2.6482 | -54.9959 | -170.5566 | 22.2743 | 125.0041 | 9.4434 | -157.7257 | 1.189 | 0.75859 | 0.53912 | 1.1788 | 0.72265 | 0.53548 | 1.9557 | -158.3623 | 153.6676 | 2.0284 | -160.4937 | 158.117

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26375 | 1.2082 | 1.1737 | 0.26375 | 1.2082 | 1.1737 | 3.0455 | 13.9508 | 13.5526 | 3.0455 | 13.9508 | 13.5526 | -1.7236 | 14.6366 | 0.36638 | 1.7598 | -13.8776 | 0.34995 | -3.0377 | 0.70931 | 11.719 | 3.0787 | 0.15191 | -10.9062 | 120.8148 | -135.4144 | 31.9789 | -59.1852 | 44.5856 | -148.0211 | 1.1468 | 1.0504 | 0.86513 | 1.1644 | 0.99481 | 0.80515 | 1.244 | -132.6399 | 120.1882 | 1.0629 | -136.0415 | 123.8167
Line_1 | 0.14172 | 1.5139 | 1.518 | 0.14172 | 1.5139 | 1.518 | 1.6364 | 17.4815 | 17.5279 | 1.6364 | 17.4815 | 17.5279 | 1.1337 | -16.1122 | 1.4292 | -1.1232 | 17.3041 | -0.23098 | 1.5511 | -0.38203 | -12.7512 | -1.5392 | 1.7343 | 14.1107 | -52.8182 | 38.235 | -147.1211 | 127.1818 | -141.765 | 32.8789 | 1.174 | 0.92193 | 0.73203 | 1.1644 | 0.99481 | 0.80515 | 1.0196 | -140.4067 | 129.274 | 1.0629 | -136.0415 | 123.8167
Line_2 | 0.1239 | 0.3405 | 0.34491 | 0.1239 | 0.3405 | 0.34491 | 1.4307 | 3.9318 | 3.9827 | 1.4307 | 3.9318 | 3.9827 | 0.64456 | 3.4868 | 0.18083 | -0.63657 | -3.4265 | -0.11897 | 1.5486 | 1.9546 | 3.2746 | -1.5395 | -1.8862 | -3.2044 | -66.4724 | -164.8737 | 35.9428 | 113.5276 | 15.1263 | -144.0572 | 1.1724 | 1.0167 | 0.82347 | 1.1644 | 0.99481 | 0.80515 | 0.92914 | -135.5993 | 122.7821 | 1.0629 | -136.0415 | 123.8167

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26375 | 1.2082 | 1.1737 | 0.26375 | 1.2082 | 1.1737 | 3.0455 | 13.9508 | 13.5526 | 3.0455 | 13.9508 | 13.5526 | -1.7236 | 14.6366 | 0.36638 | 1.7598 | -13.8776 | 0.34995 | -3.0377 | 0.70931 | 11.719 | 3.0787 | 0.15191 | -10.9062 | 120.8148 | -135.4144 | 31.9789 | -59.1852 | 44.5856 | -148.0211 | 1.1468 | 1.0504 | 0.86513 | 1.1644 | 0.99481 | 0.80515 | 1.244 | -132.6399 | 120.1882 | 1.0629 | -136.0415 | 123.8167
Line_1 | 0.14172 | 1.5139 | 1.518 | 0.14172 | 1.5139 | 1.518 | 1.6364 | 17.4815 | 17.5279 | 1.6364 | 17.4815 | 17.5279 | 1.1337 | -16.1122 | 1.4292 | -1.1232 | 17.3041 | -0.23098 | 1.5511 | -0.38203 | -12.7512 | -1.5392 | 1.7343 | 14.1107 | -52.8182 | 38.235 | -147.1211 | 127.1818 | -141.765 | 32.8789 | 1.174 | 0.92193 | 0.73203 | 1.1644 | 0.99481 | 0.80515 | 1.0196 | -140.4067 | 129.274 | 1.0629 | -136.0415 | 123.8167
Line_2 | 0.1239 | 0.3405 | 0.34491 | 0.1239 | 0.3405 | 0.34491 | 1.4307 | 3.9318 | 3.9827 | 1.4307 | 3.9318 | 3.9827 | 0.64456 | 3.4868 | 0.18083 | -0.63657 | -3.4265 | -0.11897 | 1.5486 | 1.9546 | 3.2746 | -1.5395 | -1.8862 | -3.2044 | -66.4724 | -164.8737 | 35.9428 | 113.5276 | 15.1263 | -144.0572 | 1.1724 | 1.0167 | 0.82347 | 1.1644 | 0.99481 | 0.80515 | 0.92914 | -135.5993 | 122.7821 | 1.0629 | -136.0415 | 123.8167

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.14068 | 2.2375 | 2.3511 | 0.14068 | 2.2375 | 2.3511 | 1.6245 | 25.8369 | 27.1481 | 1.6245 | 25.8369 | 27.1481 | -1.6231 | 22.5203 | -0.019694 | 1.6429 | -17.5218 | 5.5385 | -0.15684 | -0.52064 | 13.7841 | 0.16852 | 3.4745 | -10.5228 | 176.1521 | -146.6212 | 31.3043 | -3.8479 | 33.3788 | -148.6957 | 1.0038 | 0.87187 | 0.50774 | 1.0166 | 0.69137 | 0.43802 | 1.6715 | -147.9456 | 121.3861 | 2.0088 | -157.8373 | 149.0637
Line_1 | 0.088507 | 2.7229 | 2.7871 | 0.088507 | 2.7229 | 2.7871 | 1.022 | 31.441 | 32.1826 | 1.022 | 31.441 | 32.1826 | 1.0131 | -14.0477 | 14.5542 | -1.0053 | 21.4498 | -6.7988 | 0.26704 | 7.8991 | -7.7655 | -0.26242 | -3.5248 | 12.3486 | -12.6212 | 31.4946 | -149.7721 | 167.3788 | -148.5054 | 30.2279 | 1.0252 | 0.51259 | 0.51259 | 1.0166 | 0.69137 | 0.43802 | 2.1453 | -177.8547 | -177.8547 | 2.0088 | -157.8373 | 149.0637
Line_2 | 0.054898 | 0.49207 | 0.43864 | 0.054898 | 0.49207 | 0.43864 | 0.6339 | 5.682 | 5.065 | 0.6339 | 5.682 | 5.065 | 0.64057 | 4.1698 | -1.0682 | -0.63756 | -3.928 | 1.2602 | -0.092125 | 0.092595 | 1.9394 | 0.093903 | 0.050265 | -1.8258 | 10.3873 | -157.1042 | 24.4491 | -169.6127 | 22.8958 | -155.5509 | 1.0209 | 0.73405 | 0.43713 | 1.0166 | 0.69137 | 0.43802 | 2.2033 | -155.8321 | 143.2941 | 2.0088 | -157.8373 | 149.0637

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064934 | 1.0328 | 1.0852 | 0.064934 | 1.0328 | 1.0852 | 0.7498 | 11.9253 | 12.5306 | 0.7498 | 11.9253 | 12.5306 | -0.74591 | 11.3062 | 2.3283 | 0.75012 | -10.2413 | -1.1526 | 0.070648 | 0.82643 | 9.4403 | -0.06816 | -0.19713 | -8.7455 | -173.8109 | -136.5841 | 41.3413 | 6.1891 | 43.4159 | -138.6587 | 0.99927 | 0.95061 | 0.77596 | 1.0046 | 0.85895 | 0.70397 | 0.77863 | -132.4035 | 117.4865 | 0.99722 | -135.4814 | 123.8333
Line_1 | 0.040852 | 1.2568 | 1.2864 | 0.040852 | 1.2568 | 1.2864 | 0.47172 | 14.512 | 14.8543 | 0.47172 | 14.512 | 14.8543 | 0.47461 | -10.8711 | 0.48087 | -0.47294 | 12.4481 | 1.1714 | 0.030585 | 0.28236 | -9.4148 | -0.0296 | 0.64954 | 10.3912 | -2.5841 | 41.5316 | -139.7351 | 177.4159 | -138.4684 | 40.2649 | 1.0082 | 0.74937 | 0.63463 | 1.0046 | 0.85895 | 0.70397 | 1.1031 | -139.9562 | 133.1889 | 0.99722 | -135.4814 | 123.8333
Line_2 | 0.025339 | 0.22712 | 0.20246 | 0.025339 | 0.22712 | 0.20246 | 0.29259 | 2.6226 | 2.3378 | 0.29259 | 2.6226 | 2.3378 | 0.27783 | 2.2583 | 0.059675 | -0.27718 | -2.2068 | -0.018751 | -0.097381 | 0.48284 | 1.6698 | 0.09776 | -0.45241 | -1.6456 | 20.4244 | -147.0671 | 34.4862 | -159.5756 | 32.9329 | -145.5138 | 1.0062 | 0.88055 | 0.71472 | 1.0046 | 0.85895 | 0.70397 | 1.1082 | -134.9983 | 122.4394 | 0.99722 | -135.4814 | 123.8333

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.8804 | 0.68635 | 0.55959 | 1.8786 | 0.6879 | 0.56132 | 21.7134 | 7.9253 | 6.4616 | 21.6927 | 7.9432 | 6.4816 | 9.2935 | -9.4151 | 7.263 | -6.0523 | 9.3297 | -7.5805 | 7.8431 | 4.3298 | -0.092716 | -5.0936 | -4.5195 | 0.22247 | -69.005 | 84.0592 | 130.114 | 110.9918 | -95.8655 | -49.9358 |  | 0.56006 | 1.3076 | 1.1241 | 0.36466 | 1.3051 | 1.1701 | -28.8429 | -120.6372 | 129.3826 | -28.9242 | -121.712 | 128.3831
Line_1 | 2.7057 | 0.55934 | 0.38191 | 2.708 | 0.55725 | 0.37962 | 31.2432 | 6.4587 | 4.4099 | 31.2688 | 6.4346 | 4.3834 | 1.1249e-10 | 7.846 | -5.0302 | 8.9193 | -8.1123 | 4.4703 | -9.6107e-11 | -3.1207 | -2.9936 | 7.1035 | 2.1715 | 2.5142 | 112.5536 | -106.629 | -80.9792 | -67.4588 | 73.2737 | 99.0284 |  | 0 | 1.3074 | 1.3274 | 0.36466 | 1.3051 | 1.1701 | 0 | -128.3191 | 129.779 | -28.9242 | -121.712 | 128.3831
Line_2 | 0.83325 | 0.17719 | 0.30768 | 0.83155 | 0.1755 | 0.30664 | 9.6215 | 2.0461 | 3.5527 | 9.6019 | 2.0265 | 3.5407 | 4.2201 | 1.4651 | -2.712 | -2.8671 | -1.2174 | 3.1102 | 2.9447 | -2.2585 | 2.6105 | -2.01 | 2.348 | -2.7367 | -63.9537 | -59.1512 | -10.5216 | 116.0433 | 120.8813 | 169.728 |  | 0.53483 | 1.3157 | 1.0595 | 0.36466 | 1.3051 | 1.1701 | -29.0466 | -116.1803 | 125.5712 | -28.9242 | -121.712 | 128.3831

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.8804 | 0.68635 | 0.55959 | 1.8786 | 0.6879 | 0.56132 | 21.7134 | 7.9253 | 6.4616 | 21.6927 | 7.9432 | 6.4816 | 9.2935 | -9.4151 | 7.263 | -6.0523 | 9.3297 | -7.5805 | 7.8431 | 4.3298 | -0.092716 | -5.0936 | -4.5195 | 0.22247 | -69.005 | 84.0592 | 130.114 | 110.9918 | -95.8655 | -49.9358 |  | 0.56006 | 1.3076 | 1.1241 | 0.36466 | 1.3051 | 1.1701 | -28.8429 | -120.6372 | 129.3826 | -28.9242 | -121.712 | 128.3831
Line_1 | 2.7057 | 0.55934 | 0.38191 | 2.708 | 0.55725 | 0.37962 | 31.2432 | 6.4587 | 4.4099 | 31.2688 | 6.4346 | 4.3834 | 1.1249e-10 | 7.846 | -5.0302 | 8.9193 | -8.1123 | 4.4703 | -9.6107e-11 | -3.1207 | -2.9936 | 7.1035 | 2.1715 | 2.5142 | 112.5536 | -106.629 | -80.9792 | -67.4588 | 73.2737 | 99.0284 |  | 0 | 1.3074 | 1.3274 | 0.36466 | 1.3051 | 1.1701 | 0 | -128.3191 | 129.779 | -28.9242 | -121.712 | 128.3831
Line_2 | 0.83325 | 0.17719 | 0.30768 | 0.83155 | 0.1755 | 0.30664 | 9.6215 | 2.0461 | 3.5527 | 9.6019 | 2.0265 | 3.5407 | 4.2201 | 1.4651 | -2.712 | -2.8671 | -1.2174 | 3.1102 | 2.9447 | -2.2585 | 2.6105 | -2.01 | 2.348 | -2.7367 | -63.9537 | -59.1512 | -10.5216 | 116.0433 | 120.8813 | 169.728 |  | 0.53483 | 1.3157 | 1.0595 | 0.36466 | 1.3051 | 1.1701 | -29.0466 | -116.1803 | 125.5712 | -28.9242 | -121.712 | 128.3831

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.50161 | 0.18567 | 0.29661 | 0.50101 | 0.18582 | 0.29702 | 5.792 | 2.144 | 3.425 | 5.7851 | 2.1457 | 3.4297 | 4.8997 | -2.5695 | 2.0765 | -4.63 | 2.597 | -2.1126 | 2.878 | -0.16771 | -3.2169 | -2.6911 | 0.12931 | 3.3049 | -39.2494 | 57.2156 | -179.7132 | 140.7596 | -122.6041 | 0.20183 |  | 0.98108 | 1.201 | 1.1179 | 0.92568 | 1.2118 | 1.1437 | -8.82 | -119.05 | 123.129 | -9.0739 | -119.7535 | 122.7905
Line_1 | 0.83697 | 0.17583 | 0.13616 | 0.8377 | 0.17534 | 0.13555 | 9.6645 | 2.0303 | 1.5722 | 9.6729 | 2.0247 | 1.5652 | -6.284 | 2.4731 | -1.6131 | 7.1972 | -2.4421 | 1.5149 | -4.6459 | -0.35442 | 0.9545 | 5.3269 | 0.23723 | -0.95368 | 134.4354 | -114.0104 | -25.218 | -45.5806 | 65.7949 | 154.9824 |  | 0.80862 | 1.2306 | 1.1922 | 0.92568 | 1.2118 | 1.1437 | -9.0887 | -122.1659 | 124.1688 | -9.0739 | -119.7535 | 122.7905
Line_2 | 0.34479 | 0.027984 | 0.18397 | 0.34423 | 0.028438 | 0.1837 | 3.9813 | 0.32313 | 2.1243 | 3.9748 | 0.32837 | 2.1212 | 2.7566 | 0.14489 | -0.52013 | -2.5672 | -0.15493 | 0.59773 | 2.8042 | 0.36166 | 2.325 | -2.6359 | -0.36654 | -2.3512 | -54.8112 | 173.8549 | 18.37 | 125.1703 | -6.841 | -161.4735 |  | 0.98767 | 1.2057 | 1.1215 | 0.92568 | 1.2118 | 1.1437 | -9.3211 | -117.9769 | 120.9803 | -9.0739 | -119.7535 | 122.7905

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.50161 | 0.18567 | 0.29661 | 0.50101 | 0.18582 | 0.29702 | 5.792 | 2.144 | 3.425 | 5.7851 | 2.1457 | 3.4297 | 4.8997 | -2.5695 | 2.0765 | -4.63 | 2.597 | -2.1126 | 2.878 | -0.16771 | -3.2169 | -2.6911 | 0.12931 | 3.3049 | -39.2494 | 57.2156 | -179.7132 | 140.7596 | -122.6041 | 0.20183 |  | 0.98108 | 1.201 | 1.1179 | 0.92568 | 1.2118 | 1.1437 | -8.82 | -119.05 | 123.129 | -9.0739 | -119.7535 | 122.7905
Line_1 | 0.83697 | 0.17583 | 0.13616 | 0.8377 | 0.17534 | 0.13555 | 9.6645 | 2.0303 | 1.5722 | 9.6729 | 2.0247 | 1.5652 | -6.284 | 2.4731 | -1.6131 | 7.1972 | -2.4421 | 1.5149 | -4.6459 | -0.35442 | 0.9545 | 5.3269 | 0.23723 | -0.95368 | 134.4354 | -114.0104 | -25.218 | -45.5806 | 65.7949 | 154.9824 |  | 0.80862 | 1.2306 | 1.1922 | 0.92568 | 1.2118 | 1.1437 | -9.0887 | -122.1659 | 124.1688 | -9.0739 | -119.7535 | 122.7905
Line_2 | 0.34479 | 0.027984 | 0.18397 | 0.34423 | 0.028438 | 0.1837 | 3.9813 | 0.32313 | 2.1243 | 3.9748 | 0.32837 | 2.1212 | 2.7566 | 0.14489 | -0.52013 | -2.5672 | -0.15493 | 0.59773 | 2.8042 | 0.36166 | 2.325 | -2.6359 | -0.36654 | -2.3512 | -54.8112 | 173.8549 | 18.37 | 125.1703 | -6.841 | -161.4735 |  | 0.98767 | 1.2057 | 1.1215 | 0.92568 | 1.2118 | 1.1437 | -9.3211 | -117.9769 | 120.9803 | -9.0739 | -119.7535 | 122.7905

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5192 | 0.58555 | 0.47724 | 1.518 | 0.5867 | 0.47842 | 17.5424 | 6.7614 | 5.5107 | 17.5286 | 6.7746 | 5.5243 | 9.8608 | -5.0253 | 5.0719 | -6.1758 | 4.904 | -5.2728 | 6.2202 | 5.4837 | 0.73569 | -4.1863 | -5.6516 | -0.84356 | -58.8226 | 109.9605 | 116.8267 | 121.173 | -70.0054 | -63.1483 |  | 0.66461 | 1.1001 | 0.93001 | 0.42565 | 1.1045 | 0.96661 | -26.5788 | -117.5373 | 125.08 | -24.6954 | -119.0565 | 125.9409
Line_1 | 2.0098 | 0.54287 | 0.46806 | 2.0114 | 0.54106 | 0.46625 | 23.2066 | 6.2685 | 5.4047 | 23.2262 | 6.2477 | 5.3838 | -4.3554e-11 | 5.6685 | -4.7936 | 8.4176 | -5.9526 | 4.4257 | 4.5953e-12 | -4.6026 | -3.6851 | 5.1846 | 3.4908 | 2.7376 | 123.6942 | -88.6328 | -85.7698 | -56.3254 | 91.3326 | 94.2012 |  | 0 | 1.1648 | 1.1187 | 0.42565 | 1.1045 | 0.96661 | 0 | -127.7081 | 131.7816 | -24.6954 | -119.0565 | 125.9409
Line_2 | 0.50035 | 0.18906 | 0.18642 | 0.49929 | 0.18832 | 0.1859 | 5.7775 | 2.1831 | 2.1526 | 5.7653 | 2.1745 | 2.1465 | 3.1895 | -0.71486 | -0.56443 | -2.2418 | 1.0485 | 0.8471 | 1.5549 | -2.2304 | 1.7667 | -0.99829 | 2.1608 | -1.8941 | -48.6993 | -3.3995 | 11.5626 | 131.3005 | 176.8283 | -168.1552 |  | 0.61417 | 1.0729 | 0.86159 | 0.42565 | 1.1045 | 0.96661 | -22.7099 | -111.1703 | 119.2808 | -24.6954 | -119.0565 | 125.9409

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.5192 | 0.58555 | 0.47724 | 1.518 | 0.5867 | 0.47842 | 17.5424 | 6.7614 | 5.5107 | 17.5286 | 6.7746 | 5.5243 | 9.8608 | -5.0253 | 5.0719 | -6.1758 | 4.904 | -5.2728 | 6.2202 | 5.4837 | 0.73569 | -4.1863 | -5.6516 | -0.84356 | -58.8226 | 109.9605 | 116.8267 | 121.173 | -70.0054 | -63.1483 |  | 0.66461 | 1.1001 | 0.93001 | 0.42565 | 1.1045 | 0.96661 | -26.5788 | -117.5373 | 125.08 | -24.6954 | -119.0565 | 125.9409
Line_1 | 2.0098 | 0.54287 | 0.46806 | 2.0114 | 0.54106 | 0.46625 | 23.2066 | 6.2685 | 5.4047 | 23.2262 | 6.2477 | 5.3838 | -4.3554e-11 | 5.6685 | -4.7936 | 8.4176 | -5.9526 | 4.4257 | 4.5953e-12 | -4.6026 | -3.6851 | 5.1846 | 3.4908 | 2.7376 | 123.6942 | -88.6328 | -85.7698 | -56.3254 | 91.3326 | 94.2012 |  | 0 | 1.1648 | 1.1187 | 0.42565 | 1.1045 | 0.96661 | 0 | -127.7081 | 131.7816 | -24.6954 | -119.0565 | 125.9409
Line_2 | 0.50035 | 0.18906 | 0.18642 | 0.49929 | 0.18832 | 0.1859 | 5.7775 | 2.1831 | 2.1526 | 5.7653 | 2.1745 | 2.1465 | 3.1895 | -0.71486 | -0.56443 | -2.2418 | 1.0485 | 0.8471 | 1.5549 | -2.2304 | 1.7667 | -0.99829 | 2.1608 | -1.8941 | -48.6993 | -3.3995 | 11.5626 | 131.3005 | 176.8283 | -168.1552 |  | 0.61417 | 1.0729 | 0.86159 | 0.42565 | 1.1045 | 0.96661 | -22.7099 | -111.1703 | 119.2808 | -24.6954 | -119.0565 | 125.9409

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.54276 | 0.2092 | 0.1705 | 0.54233 | 0.20961 | 0.17092 | 6.2672 | 2.4156 | 1.9688 | 6.2623 | 2.4203 | 1.9736 | 4.5515 | -1.1433 | 1.8782 | -4.0784 | 1.128 | -1.9067 | 3.2894 | 2.2112 | -0.31779 | -3.028 | -2.2359 | 0.30558 | -44.7354 | 124.0477 | 130.9139 | 135.2602 | -55.9182 | -49.0612 |  | 0.89604 | 1.0305 | 0.96758 | 0.81114 | 1.0347 | 0.97843 | -8.8798 | -118.6102 | 121.3107 | -8.1472 | -119.1485 | 121.834
Line_1 | 0.71801 | 0.19395 | 0.16722 | 0.71862 | 0.1933 | 0.16657 | 8.2909 | 2.2395 | 1.9309 | 8.2979 | 2.2321 | 1.9234 | -4.4969 | 1.6113 | -1.8815 | 5.574 | -1.6453 | 1.8296 | -3.1067 | -1.7671 | -0.56143 | 3.7726 | 1.6207 | 0.44079 | 137.7814 | -74.5456 | -71.6826 | -42.2382 | 105.4198 | 108.2884 |  | 0.65924 | 1.0678 | 1.0169 | 0.81114 | 1.0347 | 0.97843 | -7.5797 | -122.1854 | 124.9321 | -8.1472 | -119.1485 | 121.834
Line_2 | 0.17876 | 0.067544 | 0.066601 | 0.17838 | 0.067278 | 0.066414 | 2.0641 | 0.77993 | 0.76904 | 2.0597 | 0.77686 | 0.76688 | 1.6192 | -0.47494 | -0.043481 | -1.4956 | 0.51737 | 0.077155 | 0.81691 | -0.62694 | 0.73167 | -0.74457 | 0.61518 | -0.74636 | -34.6121 | 10.6877 | 25.6498 | 145.3877 | -169.0845 | -154.068 |  | 0.87863 | 1.0085 | 0.95308 | 0.81114 | 1.0347 | 0.97843 | -7.8401 | -116.4582 | 119.0508 | -8.1472 | -119.1485 | 121.834

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.54276 | 0.2092 | 0.1705 | 0.54233 | 0.20961 | 0.17092 | 6.2672 | 2.4156 | 1.9688 | 6.2623 | 2.4203 | 1.9736 | 4.5515 | -1.1433 | 1.8782 | -4.0784 | 1.128 | -1.9067 | 3.2894 | 2.2112 | -0.31779 | -3.028 | -2.2359 | 0.30558 | -44.7354 | 124.0477 | 130.9139 | 135.2602 | -55.9182 | -49.0612 |  | 0.89604 | 1.0305 | 0.96758 | 0.81114 | 1.0347 | 0.97843 | -8.8798 | -118.6102 | 121.3107 | -8.1472 | -119.1485 | 121.834
Line_1 | 0.71801 | 0.19395 | 0.16722 | 0.71862 | 0.1933 | 0.16657 | 8.2909 | 2.2395 | 1.9309 | 8.2979 | 2.2321 | 1.9234 | -4.4969 | 1.6113 | -1.8815 | 5.574 | -1.6453 | 1.8296 | -3.1067 | -1.7671 | -0.56143 | 3.7726 | 1.6207 | 0.44079 | 137.7814 | -74.5456 | -71.6826 | -42.2382 | 105.4198 | 108.2884 |  | 0.65924 | 1.0678 | 1.0169 | 0.81114 | 1.0347 | 0.97843 | -7.5797 | -122.1854 | 124.9321 | -8.1472 | -119.1485 | 121.834
Line_2 | 0.17876 | 0.067544 | 0.066601 | 0.17838 | 0.067278 | 0.066414 | 2.0641 | 0.77993 | 0.76904 | 2.0597 | 0.77686 | 0.76688 | 1.6192 | -0.47494 | -0.043481 | -1.4956 | 0.51737 | 0.077155 | 0.81691 | -0.62694 | 0.73167 | -0.74457 | 0.61518 | -0.74636 | -34.6121 | 10.6877 | 25.6498 | 145.3877 | -169.0845 | -154.068 |  | 0.87863 | 1.0085 | 0.95308 | 0.81114 | 1.0347 | 0.97843 | -7.8401 | -116.4582 | 119.0508 | -8.1472 | -119.1485 | 121.834

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.30463 | 2.901 | 2.9071 | 0.30583 | 2.9006 | 2.9071 | 3.5175 | 33.4982 | 33.5684 | 3.5315 | 33.4935 | 33.5679 | -1.332 | 15.4058 | 6.1158 | 1.2635 | -9.8058 | -2.4082 | 4.218 | 5.3763 | 18.115 | -4.3647 | -1.9963 | -11.2422 | -100.7125 | -169.372 | 28.035 | 79.4578 | 10.6567 | -151.9948 |  | 1.2575 | 0.4871 | 0.56957 | 1.2867 | 0.29877 | 0.34251 | 6.8126 | -150.1341 | 99.38 | 5.6023 | -157.8362 | 105.9147
Line_1 | 0.32943 | 3.7658 | 3.4827 | 0.32788 | 3.7659 | 3.4835 | 3.804 | 43.4836 | 40.2149 | 3.786 | 43.4853 | 40.224 | 2.5443 | 8.7171e-11 | 1.0708e-10 | -2.5988 | 12.4243 | 4.2403 | -4.671 | -8.5161e-11 | -2.6106e-11 | 4.1203 | 3.7995 | 13.1082 | 63.5599 | 5.1889 | -146.1886 | -116.6391 | -174.8404 | 33.8404 |  | 1.3983 | 0 | 0 | 1.2867 | 0.29877 | 0.34251 | 2.137 | 0 | 0 | 5.6023 | -157.8362 | 105.9147
Line_2 | 0.092181 | 0.9225 | 0.66197 | 0.091371 | 0.92155 | 0.66123 | 1.0644 | 10.6521 | 7.6438 | 1.0551 | 10.6411 | 7.6353 | -1.2483 | 4.028 | 2.126 | 1.3353 | -2.6185 | -1.8322 | -0.30867 | 1.9257 | 2.8672 | 0.24446 | -1.8032 | -1.866 | 174.4943 | 167.5446 | 60.4959 | -4.7717 | -12.3893 | -119.6101 |  | 1.2081 | 0.41914 | 0.46697 | 1.2867 | 0.29877 | 0.34251 | 8.3836 | -166.9045 | 113.9395 | 5.6023 | -157.8362 | 105.9147

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.30463 | 2.901 | 2.9071 | 0.30583 | 2.9006 | 2.9071 | 3.5175 | 33.4982 | 33.5684 | 3.5315 | 33.4935 | 33.5679 | -1.332 | 15.4058 | 6.1158 | 1.2635 | -9.8058 | -2.4082 | 4.218 | 5.3763 | 18.115 | -4.3647 | -1.9963 | -11.2422 | -100.7125 | -169.372 | 28.035 | 79.4578 | 10.6567 | -151.9948 |  | 1.2575 | 0.4871 | 0.56957 | 1.2867 | 0.29877 | 0.34251 | 6.8126 | -150.1341 | 99.38 | 5.6023 | -157.8362 | 105.9147
Line_1 | 0.32943 | 3.7658 | 3.4827 | 0.32788 | 3.7659 | 3.4835 | 3.804 | 43.4836 | 40.2149 | 3.786 | 43.4853 | 40.224 | 2.5443 | 8.7171e-11 | 1.0708e-10 | -2.5988 | 12.4243 | 4.2403 | -4.671 | -8.5161e-11 | -2.6106e-11 | 4.1203 | 3.7995 | 13.1082 | 63.5599 | 5.1889 | -146.1886 | -116.6391 | -174.8404 | 33.8404 |  | 1.3983 | 0 | 0 | 1.2867 | 0.29877 | 0.34251 | 2.137 | 0 | 0 | 5.6023 | -157.8362 | 105.9147
Line_2 | 0.092181 | 0.9225 | 0.66197 | 0.091371 | 0.92155 | 0.66123 | 1.0644 | 10.6521 | 7.6438 | 1.0551 | 10.6411 | 7.6353 | -1.2483 | 4.028 | 2.126 | 1.3353 | -2.6185 | -1.8322 | -0.30867 | 1.9257 | 2.8672 | 0.24446 | -1.8032 | -1.866 | 174.4943 | 167.5446 | 60.4959 | -4.7717 | -12.3893 | -119.6101 |  | 1.2081 | 0.41914 | 0.46697 | 1.2867 | 0.29877 | 0.34251 | 8.3836 | -166.9045 | 113.9395 | 5.6023 | -157.8362 | 105.9147

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.04334 | 0.7173 | 0.66703 | 0.043041 | 0.71725 | 0.66691 | 0.50045 | 8.2827 | 7.7022 | 0.497 | 8.2821 | 7.7008 | 0.18521 | 7.6039 | 4.285 | -0.18724 | -7.2524 | -4.0757 | -0.55575 | 2.1547 | 6.5589 | 0.56194 | -2.0104 | -6.1283 | 74.8906 | -142.61 | 55.3102 | -105.7465 | 37.435 | -124.7373 |  | 1.1706 | 0.95419 | 1.0172 | 1.1918 | 0.90869 | 0.95572 | 3.3215 | -126.7888 | 112.1534 | 2.6814 | -127.0718 | 111.6363
Line_1 | 0.053075 | 1.0159 | 0.93179 | 0.052687 | 1.016 | 0.9322 | 0.61286 | 11.731 | 10.7594 | 0.60837 | 11.7314 | 10.7641 | 0.41282 | -8.236 | -6.0671 | -0.4088 | 9.2652 | 6.4256 | -0.6416 | -5.1332 | -6.8997 | 0.5988 | 5.2722 | 8.034 | 59.0199 | 23.3275 | -119.7478 | -121.6399 | -156.7132 | 60.289 |  | 1.2449 | 0.82727 | 0.85392 | 1.1918 | 0.90869 | 0.95572 | 1.7782 | -124.7391 | 108.9262 | 2.6814 | -127.0718 | 111.6363
Line_2 | 0.09464 | 0.36571 | 0.27439 | 0.094818 | 0.36529 | 0.27415 | 1.0928 | 4.2228 | 3.1684 | 1.0949 | 4.218 | 3.1656 | -0.59149 | 2.2324 | 2.3952 | 0.59604 | -2.0128 | -2.3498 | 1.121 | 3.3136 | 2.0635 | -1.1607 | -3.2619 | -1.9057 | -114.8035 | 174.5528 | 72.6943 | 65.501 | -5.3949 | -107.4054 |  | 1.1599 | 0.94614 | 0.9978 | 1.1918 | 0.90869 | 0.95572 | 3.0135 | -129.4156 | 113.4388 | 2.6814 | -127.0718 | 111.6363

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.04334 | 0.7173 | 0.66703 | 0.043041 | 0.71725 | 0.66691 | 0.50045 | 8.2827 | 7.7022 | 0.497 | 8.2821 | 7.7008 | 0.18521 | 7.6039 | 4.285 | -0.18724 | -7.2524 | -4.0757 | -0.55575 | 2.1547 | 6.5589 | 0.56194 | -2.0104 | -6.1283 | 74.8906 | -142.61 | 55.3102 | -105.7465 | 37.435 | -124.7373 |  | 1.1706 | 0.95419 | 1.0172 | 1.1918 | 0.90869 | 0.95572 | 3.3215 | -126.7888 | 112.1534 | 2.6814 | -127.0718 | 111.6363
Line_1 | 0.053075 | 1.0159 | 0.93179 | 0.052687 | 1.016 | 0.9322 | 0.61286 | 11.731 | 10.7594 | 0.60837 | 11.7314 | 10.7641 | 0.41282 | -8.236 | -6.0671 | -0.4088 | 9.2652 | 6.4256 | -0.6416 | -5.1332 | -6.8997 | 0.5988 | 5.2722 | 8.034 | 59.0199 | 23.3275 | -119.7478 | -121.6399 | -156.7132 | 60.289 |  | 1.2449 | 0.82727 | 0.85392 | 1.1918 | 0.90869 | 0.95572 | 1.7782 | -124.7391 | 108.9262 | 2.6814 | -127.0718 | 111.6363
Line_2 | 0.09464 | 0.36571 | 0.27439 | 0.094818 | 0.36529 | 0.27415 | 1.0928 | 4.2228 | 3.1684 | 1.0949 | 4.218 | 3.1656 | -0.59149 | 2.2324 | 2.3952 | 0.59604 | -2.0128 | -2.3498 | 1.121 | 3.3136 | 2.0635 | -1.1607 | -3.2619 | -1.9057 | -114.8035 | 174.5528 | 72.6943 | 65.501 | -5.3949 | -107.4054 |  | 1.1599 | 0.94614 | 0.9978 | 1.1918 | 0.90869 | 0.95572 | 3.0135 | -129.4156 | 113.4388 | 2.6814 | -127.0718 | 111.6363

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.39944 | 2.288 | 2.3534 | 0.40029 | 2.2878 | 2.3533 | 4.6123 | 26.42 | 27.1744 | 4.6221 | 26.4172 | 27.1735 | -0.15991 | 16.6645 | 9.0504 | 0.10904 | -10.3519 | -4.057 | 4.7379 | 1.4078 | 13.8585 | -4.9205 | 0.10061 | -8.6923 | -85.2922 | -157.1309 | 41.398 | 94.7842 | 22.8934 | -138.6263 |  | 1.0278 | 0.633 | 0.6091 | 1.0648 | 0.39188 | 0.35301 | 6.6409 | -152.3021 | 98.251 | 6.0538 | -157.6634 | 106.3535
Line_1 | 0.40735 | 2.9325 | 2.7227 | 0.40592 | 2.9323 | 2.7235 | 4.7036 | 33.8614 | 31.4393 | 4.6872 | 33.8592 | 31.4488 | 1.2804 | -1.0501e-10 | -4.9425e-11 | -1.333 | 13.2439 | 5.1988 | -5.5811 | -6.3001e-11 | -1.0363e-10 | 4.8097 | 0.8127 | 9.8092 | 80.6411 | 18.8547 | -135.7505 | -99.4366 | -161.1749 | 44.2766 |  | 1.2174 | 0 | 0 | 1.0648 | 0.39188 | 0.35301 | 3.5618 | 0 | 0 | 6.0538 | -157.6634 | 106.3535
Line_2 | 0.10053 | 0.67075 | 0.39214 | 0.099951 | 0.67022 | 0.39183 | 1.1608 | 7.7451 | 4.5281 | 1.1541 | 7.739 | 4.5245 | -1.0926 | 4.1697 | 1.2097 | 1.2239 | -2.892 | -1.1417 | -0.15669 | 0.833 | 1.7235 | 0.11079 | -0.91331 | -1.1169 | -179.4989 | -175.2501 | 62.1046 | 0.88146 | 4.8101 | -118.0159 |  | 0.9509 | 0.54901 | 0.46503 | 1.0648 | 0.39188 | 0.35301 | 8.6621 | -163.9527 | 117.0411 | 6.0538 | -157.6634 | 106.3535

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.39944 | 2.288 | 2.3534 | 0.40029 | 2.2878 | 2.3533 | 4.6123 | 26.42 | 27.1744 | 4.6221 | 26.4172 | 27.1735 | -0.15991 | 16.6645 | 9.0504 | 0.10904 | -10.3519 | -4.057 | 4.7379 | 1.4078 | 13.8585 | -4.9205 | 0.10061 | -8.6923 | -85.2922 | -157.1309 | 41.398 | 94.7842 | 22.8934 | -138.6263 |  | 1.0278 | 0.633 | 0.6091 | 1.0648 | 0.39188 | 0.35301 | 6.6409 | -152.3021 | 98.251 | 6.0538 | -157.6634 | 106.3535
Line_1 | 0.40735 | 2.9325 | 2.7227 | 0.40592 | 2.9323 | 2.7235 | 4.7036 | 33.8614 | 31.4393 | 4.6872 | 33.8592 | 31.4488 | 1.2804 | -1.0501e-10 | -4.9425e-11 | -1.333 | 13.2439 | 5.1988 | -5.5811 | -6.3001e-11 | -1.0363e-10 | 4.8097 | 0.8127 | 9.8092 | 80.6411 | 18.8547 | -135.7505 | -99.4366 | -161.1749 | 44.2766 |  | 1.2174 | 0 | 0 | 1.0648 | 0.39188 | 0.35301 | 3.5618 | 0 | 0 | 6.0538 | -157.6634 | 106.3535
Line_2 | 0.10053 | 0.67075 | 0.39214 | 0.099951 | 0.67022 | 0.39183 | 1.1608 | 7.7451 | 4.5281 | 1.1541 | 7.739 | 4.5245 | -1.0926 | 4.1697 | 1.2097 | 1.2239 | -2.892 | -1.1417 | -0.15669 | 0.833 | 1.7235 | 0.11079 | -0.91331 | -1.1169 | -179.4989 | -175.2501 | 62.1046 | 0.88146 | 4.8101 | -118.0159 |  | 0.9509 | 0.54901 | 0.46503 | 1.0648 | 0.39188 | 0.35301 | 8.6621 | -163.9527 | 117.0411 | 6.0538 | -157.6634 | 106.3535

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16249 | 0.68923 | 0.7023 | 0.16284 | 0.68911 | 0.70225 | 1.8762 | 7.9585 | 8.1095 | 1.8803 | 7.9571 | 8.1088 | 0.64216 | 6.5286 | 4.2069 | -0.65614 | -5.9117 | -3.7624 | 1.7609 | 2.335 | 6.0435 | -1.7887 | -2.2331 | -5.524 | -67.3714 | -148.0287 | 57.5023 | 112.6929 | 32.003 | -122.5301 |  | 0.999 | 0.87122 | 0.90802 | 1.0132 | 0.79418 | 0.82424 | 2.593 | -128.3492 | 112.6605 | 2.5488 | -127.303 | 113.2112
Line_1 | 0.16367 | 0.90078 | 0.81105 | 0.16309 | 0.90075 | 0.81142 | 1.8899 | 10.4013 | 9.3653 | 1.8832 | 10.4009 | 9.3695 | -0.15332 | -6.0592 | -4.3683 | 0.13499 | 7.4755 | 4.8222 | -2.0288 | -3.5124 | -4.9769 | 1.9033 | 3.514 | 6.0322 | 96.6716 | 27.5591 | -118.1841 | -83.3944 | -152.4797 | 61.8502 |  | 1.0765 | 0.67334 | 0.70709 | 1.0132 | 0.79418 | 0.82424 | 2.3497 | -122.3409 | 110.5416 | 2.5488 | -127.303 | 113.2112
Line_2 | 0.045832 | 0.22066 | 0.12368 | 0.045607 | 0.22043 | 0.12349 | 0.52922 | 2.548 | 1.4281 | 0.52663 | 2.5453 | 1.4259 | -0.49921 | 1.7245 | 1.0814 | 0.52114 | -1.5638 | -1.0598 | 0.10496 | 1.275 | 0.58159 | -0.11464 | -1.2809 | -0.50814 | -165.3851 | -166.6913 | 87.7303 | 14.9549 | 13.3777 | -92.4062 |  | 0.96391 | 0.84173 | 0.8598 | 1.0132 | 0.79418 | 0.82424 | 2.7417 | -130.2142 | 116.0016 | 2.5488 | -127.303 | 113.2112

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.16249 | 0.68923 | 0.7023 | 0.16284 | 0.68911 | 0.70225 | 1.8762 | 7.9585 | 8.1095 | 1.8803 | 7.9571 | 8.1088 | 0.64216 | 6.5286 | 4.2069 | -0.65614 | -5.9117 | -3.7624 | 1.7609 | 2.335 | 6.0435 | -1.7887 | -2.2331 | -5.524 | -67.3714 | -148.0287 | 57.5023 | 112.6929 | 32.003 | -122.5301 |  | 0.999 | 0.87122 | 0.90802 | 1.0132 | 0.79418 | 0.82424 | 2.593 | -128.3492 | 112.6605 | 2.5488 | -127.303 | 113.2112
Line_1 | 0.16367 | 0.90078 | 0.81105 | 0.16309 | 0.90075 | 0.81142 | 1.8899 | 10.4013 | 9.3653 | 1.8832 | 10.4009 | 9.3695 | -0.15332 | -6.0592 | -4.3683 | 0.13499 | 7.4755 | 4.8222 | -2.0288 | -3.5124 | -4.9769 | 1.9033 | 3.514 | 6.0322 | 96.6716 | 27.5591 | -118.1841 | -83.3944 | -152.4797 | 61.8502 |  | 1.0765 | 0.67334 | 0.70709 | 1.0132 | 0.79418 | 0.82424 | 2.3497 | -122.3409 | 110.5416 | 2.5488 | -127.303 | 113.2112
Line_2 | 0.045832 | 0.22066 | 0.12368 | 0.045607 | 0.22043 | 0.12349 | 0.52922 | 2.548 | 1.4281 | 0.52663 | 2.5453 | 1.4259 | -0.49921 | 1.7245 | 1.0814 | 0.52114 | -1.5638 | -1.0598 | 0.10496 | 1.275 | 0.58159 | -0.11464 | -1.2809 | -0.50814 | -165.3851 | -166.6913 | 87.7303 | 14.9549 | 13.3777 | -92.4062 |  | 0.96391 | 0.84173 | 0.8598 | 1.0132 | 0.79418 | 0.82424 | 2.7417 | -130.2142 | 116.0016 | 2.5488 | -127.303 | 113.2112