## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 4.283 | 4.283 | 0 | 9.0614 | 148.3662 | 148.3662 | 28.6163 | -1e-07 | 32.4685 | -1e-07 | -77.7798 | 102.2202 | 0.29171 | 0 | -29.1714 | 0
Line_1 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0
Line_2 | 0.9515 | 0.9515 | 0 | 1.8972 | 32.9609 | 32.9609 | 1.4123 | -1e-07 | 1.6025 | -1e-07 | -72.853 | 107.147 | 0.064805 | 0 | -24.2445 | 0

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.8763 | 0.8763 | 0 | 1.9596 | 30.3558 | 30.3558 | 22.4252 | -21.2272 | 19.1954 | -17.8362 | -47.233 | 132.767 | 0.97242 | 0.91337 | -6.6703 | -7.1943
Line_1 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943
Line_2 | 0.31157 | 0.31157 | 0 | 0.57123 | 10.793 | 10.793 | 6.2226 | -6.0711 | 7.9384 | -7.7666 | -59.1798 | 120.8202 | 0.93455 | 0.91337 | -7.271 | -7.1943

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6016 | 3.6016 | 0 | 6.8561 | 124.7634 | 124.7634 | 38.8525 | -1e-07 | 22.9597 | -1e-07 | -69.6723 | 110.3277 | 0.36172 | 0 | -39.0915 | 0
Line_1 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0
Line_2 | 0.77473 | 0.77473 | 0 | 1.4748 | 26.8374 | 26.8374 | 1.7977 | -1e-07 | 1.0624 | -1e-07 | -70.2749 | 109.7251 | 0.077808 | 0 | -39.6941 | 0

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.88201 | 0.88201 | 0 | 1.679 | 30.5537 | 30.5537 | 19.072 | -16.7419 | 18.0132 | -16.6363 | -50.7266 | 129.2734 | 0.85861 | 0.77248 | -7.3619 | -5.9079
Line_1 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079
Line_2 | 0.18973 | 0.18973 | 0 | 0.36117 | 6.5723 | 6.5723 | 3.6713 | -3.5635 | 3.68 | -3.6162 | -51.3292 | 128.6708 | 0.79091 | 0.77248 | -6.2614 | -5.9079

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.35595 | 3.6314 | 3.7936 | 0.35595 | 3.6314 | 3.7936 | 4.1102 | 41.9321 | 43.8052 | 4.1102 | 41.9321 | 43.8052 | -2.8809 | 31.035 | -18.1673 | 2.9468 | -24.1776 | 25.651 | -3.7882 | 2.3326 | 12.0075 | 3.8629 | 5.4478 | -3.5164 | 129.3592 | -165.2802 | 9.8274 | -50.6408 | 14.7198 | -170.1726 | 1.1579 | 0.74221 | 0.49713 | 1.1821 | 0.59105 | 0.59105 | 2.1065 | -160.9818 | 156.365 | 2.0217 | -177.9783 | -177.9783
Line_1 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783
Line_2 | 0.17798 | 0.82688 | 0.74081 | 0.17798 | 0.82688 | 0.74081 | 2.0551 | 9.548 | 8.5541 | 2.0551 | 9.548 | 8.5541 | 1.4899 | 5.9918 | -4.6142 | -1.4734 | -5.6362 | 4.8995 | 1.9502 | 0.12158 | 1.5713 | -1.9315 | 0.28182 | -1.2476 | -50.6408 | -175.1159 | 16.3071 | 129.3592 | 4.8841 | -163.6929 | 1.1942 | 0.62767 | 0.56983 | 1.1821 | 0.59105 | 0.59105 | 1.9805 | -173.9534 | 177.501 | 2.0217 | -177.9783 | -177.9783

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.25737 | 1.3967 | 1.3626 | 0.25737 | 1.3967 | 1.3626 | 2.9719 | 16.1276 | 15.7336 | 2.9719 | 16.1276 | 15.7336 | -1.5571 | 16.583 | -0.024169 | 1.5915 | -15.5686 | 0.9896 | -3.0312 | 1.2162 | 13.0202 | 3.0703 | -0.065208 | -11.9248 | 118.302 | -138.8076 | 30.5822 | -61.698 | 41.1924 | -149.4178 | 1.1467 | 1.031 | 0.82754 | 1.1637 | 0.96535 | 0.76053 | 1.1134 | -134.6132 | 120.6885 | 0.90162 | -138.5676 | 125.3261
Line_1 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261
Line_2 | 0.12869 | 0.3798 | 0.37361 | 0.12869 | 0.3798 | 0.37361 | 1.4859 | 4.3855 | 4.314 | 1.4859 | 4.3855 | 4.314 | 0.80437 | 3.8907 | 0.077321 | -0.79576 | -3.8157 | -0.0047391 | 1.5449 | 1.9191 | 3.3633 | -1.5351 | -1.834 | -3.2809 | -61.698 | -164.2384 | 35.4088 | 118.302 | 15.7616 | -144.5912 | 1.1722 | 0.98922 | 0.77982 | 1.1637 | 0.96535 | 0.76053 | 0.79804 | -137.9837 | 124.0918 | 0.90162 | -138.5676 | 125.3261

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.15892 | 3.0486 | 3.19 | 0.15892 | 3.0486 | 3.19 | 1.8351 | 35.2024 | 36.8347 | 1.8351 | 35.2024 | 36.8347 | -1.8248 | 26.2892 | -7.7754 | 1.8501 | -17.01 | 17.935 | -0.28017 | -0.30937 | 11.6491 | 0.29507 | 5.7929 | -5.6453 | 173.1413 | -158.99 | 19.6756 | -6.8587 | 21.01 | -160.3244 | 1.0061 | 0.74685 | 0.38023 | 1.0209 | 0.51046 | 0.51046 | 1.8699 | -159.6642 | 143.3972 | 2.2033 | -177.7967 | -177.7967
Line_1 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967
Line_2 | 0.079461 | 0.67052 | 0.59523 | 0.079461 | 0.67052 | 0.59523 | 0.91753 | 7.7425 | 6.8731 | 0.91753 | 7.7425 | 6.8731 | 0.93133 | 4.3581 | -3.093 | -0.92503 | -3.9093 | 3.4467 | 0.15126 | -0.3159 | 0.86397 | -0.14754 | 0.58117 | -0.65493 | -6.8587 | -169.3408 | 12.9622 | 173.1413 | 10.6592 | -167.0378 | 1.0283 | 0.56436 | 0.46725 | 1.0209 | 0.51046 | 0.51046 | 2.3664 | -173.4866 | 177.3556 | 2.2033 | -177.7967 | -177.7967

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.064112 | 1.2299 | 1.2869 | 0.064112 | 1.2299 | 1.2869 | 0.7403 | 14.2014 | 14.8599 | 0.7403 | 14.2014 | 14.8599 | -0.73023 | 12.9507 | 1.4179 | 0.73434 | -11.4405 | 0.23553 | 0.11457 | 1.7681 | 10.7707 | -0.11214 | -0.87564 | -9.7936 | -170.3183 | -142.4496 | 36.216 | 9.6817 | 37.5504 | -143.784 | 0.99846 | 0.92039 | 0.73107 | 1.0034 | 0.80795 | 0.65925 | 0.76513 | -134.6755 | 118.7162 | 0.99898 | -138.0728 | 127.5936
Line_1 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936
Line_2 | 0.032056 | 0.2705 | 0.24013 | 0.032056 | 0.2705 | 0.24013 | 0.37015 | 3.1235 | 2.7727 | 0.37015 | 3.1235 | 2.7727 | 0.36819 | 2.5137 | -0.19971 | -0.36717 | -2.4407 | 0.25728 | -0.055465 | 0.68473 | 1.8438 | 0.056071 | -0.64156 | -1.8097 | 9.6817 | -152.8004 | 29.5025 | -170.3183 | 27.1996 | -150.4975 | 1.0059 | 0.83411 | 0.66885 | 1.0034 | 0.80795 | 0.65925 | 1.115 | -137.563 | 125.6845 | 0.99898 | -138.0728 | 127.5936

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.9736 | 0.90526 | 0.8184 | 1.9708 | 0.90828 | 0.82082 | 22.7895 | 10.453 | 9.45 | 22.7565 | 10.4879 | 9.478 | 2.6938 | -9.4405 | 13.5164 | 1.0218e-10 | 9.6198 | -13.4848 | 2.4305 | 10.297 | 2.0456 | -7.9139e-11 | -9.9798 | -1.6521 | -73.2484 | 92.2097 | 124.6774 | 106.7804 | -87.8054 | -55.45 |  | 0.1592 | 1.3364 | 1.4466 | 0 | 1.3217 | 1.4334 | -31.1896 | -135.2748 | 133.2832 | 0 | -133.8577 | 131.5348
Line_1 | 1.1439 | 0.45688 | 0.4128 | 1.1412 | 0.45414 | 0.41041 | 13.2091 | 5.2756 | 4.7667 | 13.1779 | 5.244 | 4.739 | 3.0596 | 5.8097 | -5.7962 | 6.0485e-11 | -4.8099 | 6.7424 | 1.4758 | -4.4128 | -0.7963 | -4.4076e-11 | 4.9899 | 0.82605 | -74.9211 | -87.7878 | -55.6372 | 105.1027 | 92.1946 | 124.55 |  | 0.25716 | 1.3829 | 1.2274 | 0 | 1.3217 | 1.4334 | -49.17 | -125.0063 | 132.1853 | 0 | -133.8577 | 131.5348
Line_2 | 1.1439 | 0.45688 | 0.4128 | 1.1412 | 0.45414 | 0.41041 | 13.2091 | 5.2756 | 4.7667 | 13.1779 | 5.244 | 4.739 | 3.0596 | 5.8097 | -5.7962 | 6.0485e-11 | -4.8099 | 6.7424 | 1.4758 | -4.4128 | -0.7963 | -4.4076e-11 | 4.9899 | 0.82605 | -74.9211 | -87.7878 | -55.6372 | 105.1027 | 92.1946 | 124.55 |  | 0.25716 | 1.3829 | 1.2274 | 0 | 1.3217 | 1.4334 | -49.17 | -125.0063 | 132.1853 | 0 | -133.8577 | 131.5348

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.9736 | 0.90526 | 0.8184 | 1.9708 | 0.90828 | 0.82082 | 22.7895 | 10.453 | 9.45 | 22.7565 | 10.4879 | 9.478 | 2.6938 | -9.4405 | 13.5164 | 1.0218e-10 | 9.6198 | -13.4848 | 2.4305 | 10.297 | 2.0456 | -7.9139e-11 | -9.9798 | -1.6521 | -73.2484 | 92.2097 | 124.6774 | 106.7804 | -87.8054 | -55.45 |  | 0.1592 | 1.3364 | 1.4466 | 0 | 1.3217 | 1.4334 | -31.1896 | -135.2748 | 133.2832 | 0 | -133.8577 | 131.5348
Line_1 | 1.1439 | 0.45688 | 0.4128 | 1.1412 | 0.45414 | 0.41041 | 13.2091 | 5.2756 | 4.7667 | 13.1779 | 5.244 | 4.739 | 3.0596 | 5.8097 | -5.7962 | 6.0485e-11 | -4.8099 | 6.7424 | 1.4758 | -4.4128 | -0.7963 | -4.4076e-11 | 4.9899 | 0.82605 | -74.9211 | -87.7878 | -55.6372 | 105.1027 | 92.1946 | 124.55 |  | 0.25716 | 1.3829 | 1.2274 | 0 | 1.3217 | 1.4334 | -49.17 | -125.0063 | 132.1853 | 0 | -133.8577 | 131.5348
Line_2 | 1.1439 | 0.45688 | 0.4128 | 1.1412 | 0.45414 | 0.41041 | 13.2091 | 5.2756 | 4.7667 | 13.1779 | 5.244 | 4.739 | 3.0596 | 5.8097 | -5.7962 | 6.0485e-11 | -4.8099 | 6.7424 | 1.4758 | -4.4128 | -0.7963 | -4.4076e-11 | 4.9899 | 0.82605 | -74.9211 | -87.7878 | -55.6372 | 105.1027 | 92.1946 | 124.55 |  | 0.25716 | 1.3829 | 1.2274 | 0 | 1.3217 | 1.4334 | -49.17 | -125.0063 | 132.1853 | 0 | -133.8577 | 131.5348

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.49207 | 0.19327 | 0.36053 | 0.49124 | 0.19409 | 0.36096 | 5.6819 | 2.2317 | 4.1631 | 5.6723 | 2.2412 | 4.1681 | 4.1194 | -2.5735 | 3.5292 | -3.9355 | 2.5913 | -3.5075 | 2.6956 | 0.96951 | -3.5185 | -2.5446 | -0.97682 | 3.6127 | -41.823 | 76.7515 | 171.2976 | 138.2336 | -103.1017 | -8.8388 |  | 0.86643 | 1.2323 | 1.1971 | 0.8262 | 1.2356 | 1.2081 | -8.6235 | -123.8916 | 126.385 | -8.881 | -123.7563 | 125.3146
Line_1 | 0.43836 | 0.09773 | 0.18097 | 0.43749 | 0.097046 | 0.18048 | 5.0617 | 1.1285 | 2.0897 | 5.0517 | 1.1206 | 2.084 | 2.9663 | 1.3359 | -1.6399 | -2.5829 | -1.2956 | 1.7538 | 3.5138 | -0.43271 | 1.763 | -3.2784 | 0.48841 | -1.8064 | -60.6556 | -102.7839 | -9.0669 | 119.3523 | 76.8983 | 171.1612 |  | 0.90848 | 1.2443 | 1.1522 | 0.8262 | 1.2356 | 1.2081 | -10.8258 | -120.7322 | 123.8625 | -8.881 | -123.7563 | 125.3146
Line_2 | 0.43836 | 0.09773 | 0.18097 | 0.43749 | 0.097046 | 0.18048 | 5.0617 | 1.1285 | 2.0897 | 5.0517 | 1.1206 | 2.084 | 2.9663 | 1.3359 | -1.6399 | -2.5829 | -1.2956 | 1.7538 | 3.5138 | -0.43271 | 1.763 | -3.2784 | 0.48841 | -1.8064 | -60.6556 | -102.7839 | -9.0669 | 119.3523 | 76.8983 | 171.1612 |  | 0.90848 | 1.2443 | 1.1522 | 0.8262 | 1.2356 | 1.2081 | -10.8258 | -120.7322 | 123.8625 | -8.881 | -123.7563 | 125.3146

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.49207 | 0.19327 | 0.36053 | 0.49124 | 0.19409 | 0.36096 | 5.6819 | 2.2317 | 4.1631 | 5.6723 | 2.2412 | 4.1681 | 4.1194 | -2.5735 | 3.5292 | -3.9355 | 2.5913 | -3.5075 | 2.6956 | 0.96951 | -3.5185 | -2.5446 | -0.97682 | 3.6127 | -41.823 | 76.7515 | 171.2976 | 138.2336 | -103.1017 | -8.8388 |  | 0.86643 | 1.2323 | 1.1971 | 0.8262 | 1.2356 | 1.2081 | -8.6235 | -123.8916 | 126.385 | -8.881 | -123.7563 | 125.3146
Line_1 | 0.43836 | 0.09773 | 0.18097 | 0.43749 | 0.097046 | 0.18048 | 5.0617 | 1.1285 | 2.0897 | 5.0517 | 1.1206 | 2.084 | 2.9663 | 1.3359 | -1.6399 | -2.5829 | -1.2956 | 1.7538 | 3.5138 | -0.43271 | 1.763 | -3.2784 | 0.48841 | -1.8064 | -60.6556 | -102.7839 | -9.0669 | 119.3523 | 76.8983 | 171.1612 |  | 0.90848 | 1.2443 | 1.1522 | 0.8262 | 1.2356 | 1.2081 | -10.8258 | -120.7322 | 123.8625 | -8.881 | -123.7563 | 125.3146
Line_2 | 0.43836 | 0.09773 | 0.18097 | 0.43749 | 0.097046 | 0.18048 | 5.0617 | 1.1285 | 2.0897 | 5.0517 | 1.1206 | 2.084 | 2.9663 | 1.3359 | -1.6399 | -2.5829 | -1.2956 | 1.7538 | 3.5138 | -0.43271 | 1.763 | -3.2784 | 0.48841 | -1.8064 | -60.6556 | -102.7839 | -9.0669 | 119.3523 | 76.8983 | 171.1612 |  | 0.90848 | 1.2443 | 1.1522 | 0.8262 | 1.2356 | 1.2081 | -10.8258 | -120.7322 | 123.8625 | -8.881 | -123.7563 | 125.3146

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7437 | 0.79636 | 0.6864 | 1.7415 | 0.79853 | 0.68843 | 20.1346 | 9.1956 | 7.9258 | 20.1092 | 9.2206 | 7.9493 | 4.0034 | -2.1121 | 10.3103 | -4.9934e-11 | 2.3304 | -10.2397 | 1.6248 | 10.3376 | 1.3376 | 7.9164e-14 | -9.8999 | -0.98212 | -61.0299 | 120.1109 | 124.964 | 119.0196 | -60.0001 | -55.1795 |  | 0.21459 | 1.1474 | 1.3118 | 0 | 1.103 | 1.294 | -38.9398 | -138.3419 | 132.3559 | 0 | -136.7542 | 130.2991
Line_1 | 0.87346 | 0.40127 | 0.34614 | 0.8714 | 0.39927 | 0.34421 | 10.0859 | 4.6334 | 3.9968 | 10.0621 | 4.6103 | 3.9746 | 3.6036 | 2.6624 | -3.8808 | -2.4953e-11 | -1.1652 | 5.1198 | 1.0045 | -4.7127 | -0.3917 | -1.2806e-12 | 4.9499 | 0.49106 | -64.0563 | -60.1231 | -55.3495 | 115.9909 | 119.9999 | 124.8205 |  | 0.37092 | 1.1682 | 0.97591 | 0 | 1.103 | 1.294 | -48.4802 | -120.6588 | 130.4139 | 0 | -136.7542 | 130.2991
Line_2 | 0.87346 | 0.40127 | 0.34614 | 0.8714 | 0.39927 | 0.34421 | 10.0859 | 4.6334 | 3.9968 | 10.0621 | 4.6103 | 3.9746 | 3.6036 | 2.6624 | -3.8808 | -2.4953e-11 | -1.1652 | 5.1198 | 1.0045 | -4.7127 | -0.3917 | -1.2806e-12 | 4.9499 | 0.49106 | -64.0563 | -60.1231 | -55.3495 | 115.9909 | 119.9999 | 124.8205 |  | 0.37092 | 1.1682 | 0.97591 | 0 | 1.103 | 1.294 | -48.4802 | -120.6588 | 130.4139 | 0 | -136.7542 | 130.2991

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.7437 | 0.79636 | 0.6864 | 1.7415 | 0.79853 | 0.68843 | 20.1346 | 9.1956 | 7.9258 | 20.1092 | 9.2206 | 7.9493 | 4.0034 | -2.1121 | 10.3103 | -4.9934e-11 | 2.3304 | -10.2397 | 1.6248 | 10.3376 | 1.3376 | 7.9164e-14 | -9.8999 | -0.98212 | -61.0299 | 120.1109 | 124.964 | 119.0196 | -60.0001 | -55.1795 |  | 0.21459 | 1.1474 | 1.3118 | 0 | 1.103 | 1.294 | -38.9398 | -138.3419 | 132.3559 | 0 | -136.7542 | 130.2991
Line_1 | 0.87346 | 0.40127 | 0.34614 | 0.8714 | 0.39927 | 0.34421 | 10.0859 | 4.6334 | 3.9968 | 10.0621 | 4.6103 | 3.9746 | 3.6036 | 2.6624 | -3.8808 | -2.4953e-11 | -1.1652 | 5.1198 | 1.0045 | -4.7127 | -0.3917 | -1.2806e-12 | 4.9499 | 0.49106 | -64.0563 | -60.1231 | -55.3495 | 115.9909 | 119.9999 | 124.8205 |  | 0.37092 | 1.1682 | 0.97591 | 0 | 1.103 | 1.294 | -48.4802 | -120.6588 | 130.4139 | 0 | -136.7542 | 130.2991
Line_2 | 0.87346 | 0.40127 | 0.34614 | 0.8714 | 0.39927 | 0.34421 | 10.0859 | 4.6334 | 3.9968 | 10.0621 | 4.6103 | 3.9746 | 3.6036 | 2.6624 | -3.8808 | -2.4953e-11 | -1.1652 | 5.1198 | 1.0045 | -4.7127 | -0.3917 | -1.2806e-12 | 4.9499 | 0.49106 | -64.0563 | -60.1231 | -55.3495 | 115.9909 | 119.9999 | 124.8205 |  | 0.37092 | 1.1682 | 0.97591 | 0 | 1.103 | 1.294 | -48.4802 | -120.6588 | 130.4139 | 0 | -136.7542 | 130.2991

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.56225 | 0.25678 | 0.22133 | 0.56154 | 0.25748 | 0.22198 | 6.4923 | 2.9651 | 2.5556 | 6.4841 | 2.9732 | 2.5632 | 3.6533 | -0.65728 | 2.6963 | -3.2356 | 0.68504 | -2.6955 | 3.2445 | 3.0665 | -0.53241 | -3.0689 | -3.0256 | 0.56727 | -49.0973 | 132.0434 | 136.8966 | 130.9521 | -48.0675 | -43.2469 |  | 0.75259 | 1.0577 | 1.0754 | 0.68776 | 1.0434 | 1.0746 | -7.489 | -125.8589 | 125.7268 | -5.5628 | -125.3101 | 124.8684
Line_1 | 0.28164 | 0.12939 | 0.11161 | 0.28098 | 0.12874 | 0.11099 | 3.2521 | 1.494 | 1.2888 | 3.2445 | 1.4866 | 1.2816 | 1.9126 | 0.50145 | -1.2245 | -1.5356 | -0.34252 | 1.3477 | 1.7285 | -1.4927 | 0.2934 | -1.619 | 1.5128 | -0.28364 | -52.1237 | -48.1906 | -43.4169 | 127.9235 | 131.9325 | 136.7531 |  | 0.79269 | 1.054 | 0.97701 | 0.68776 | 1.0434 | 1.0746 | -10.0177 | -119.621 | 123.1081 | -5.5628 | -125.3101 | 124.8684
Line_2 | 0.28164 | 0.12939 | 0.11161 | 0.28098 | 0.12874 | 0.11099 | 3.2521 | 1.494 | 1.2888 | 3.2445 | 1.4866 | 1.2816 | 1.9126 | 0.50145 | -1.2245 | -1.5356 | -0.34252 | 1.3477 | 1.7285 | -1.4927 | 0.2934 | -1.619 | 1.5128 | -0.28364 | -52.1237 | -48.1906 | -43.4169 | 127.9235 | 131.9325 | 136.7531 |  | 0.79269 | 1.054 | 0.97701 | 0.68776 | 1.0434 | 1.0746 | -10.0177 | -119.621 | 123.1081 | -5.5628 | -125.3101 | 124.8684

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.56225 | 0.25678 | 0.22133 | 0.56154 | 0.25748 | 0.22198 | 6.4923 | 2.9651 | 2.5556 | 6.4841 | 2.9732 | 2.5632 | 3.6533 | -0.65728 | 2.6963 | -3.2356 | 0.68504 | -2.6955 | 3.2445 | 3.0665 | -0.53241 | -3.0689 | -3.0256 | 0.56727 | -49.0973 | 132.0434 | 136.8966 | 130.9521 | -48.0675 | -43.2469 |  | 0.75259 | 1.0577 | 1.0754 | 0.68776 | 1.0434 | 1.0746 | -7.489 | -125.8589 | 125.7268 | -5.5628 | -125.3101 | 124.8684
Line_1 | 0.28164 | 0.12939 | 0.11161 | 0.28098 | 0.12874 | 0.11099 | 3.2521 | 1.494 | 1.2888 | 3.2445 | 1.4866 | 1.2816 | 1.9126 | 0.50145 | -1.2245 | -1.5356 | -0.34252 | 1.3477 | 1.7285 | -1.4927 | 0.2934 | -1.619 | 1.5128 | -0.28364 | -52.1237 | -48.1906 | -43.4169 | 127.9235 | 131.9325 | 136.7531 |  | 0.79269 | 1.054 | 0.97701 | 0.68776 | 1.0434 | 1.0746 | -10.0177 | -119.621 | 123.1081 | -5.5628 | -125.3101 | 124.8684
Line_2 | 0.28164 | 0.12939 | 0.11161 | 0.28098 | 0.12874 | 0.11099 | 3.2521 | 1.494 | 1.2888 | 3.2445 | 1.4866 | 1.2816 | 1.9126 | 0.50145 | -1.2245 | -1.5356 | -0.34252 | 1.3477 | 1.7285 | -1.4927 | 0.2934 | -1.619 | 1.5128 | -0.28364 | -52.1237 | -48.1906 | -43.4169 | 127.9235 | 131.9325 | 136.7531 |  | 0.79269 | 1.054 | 0.97701 | 0.68776 | 1.0434 | 1.0746 | -10.0177 | -119.621 | 123.1081 | -5.5628 | -125.3101 | 124.8684

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.41737 | 3.7098 | 3.7381 | 0.41973 | 3.71 | 3.7374 | 4.8194 | 42.8375 | 43.1634 | 4.8466 | 42.8399 | 43.1562 | 0.60947 | 7.5813 | 7.0065 | -0.6203 | 9.1909e-11 | 1.2127e-10 | 7.0539 | 7.2162 | 9.2164 | -7.0412 | -8.1959e-11 | 1.5459e-11 | -84.3217 | -172.9081 | 17.3095 | 95.6573 | 7.1283 | -162.7254 |  | 1.4691 | 0.24433 | 0.26822 | 1.4584 | 0 | 0 | 0.74003 | -129.3216 | 70.0666 | 0.62276 | 0 | 0
Line_1 | 0.212 | 1.1255 | 0.92899 | 0.20986 | 1.1243 | 0.92742 | 2.448 | 12.9958 | 10.727 | 2.4233 | 12.9822 | 10.7089 | 0.01773 | 2.307 | 1.0067 | 0.31015 | 3.6685e-11 | 2.5719e-11 | -3.3495 | -0.20501 | 1.9781 | 3.5206 | -6.8417e-12 | -1.6088e-11 | 95.6955 | 155.8767 | 56.6566 | -84.3427 | -24.0324 | -123.4333 |  | 1.3683 | 0.17822 | 0.20691 | 1.4584 | 0 | 0 | 5.9987 | 150.7985 | 119.6841 | 0.62276 | 0 | 0
Line_2 | 0.212 | 1.1255 | 0.92899 | 0.20986 | 1.1243 | 0.92742 | 2.448 | 12.9958 | 10.727 | 2.4233 | 12.9822 | 10.7089 | 0.01773 | 2.307 | 1.0067 | 0.31015 | 3.6685e-11 | 2.5719e-11 | -3.3495 | -0.20501 | 1.9781 | 3.5206 | -6.8417e-12 | -1.6088e-11 | 95.6955 | 155.8767 | 56.6566 | -84.3427 | -24.0324 | -123.4333 |  | 1.3683 | 0.17822 | 0.20691 | 1.4584 | 0 | 0 | 5.9987 | 150.7985 | 119.6841 | 0.62276 | 0 | 0

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.41737 | 3.7098 | 3.7381 | 0.41973 | 3.71 | 3.7374 | 4.8194 | 42.8375 | 43.1634 | 4.8466 | 42.8399 | 43.1562 | 0.60947 | 7.5813 | 7.0065 | -0.6203 | 9.1909e-11 | 1.2127e-10 | 7.0539 | 7.2162 | 9.2164 | -7.0412 | -8.1959e-11 | 1.5459e-11 | -84.3217 | -172.9081 | 17.3095 | 95.6573 | 7.1283 | -162.7254 |  | 1.4691 | 0.24433 | 0.26822 | 1.4584 | 0 | 0 | 0.74003 | -129.3216 | 70.0666 | 0.62276 | 0 | 0
Line_1 | 0.212 | 1.1255 | 0.92899 | 0.20986 | 1.1243 | 0.92742 | 2.448 | 12.9958 | 10.727 | 2.4233 | 12.9822 | 10.7089 | 0.01773 | 2.307 | 1.0067 | 0.31015 | 3.6685e-11 | 2.5719e-11 | -3.3495 | -0.20501 | 1.9781 | 3.5206 | -6.8417e-12 | -1.6088e-11 | 95.6955 | 155.8767 | 56.6566 | -84.3427 | -24.0324 | -123.4333 |  | 1.3683 | 0.17822 | 0.20691 | 1.4584 | 0 | 0 | 5.9987 | 150.7985 | 119.6841 | 0.62276 | 0 | 0
Line_2 | 0.212 | 1.1255 | 0.92899 | 0.20986 | 1.1243 | 0.92742 | 2.448 | 12.9958 | 10.727 | 2.4233 | 12.9822 | 10.7089 | 0.01773 | 2.307 | 1.0067 | 0.31015 | 3.6685e-11 | 2.5719e-11 | -3.3495 | -0.20501 | 1.9781 | 3.5206 | -6.8417e-12 | -1.6088e-11 | 95.6955 | 155.8767 | 56.6566 | -84.3427 | -24.0324 | -123.4333 |  | 1.3683 | 0.17822 | 0.20691 | 1.4584 | 0 | 0 | 5.9987 | 150.7985 | 119.6841 | 0.62276 | 0 | 0

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.070733 | 0.79283 | 0.75661 | 0.070919 | 0.79315 | 0.75615 | 0.81675 | 9.1548 | 8.7366 | 0.8189 | 9.1585 | 8.7313 | 1.0274 | 7.9063 | 4.357 | -1.0331 | -7.5731 | -4.0486 | -0.068514 | 2.6689 | 7.0072 | 0.064401 | -2.3695 | -6.5939 | 5.5988 | -140.8015 | 49.1666 | -175.0948 | 39.2574 | -130.89 |  | 1.2607 | 0.9115 | 0.94446 | 1.2641 | 0.86642 | 0.88619 | 1.7837 | -122.1488 | 107.2937 | 1.3383 | -123.3685 | 107.5606
Line_1 | 0.03574 | 0.40127 | 0.3672 | 0.035459 | 0.40075 | 0.36658 | 0.41269 | 4.6335 | 4.24 | 0.40945 | 4.6275 | 4.2328 | -0.50397 | 1.5298 | 3.3873 | 0.51657 | -1.218 | -3.2113 | 0.0072305 | 3.824 | 2.2259 | -0.0322 | -3.8198 | -1.9387 | -176.2916 | 164.2314 | 76.5188 | 4.9052 | -15.6826 | -103.5585 |  | 1.2213 | 0.88888 | 0.95593 | 1.2641 | 0.86642 | 0.88619 | 2.8864 | -127.5725 | 109.8288 | 1.3383 | -123.3685 | 107.5606
Line_2 | 0.03574 | 0.40127 | 0.3672 | 0.035459 | 0.40075 | 0.36658 | 0.41269 | 4.6335 | 4.24 | 0.40945 | 4.6275 | 4.2328 | -0.50397 | 1.5298 | 3.3873 | 0.51657 | -1.218 | -3.2113 | 0.0072305 | 3.824 | 2.2259 | -0.0322 | -3.8198 | -1.9387 | -176.2916 | 164.2314 | 76.5188 | 4.9052 | -15.6826 | -103.5585 |  | 1.2213 | 0.88888 | 0.95593 | 1.2641 | 0.86642 | 0.88619 | 2.8864 | -127.5725 | 109.8288 | 1.3383 | -123.3685 | 107.5606

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.070733 | 0.79283 | 0.75661 | 0.070919 | 0.79315 | 0.75615 | 0.81675 | 9.1548 | 8.7366 | 0.8189 | 9.1585 | 8.7313 | 1.0274 | 7.9063 | 4.357 | -1.0331 | -7.5731 | -4.0486 | -0.068514 | 2.6689 | 7.0072 | 0.064401 | -2.3695 | -6.5939 | 5.5988 | -140.8015 | 49.1666 | -175.0948 | 39.2574 | -130.89 |  | 1.2607 | 0.9115 | 0.94446 | 1.2641 | 0.86642 | 0.88619 | 1.7837 | -122.1488 | 107.2937 | 1.3383 | -123.3685 | 107.5606
Line_1 | 0.03574 | 0.40127 | 0.3672 | 0.035459 | 0.40075 | 0.36658 | 0.41269 | 4.6335 | 4.24 | 0.40945 | 4.6275 | 4.2328 | -0.50397 | 1.5298 | 3.3873 | 0.51657 | -1.218 | -3.2113 | 0.0072305 | 3.824 | 2.2259 | -0.0322 | -3.8198 | -1.9387 | -176.2916 | 164.2314 | 76.5188 | 4.9052 | -15.6826 | -103.5585 |  | 1.2213 | 0.88888 | 0.95593 | 1.2641 | 0.86642 | 0.88619 | 2.8864 | -127.5725 | 109.8288 | 1.3383 | -123.3685 | 107.5606
Line_2 | 0.03574 | 0.40127 | 0.3672 | 0.035459 | 0.40075 | 0.36658 | 0.41269 | 4.6335 | 4.24 | 0.40945 | 4.6275 | 4.2328 | -0.50397 | 1.5298 | 3.3873 | 0.51657 | -1.218 | -3.2113 | 0.0072305 | 3.824 | 2.2259 | -0.0322 | -3.8198 | -1.9387 | -176.2916 | 164.2314 | 76.5188 | 4.9052 | -15.6826 | -103.5585 |  | 1.2213 | 0.88888 | 0.95593 | 1.2641 | 0.86642 | 0.88619 | 2.8864 | -127.5725 | 109.8288 | 1.3383 | -123.3685 | 107.5606

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4692 | 3.156 | 3.1193 | 0.47107 | 3.1564 | 3.1185 | 5.4179 | 36.4421 | 36.0188 | 5.4395 | 36.4471 | 36.0089 | 3.1277 | 10.2325 | 9.7221 | -3.1129 | -1.0818e-10 | -1.3623e-11 | 6.3012 | 4.5377 | 7.0943 | -6.2027 | -8.2251e-11 | -1.3494e-10 | -64.051 | -165.8714 | 26.5999 | 115.847 | 14.165 | -153.4343 |  | 1.2984 | 0.30716 | 0.33414 | 1.2759 | 0 | 0 | -0.44894 | -141.9559 | 62.7184 | -0.80296 | 0 | 0
Line_1 | 0.23718 | 0.96524 | 0.62161 | 0.23554 | 0.96442 | 0.62039 | 2.7387 | 11.1456 | 7.1778 | 2.7198 | 11.1362 | 7.1636 | -0.93211 | 3.0493 | 0.84082 | 1.5564 | -1.6603e-11 | -1.7329e-11 | -2.9005 | -0.70809 | 1.7484 | 3.1014 | -3.8059e-11 | -2.0682e-11 | 115.7633 | 164.8936 | 60.8649 | -64.153 | -15.0192 | -119.2409 |  | 1.1124 | 0.28087 | 0.27028 | 1.2759 | 0 | 0 | 7.9481 | 151.8206 | 125.181 | -0.80296 | 0 | 0
Line_2 | 0.23718 | 0.96524 | 0.62161 | 0.23554 | 0.96442 | 0.62039 | 2.7387 | 11.1456 | 7.1778 | 2.7198 | 11.1362 | 7.1636 | -0.93211 | 3.0493 | 0.84082 | 1.5564 | -1.6603e-11 | -1.7329e-11 | -2.9005 | -0.70809 | 1.7484 | 3.1014 | -3.8059e-11 | -2.0682e-11 | 115.7633 | 164.8936 | 60.8649 | -64.153 | -15.0192 | -119.2409 |  | 1.1124 | 0.28087 | 0.27028 | 1.2759 | 0 | 0 | 7.9481 | 151.8206 | 125.181 | -0.80296 | 0 | 0

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4692 | 3.156 | 3.1193 | 0.47107 | 3.1564 | 3.1185 | 5.4179 | 36.4421 | 36.0188 | 5.4395 | 36.4471 | 36.0089 | 3.1277 | 10.2325 | 9.7221 | -3.1129 | -1.0818e-10 | -1.3623e-11 | 6.3012 | 4.5377 | 7.0943 | -6.2027 | -8.2251e-11 | -1.3494e-10 | -64.051 | -165.8714 | 26.5999 | 115.847 | 14.165 | -153.4343 |  | 1.2984 | 0.30716 | 0.33414 | 1.2759 | 0 | 0 | -0.44894 | -141.9559 | 62.7184 | -0.80296 | 0 | 0
Line_1 | 0.23718 | 0.96524 | 0.62161 | 0.23554 | 0.96442 | 0.62039 | 2.7387 | 11.1456 | 7.1778 | 2.7198 | 11.1362 | 7.1636 | -0.93211 | 3.0493 | 0.84082 | 1.5564 | -1.6603e-11 | -1.7329e-11 | -2.9005 | -0.70809 | 1.7484 | 3.1014 | -3.8059e-11 | -2.0682e-11 | 115.7633 | 164.8936 | 60.8649 | -64.153 | -15.0192 | -119.2409 |  | 1.1124 | 0.28087 | 0.27028 | 1.2759 | 0 | 0 | 7.9481 | 151.8206 | 125.181 | -0.80296 | 0 | 0
Line_2 | 0.23718 | 0.96524 | 0.62161 | 0.23554 | 0.96442 | 0.62039 | 2.7387 | 11.1456 | 7.1778 | 2.7198 | 11.1362 | 7.1636 | -0.93211 | 3.0493 | 0.84082 | 1.5564 | -1.6603e-11 | -1.7329e-11 | -2.9005 | -0.70809 | 1.7484 | 3.1014 | -3.8059e-11 | -2.0682e-11 | 115.7633 | 164.8936 | 60.8649 | -64.153 | -15.0192 | -119.2409 |  | 1.1124 | 0.28087 | 0.27028 | 1.2759 | 0 | 0 | 7.9481 | 151.8206 | 125.181 | -0.80296 | 0 | 0

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.19769 | 0.76729 | 0.8056 | 0.19838 | 0.76758 | 0.80508 | 2.2828 | 8.8599 | 9.3023 | 2.2907 | 8.8632 | 9.2962 | 1.4785 | 6.3899 | 4.2052 | -1.4733 | -5.8025 | -3.5102 | 2.0586 | 3.4278 | 6.2743 | -2.0434 | -3.2021 | -5.7644 | -54.1192 | -149.8303 | 50.3163 | 125.7759 | 30.2233 | -129.7245 |  | 1.1103 | 0.81844 | 0.81197 | 1.0997 | 0.74773 | 0.726 | 0.19418 | -121.6192 | 106.4856 | -0.015812 | -120.8847 | 108.9368
Line_1 | 0.0998 | 0.26452 | 0.22351 | 0.099189 | 0.26421 | 0.22292 | 1.1524 | 3.0544 | 2.5809 | 1.1453 | 3.0508 | 2.574 | -0.63625 | 1.1139 | 1.9495 | 0.73663 | -0.82615 | -1.7588 | -0.99901 | 2.0446 | 0.82885 | 1.0217 | -2.1263 | -0.63162 | 125.6772 | 170.2286 | 89.2399 | -54.2241 | -9.6521 | -90.818 |  | 1.0278 | 0.76227 | 0.8208 | 1.0997 | 0.74773 | 0.726 | 3.1849 | -128.3529 | 112.2735 | -0.015812 | -120.8847 | 108.9368
Line_2 | 0.0998 | 0.26452 | 0.22351 | 0.099189 | 0.26421 | 0.22292 | 1.1524 | 3.0544 | 2.5809 | 1.1453 | 3.0508 | 2.574 | -0.63625 | 1.1139 | 1.9495 | 0.73663 | -0.82615 | -1.7588 | -0.99901 | 2.0446 | 0.82885 | 1.0217 | -2.1263 | -0.63162 | 125.6772 | 170.2286 | 89.2399 | -54.2241 | -9.6521 | -90.818 |  | 1.0278 | 0.76227 | 0.8208 | 1.0997 | 0.74773 | 0.726 | 3.1849 | -128.3529 | 112.2735 | -0.015812 | -120.8847 | 108.9368

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.19769 | 0.76729 | 0.8056 | 0.19838 | 0.76758 | 0.80508 | 2.2828 | 8.8599 | 9.3023 | 2.2907 | 8.8632 | 9.2962 | 1.4785 | 6.3899 | 4.2052 | -1.4733 | -5.8025 | -3.5102 | 2.0586 | 3.4278 | 6.2743 | -2.0434 | -3.2021 | -5.7644 | -54.1192 | -149.8303 | 50.3163 | 125.7759 | 30.2233 | -129.7245 |  | 1.1103 | 0.81844 | 0.81197 | 1.0997 | 0.74773 | 0.726 | 0.19418 | -121.6192 | 106.4856 | -0.015812 | -120.8847 | 108.9368
Line_1 | 0.0998 | 0.26452 | 0.22351 | 0.099189 | 0.26421 | 0.22292 | 1.1524 | 3.0544 | 2.5809 | 1.1453 | 3.0508 | 2.574 | -0.63625 | 1.1139 | 1.9495 | 0.73663 | -0.82615 | -1.7588 | -0.99901 | 2.0446 | 0.82885 | 1.0217 | -2.1263 | -0.63162 | 125.6772 | 170.2286 | 89.2399 | -54.2241 | -9.6521 | -90.818 |  | 1.0278 | 0.76227 | 0.8208 | 1.0997 | 0.74773 | 0.726 | 3.1849 | -128.3529 | 112.2735 | -0.015812 | -120.8847 | 108.9368
Line_2 | 0.0998 | 0.26452 | 0.22351 | 0.099189 | 0.26421 | 0.22292 | 1.1524 | 3.0544 | 2.5809 | 1.1453 | 3.0508 | 2.574 | -0.63625 | 1.1139 | 1.9495 | 0.73663 | -0.82615 | -1.7588 | -0.99901 | 2.0446 | 0.82885 | 1.0217 | -2.1263 | -0.63162 | 125.6772 | 170.2286 | 89.2399 | -54.2241 | -9.6521 | -90.818 |  | 1.0278 | 0.76227 | 0.8208 | 1.0997 | 0.74773 | 0.726 | 3.1849 | -128.3529 | 112.2735 | -0.015812 | -120.8847 | 108.9368