## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6358 | 3.6358 | 0 | 0 | 125.9486 | 125.9486 | 36.0342 | -15.4122 | 41.0034 | -17.6054 | -73.0863 | 106.9137 | 0.43341 | 0.18578 | -24.3956 | -24.2861
Line_1 | 2.7277 | 2.7277 | 5.405 | 0 | 94.4895 | 94.4895 | -1e-07 | 11.6068 | -1e-07 | 13.1692 | 107.1055 | -72.8945 | 0 | 0.18578 | 0 | -24.2861
Line_2 | 0.90821 | 0.90821 | 0 | 0 | 31.4612 | 31.4612 | -2.5187 | 3.8055 | -2.9762 | 4.4362 | 106.3378 | -73.6622 | 0.12393 | 0.18578 | -23.9029 | -24.2861
Line_3 | 1.8196 | 1.8196 | 3.5617 | 0 | 63.0325 | 63.0325 | -1e-07 | 5.165 | -1e-07 | 5.8603 | 107.4886 | -72.5114 | 0 | 0.12393 | 0 | -23.9029

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6358 | 3.6358 | 0 | 0 | 125.9486 | 125.9486 | 36.0342 | -15.4122 | 41.0034 | -17.6054 | -73.0863 | 106.9137 | 0.43341 | 0.18578 | -24.3956 | -24.2861
Line_1 | 2.7277 | 2.7277 | 5.405 | 0 | 94.4895 | 94.4895 | -1e-07 | 11.6068 | -1e-07 | 13.1692 | 107.1055 | -72.8945 | 0 | 0.18578 | 0 | -24.2861
Line_2 | 0.90821 | 0.90821 | 0 | 0 | 31.4612 | 31.4612 | -2.5187 | 3.8055 | -2.9762 | 4.4362 | 106.3378 | -73.6622 | 0.12393 | 0.18578 | -23.9029 | -24.2861
Line_3 | 1.8196 | 1.8196 | 3.5617 | 0 | 63.0325 | 63.0325 | -1e-07 | 5.165 | -1e-07 | 5.8603 | 107.4886 | -72.5114 | 0 | 0.12393 | 0 | -23.9029

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79728 | 0.79728 | 0 | 0 | 27.6185 | 27.6185 | 20.9759 | -19.9843 | 17.3767 | -16.2516 | -45.7967 | 134.2033 | 0.98624 | 0.93264 | -6.158 | -6.6781
Line_1 | 0.63574 | 0.63574 | 1.3036 | 0 | 22.0228 | 22.0228 | -14.7741 | 15.4046 | -12.8701 | 13.5855 | 131.9124 | -48.0876 | 0.8897 | 0.93264 | -7.0275 | -6.6781
Line_2 | 0.16402 | 0.16402 | 0 | 0 | 5.6819 | 5.6819 | -4.5378 | 4.5797 | -2.6184 | 2.6661 | 143.1163 | -36.8837 | 0.92205 | 0.93264 | -6.8973 | -6.6781
Line_3 | 0.47591 | 0.47591 | 0.9321 | 0 | 16.4861 | 16.4861 | -10.3898 | 10.7431 | -10.3535 | 10.7544 | 128.0726 | -51.9274 | 0.8897 | 0.92205 | -7.0275 | -6.8973

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79728 | 0.79728 | 0 | 0 | 27.6185 | 27.6185 | 20.9759 | -19.9843 | 17.3767 | -16.2516 | -45.7967 | 134.2033 | 0.98624 | 0.93264 | -6.158 | -6.6781
Line_1 | 0.63574 | 0.63574 | 1.3036 | 0 | 22.0228 | 22.0228 | -14.7741 | 15.4046 | -12.8701 | 13.5855 | 131.9124 | -48.0876 | 0.8897 | 0.93264 | -7.0275 | -6.6781
Line_2 | 0.16402 | 0.16402 | 0 | 0 | 5.6819 | 5.6819 | -4.5378 | 4.5797 | -2.6184 | 2.6661 | 143.1163 | -36.8837 | 0.92205 | 0.93264 | -6.8973 | -6.6781
Line_3 | 0.47591 | 0.47591 | 0.9321 | 0 | 16.4861 | 16.4861 | -10.3898 | 10.7431 | -10.3535 | 10.7544 | 128.0726 | -51.9274 | 0.8897 | 0.92205 | -7.0275 | -6.8973

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36184 | 3.0849 | 3.2334 | 0.36184 | 3.0849 | 3.2334 | 4.1781 | 35.621 | 37.3363 | 4.1781 | 35.621 | 37.3363 | -3.0459 | 29.02 | -12.393 | 3.114 | -24.0714 | 17.8296 | -3.7564 | 3.1835 | 15.3596 | 3.8336 | 2.4312 | -9.1912 | 131.2748 | -159.9336 | 14.078 | -48.7252 | 20.0664 | -165.922 | 1.1575 | 0.81957 | 0.5286 | 1.1821 | 0.6792 | 0.53726 | 2.2371 | -153.6732 | 142.9765 | 2.188 | -165.7008 | 166.8068
Line_1 | 0.18371 | 2.3133 | 2.3918 | 0.18371 | 2.3133 | 2.3918 | 2.1213 | 26.7118 | 27.6179 | 2.1213 | 26.7118 | 27.6179 | 1.6145 | -15.3112 | 16.1185 | -1.597 | 18.0939 | -13.1438 | 1.9532 | 4.4866 | -3.51 | -1.9333 | -1.3293 | 6.8851 | -48.254 | 18.5008 | -165.5462 | 131.746 | -161.4992 | 14.4538 | 1.1946 | 0.5973 | 0.5973 | 1.1821 | 0.6792 | 0.53726 | 2.1688 | -177.8312 | -177.8312 | 2.188 | -165.7008 | 166.8068
Line_2 | 0.17814 | 0.77501 | 0.84184 | 0.17814 | 0.77501 | 0.84184 | 2.057 | 8.949 | 9.7207 | 2.057 | 8.949 | 9.7207 | 1.5335 | -5.6651 | 5.0543 | -1.517 | 5.9775 | -4.6858 | 1.919 | 1.4563 | -1.8879 | -1.9003 | -1.1019 | 2.306 | -49.2111 | 24.7439 | -166.9899 | 130.7889 | -155.2561 | 13.0101 | 1.1942 | 0.65363 | 0.55504 | 1.1821 | 0.6792 | 0.53726 | 2.1597 | -169.6723 | 172.5282 | 2.188 | -165.7008 | 166.8068
Line_3 | 0.006339 | 1.5452 | 1.5504 | 0.006339 | 1.5452 | 1.5504 | 0.073197 | 17.8424 | 17.902 | 0.073197 | 17.8424 | 17.902 | 0.080827 | -10.3755 | 10.4159 | -0.080806 | 11.6171 | -9.166 | 0.03336 | 2.4346 | -2.4179 | -0.033337 | -1.0259 | 3.836 | -20.2589 | 15.3742 | -164.7623 | 159.7411 | -164.6258 | 15.2377 | 1.1946 | 0.5973 | 0.5973 | 1.1942 | 0.65363 | 0.55504 | 2.1688 | -177.8312 | -177.8312 | 2.1597 | -169.6723 | 172.5282

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36184 | 3.0849 | 3.2334 | 0.36184 | 3.0849 | 3.2334 | 4.1781 | 35.621 | 37.3363 | 4.1781 | 35.621 | 37.3363 | -3.0459 | 29.02 | -12.393 | 3.114 | -24.0714 | 17.8296 | -3.7564 | 3.1835 | 15.3596 | 3.8336 | 2.4312 | -9.1912 | 131.2748 | -159.9336 | 14.078 | -48.7252 | 20.0664 | -165.922 | 1.1575 | 0.81957 | 0.5286 | 1.1821 | 0.6792 | 0.53726 | 2.2371 | -153.6732 | 142.9765 | 2.188 | -165.7008 | 166.8068
Line_1 | 0.18371 | 2.3133 | 2.3918 | 0.18371 | 2.3133 | 2.3918 | 2.1213 | 26.7118 | 27.6179 | 2.1213 | 26.7118 | 27.6179 | 1.6145 | -15.3112 | 16.1185 | -1.597 | 18.0939 | -13.1438 | 1.9532 | 4.4866 | -3.51 | -1.9333 | -1.3293 | 6.8851 | -48.254 | 18.5008 | -165.5462 | 131.746 | -161.4992 | 14.4538 | 1.1946 | 0.5973 | 0.5973 | 1.1821 | 0.6792 | 0.53726 | 2.1688 | -177.8312 | -177.8312 | 2.188 | -165.7008 | 166.8068
Line_2 | 0.17814 | 0.77501 | 0.84184 | 0.17814 | 0.77501 | 0.84184 | 2.057 | 8.949 | 9.7207 | 2.057 | 8.949 | 9.7207 | 1.5335 | -5.6651 | 5.0543 | -1.517 | 5.9775 | -4.6858 | 1.919 | 1.4563 | -1.8879 | -1.9003 | -1.1019 | 2.306 | -49.2111 | 24.7439 | -166.9899 | 130.7889 | -155.2561 | 13.0101 | 1.1942 | 0.65363 | 0.55504 | 1.1821 | 0.6792 | 0.53726 | 2.1597 | -169.6723 | 172.5282 | 2.188 | -165.7008 | 166.8068
Line_3 | 0.006339 | 1.5452 | 1.5504 | 0.006339 | 1.5452 | 1.5504 | 0.073197 | 17.8424 | 17.902 | 0.073197 | 17.8424 | 17.902 | 0.080827 | -10.3755 | 10.4159 | -0.080806 | 11.6171 | -9.166 | 0.03336 | 2.4346 | -2.4179 | -0.033337 | -1.0259 | 3.836 | -20.2589 | 15.3742 | -164.7623 | 159.7411 | -164.6258 | 15.2377 | 1.1946 | 0.5973 | 0.5973 | 1.1942 | 0.65363 | 0.55504 | 2.1688 | -177.8312 | -177.8312 | 2.1597 | -169.6723 | 172.5282

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26649 | 1.2614 | 1.2336 | 0.26649 | 1.2614 | 1.2336 | 3.0772 | 14.5653 | 14.2444 | 3.0772 | 14.5653 | 14.2444 | -1.7911 | 15.2178 | 0.28699 | 1.8281 | -14.3904 | 0.50433 | -3.0409 | 0.78464 | 12.1494 | 3.0828 | 0.15412 | -11.2516 | 121.7957 | -136.1541 | 31.6491 | -58.2043 | 43.8459 | -148.3509 | 1.1469 | 1.0462 | 0.85317 | 1.1647 | 0.98805 | 0.79069 | 1.2969 | -133.2025 | 120.296 | 1.1282 | -136.7676 | 124.2156
Line_1 | 0.13441 | 0.95605 | 0.94778 | 0.13441 | 0.95605 | 0.94778 | 1.552 | 11.0395 | 10.944 | 1.552 | 11.0395 | 10.944 | 0.95258 | -10.4164 | 0.79274 | -0.94319 | 10.8917 | -0.32563 | 1.5527 | -0.049073 | -8.1172 | -1.542 | 0.58835 | 8.6472 | -57.42 | 40.1404 | -147.941 | 122.58 | -139.8596 | 32.059 | 1.1737 | 0.94357 | 0.74523 | 1.1647 | 0.98805 | 0.79069 | 1.051 | -139.5897 | 127.6369 | 1.1282 | -136.7676 | 124.2156
Line_2 | 0.13211 | 0.31349 | 0.28593 | 0.13211 | 0.31349 | 0.28593 | 1.5255 | 3.6199 | 3.3016 | 1.5255 | 3.6199 | 3.3016 | 0.89397 | -3.4476 | 0.22121 | -0.88489 | 3.4987 | -0.1787 | 1.5511 | 0.80045 | -2.5562 | -1.5408 | -0.74246 | 2.6044 | -59.0022 | 55.2134 | -149.7095 | 120.9978 | -124.7866 | 30.2905 | 1.1735 | 0.97774 | 0.77712 | 1.1647 | 0.98805 | 0.79069 | 1.0404 | -137.8576 | 125.2365 | 1.1282 | -136.7676 | 124.2156
Line_3 | 0.0043354 | 0.65841 | 0.66204 | 0.0043354 | 0.65841 | 0.66204 | 0.050061 | 7.6027 | 7.6446 | 0.050061 | 7.6027 | 7.6446 | 0.058746 | -7.1142 | 0.47813 | -0.058736 | 7.3396 | -0.25021 | 0.0012086 | -0.92175 | -5.6769 | -0.0011976 | 1.1775 | 5.9355 | -0.1276 | 33.0278 | -147.1774 | 179.8724 | -146.9722 | 32.8226 | 1.1737 | 0.94357 | 0.74523 | 1.1735 | 0.97774 | 0.77712 | 1.051 | -139.5897 | 127.6369 | 1.0404 | -137.8576 | 125.2365

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26649 | 1.2614 | 1.2336 | 0.26649 | 1.2614 | 1.2336 | 3.0772 | 14.5653 | 14.2444 | 3.0772 | 14.5653 | 14.2444 | -1.7911 | 15.2178 | 0.28699 | 1.8281 | -14.3904 | 0.50433 | -3.0409 | 0.78464 | 12.1494 | 3.0828 | 0.15412 | -11.2516 | 121.7957 | -136.1541 | 31.6491 | -58.2043 | 43.8459 | -148.3509 | 1.1469 | 1.0462 | 0.85317 | 1.1647 | 0.98805 | 0.79069 | 1.2969 | -133.2025 | 120.296 | 1.1282 | -136.7676 | 124.2156
Line_1 | 0.13441 | 0.95605 | 0.94778 | 0.13441 | 0.95605 | 0.94778 | 1.552 | 11.0395 | 10.944 | 1.552 | 11.0395 | 10.944 | 0.95258 | -10.4164 | 0.79274 | -0.94319 | 10.8917 | -0.32563 | 1.5527 | -0.049073 | -8.1172 | -1.542 | 0.58835 | 8.6472 | -57.42 | 40.1404 | -147.941 | 122.58 | -139.8596 | 32.059 | 1.1737 | 0.94357 | 0.74523 | 1.1647 | 0.98805 | 0.79069 | 1.051 | -139.5897 | 127.6369 | 1.1282 | -136.7676 | 124.2156
Line_2 | 0.13211 | 0.31349 | 0.28593 | 0.13211 | 0.31349 | 0.28593 | 1.5255 | 3.6199 | 3.3016 | 1.5255 | 3.6199 | 3.3016 | 0.89397 | -3.4476 | 0.22121 | -0.88489 | 3.4987 | -0.1787 | 1.5511 | 0.80045 | -2.5562 | -1.5408 | -0.74246 | 2.6044 | -59.0022 | 55.2134 | -149.7095 | 120.9978 | -124.7866 | 30.2905 | 1.1735 | 0.97774 | 0.77712 | 1.1647 | 0.98805 | 0.79069 | 1.0404 | -137.8576 | 125.2365 | 1.1282 | -136.7676 | 124.2156
Line_3 | 0.0043354 | 0.65841 | 0.66204 | 0.0043354 | 0.65841 | 0.66204 | 0.050061 | 7.6027 | 7.6446 | 0.050061 | 7.6027 | 7.6446 | 0.058746 | -7.1142 | 0.47813 | -0.058736 | 7.3396 | -0.25021 | 0.0012086 | -0.92175 | -5.6769 | -0.0011976 | 1.1775 | 5.9355 | -0.1276 | 33.0278 | -147.1774 | 179.8724 | -146.9722 | 32.8226 | 1.1737 | 0.94357 | 0.74523 | 1.1735 | 0.97774 | 0.77712 | 1.051 | -139.5897 | 127.6369 | 1.0404 | -137.8576 | 125.2365

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.8895 | 0.98177 | 0.71964 | 1.8876 | 0.98378 | 0.72163 | 21.8175 | 11.3365 | 8.3097 | 21.796 | 11.3597 | 8.3327 | 5.5158 | -12.2628 | 10.2706 | -3.2285 | 13.1908 | -10.079 | 6.71 | 5.6012 | 3.5851 | -2.8711 | -5.8843 | -3.9746 | -63.3891 | 76.8561 | 107.1505 | 116.638 | -103.1142 | -72.8951 |  | 0.39812 | 1.1892 | 1.3091 | 0.19822 | 1.2715 | 1.3002 | -12.8104 | -127.6932 | 126.3926 | -21.7152 | -127.1556 | 128.6266
Line_1 | 1.618 | 0.52135 | 0.37512 | 1.6203 | 0.5189 | 0.37263 | 18.683 | 6.0201 | 4.3315 | 18.7102 | 5.9917 | 4.3027 | 6.825e-11 | 7.1244 | -5.2424 | 2.6255 | -7.0584 | 5.0429 | -6.8823e-11 | -3.2521 | -2.6601 | 2.6195 | 2.8669 | 2.4224 | 113.3861 | -104.9744 | -77.1145 | -66.6489 | 74.95 | 102.9691 |  | 0 | 1.3009 | 1.3572 | 0.19822 | 1.2715 | 1.3002 | 0 | -129.5097 | 129.7896 | -21.7152 | -127.1556 | 128.6266
Line_2 | 0.28364 | 0.4677 | 0.35323 | 0.28544 | 0.46551 | 0.351 | 3.2752 | 5.4005 | 4.0788 | 3.296 | 5.3752 | 4.053 | -0.69027 | 6.5779 | -4.7808 | 0.60294 | -6.1324 | 5.0361 | -0.062822 | -2.8538 | -1.5835 | 0.25163 | 3.0174 | 1.5522 | 135.9213 | -100.8684 | -68.596 | -44.3676 | 79.0436 | 111.496 |  | 0.21162 | 1.3277 | 1.2347 | 0.19822 | 1.2715 | 1.3002 | -38.8785 | -124.3217 | 129.7298 | -21.7152 | -127.1556 | 128.6266
Line_3 | 1.3592 | 0.064894 | 0.058875 | 1.3617 | 0.063292 | 0.057433 | 15.6949 | 0.74934 | 0.67983 | 15.7233 | 0.73083 | 0.66317 | 6.1765e-11 | 0.96946 | -0.0052174 | 2.8113 | -0.94564 | -0.02395 | -5.3055e-11 | 0.10193 | -0.92264 | 1.7799 | -0.21747 | 0.81849 | 108.8088 | -135.5116 | -139.8864 | -71.2176 | 42.7269 | 38.0537 |  | 0 | 1.3009 | 1.3572 | 0.21162 | 1.3277 | 1.2347 | 0 | -129.5097 | 129.7896 | -38.8785 | -124.3217 | 129.7298

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.8895 | 0.98177 | 0.71964 | 1.8876 | 0.98378 | 0.72163 | 21.8175 | 11.3365 | 8.3097 | 21.796 | 11.3597 | 8.3327 | 5.5158 | -12.2628 | 10.2706 | -3.2285 | 13.1908 | -10.079 | 6.71 | 5.6012 | 3.5851 | -2.8711 | -5.8843 | -3.9746 | -63.3891 | 76.8561 | 107.1505 | 116.638 | -103.1142 | -72.8951 |  | 0.39812 | 1.1892 | 1.3091 | 0.19822 | 1.2715 | 1.3002 | -12.8104 | -127.6932 | 126.3926 | -21.7152 | -127.1556 | 128.6266
Line_1 | 1.618 | 0.52135 | 0.37512 | 1.6203 | 0.5189 | 0.37263 | 18.683 | 6.0201 | 4.3315 | 18.7102 | 5.9917 | 4.3027 | 6.825e-11 | 7.1244 | -5.2424 | 2.6255 | -7.0584 | 5.0429 | -6.8823e-11 | -3.2521 | -2.6601 | 2.6195 | 2.8669 | 2.4224 | 113.3861 | -104.9744 | -77.1145 | -66.6489 | 74.95 | 102.9691 |  | 0 | 1.3009 | 1.3572 | 0.19822 | 1.2715 | 1.3002 | 0 | -129.5097 | 129.7896 | -21.7152 | -127.1556 | 128.6266
Line_2 | 0.28364 | 0.4677 | 0.35323 | 0.28544 | 0.46551 | 0.351 | 3.2752 | 5.4005 | 4.0788 | 3.296 | 5.3752 | 4.053 | -0.69027 | 6.5779 | -4.7808 | 0.60294 | -6.1324 | 5.0361 | -0.062822 | -2.8538 | -1.5835 | 0.25163 | 3.0174 | 1.5522 | 135.9213 | -100.8684 | -68.596 | -44.3676 | 79.0436 | 111.496 |  | 0.21162 | 1.3277 | 1.2347 | 0.19822 | 1.2715 | 1.3002 | -38.8785 | -124.3217 | 129.7298 | -21.7152 | -127.1556 | 128.6266
Line_3 | 1.3592 | 0.064894 | 0.058875 | 1.3617 | 0.063292 | 0.057433 | 15.6949 | 0.74934 | 0.67983 | 15.7233 | 0.73083 | 0.66317 | 6.1765e-11 | 0.96946 | -0.0052174 | 2.8113 | -0.94564 | -0.02395 | -5.3055e-11 | 0.10193 | -0.92264 | 1.7799 | -0.21747 | 0.81849 | 108.8088 | -135.5116 | -139.8864 | -71.2176 | 42.7269 | 38.0537 |  | 0 | 1.3009 | 1.3572 | 0.21162 | 1.3277 | 1.2347 | 0 | -129.5097 | 129.7896 | -38.8785 | -124.3217 | 129.7298

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4873 | 0.27231 | 0.28869 | 0.48679 | 0.27277 | 0.28909 | 5.6269 | 3.1444 | 3.3335 | 5.6209 | 3.1496 | 3.3382 | 4.8015 | -3.6792 | 3.0074 | -4.6079 | 3.7938 | -3.03 | 2.149 | 0.36655 | -2.5396 | -1.8718 | -0.3729 | 2.5208 | -30.3851 | 63.8826 | 163.4928 | 149.6637 | -116.0151 | -16.6117 |  | 0.93489 | 1.1759 | 1.1808 | 0.88483 | 1.2103 | 1.1807 | -6.2733 | -121.8068 | 123.3138 | -8.2289 | -121.6288 | 123.6299
Line_1 | 0.45254 | 0.14814 | 0.14226 | 0.45326 | 0.14758 | 0.14172 | 5.2255 | 1.7106 | 1.6426 | 5.2338 | 1.7041 | 1.6365 | -3.6901 | 2.0872 | -1.602 | 3.9238 | -2.0526 | 1.5564 | -2.2488 | -0.24336 | 1.1433 | 2.4596 | 0.20147 | -1.1451 | 139.7398 | -115.7934 | -20.2772 | -40.3107 | 63.9769 | 159.9731 |  | 0.82696 | 1.2284 | 1.1982 | 0.88483 | 1.2103 | 1.1807 | -8.9014 | -122.4439 | 124.2085 | -8.2289 | -121.6288 | 123.6299
Line_2 | 0.088354 | 0.12563 | 0.14834 | 0.088283 | 0.12519 | 0.14786 | 1.0202 | 1.4507 | 1.7129 | 1.0194 | 1.4455 | 1.7074 | -0.67136 | 1.7736 | -1.4547 | 0.6841 | -1.7411 | 1.4736 | 0.61711 | -0.1517 | 1.361 | -0.58789 | 0.17143 | -1.3757 | -147.0777 | -115.7362 | -13.5553 | 32.4455 | 63.9943 | 166.6615 |  | 0.89382 | 1.2271 | 1.163 | 0.88483 | 1.2103 | 1.1807 | -9.6666 | -120.6249 | 123.3513 | -8.2289 | -121.6288 | 123.6299
Line_3 | 0.43491 | 0.022713 | 0.01823 | 0.4357 | 0.022195 | 0.017835 | 5.0219 | 0.26226 | 0.2105 | 5.031 | 0.25629 | 0.20594 | -3.0591 | 0.31968 | -0.087612 | 3.3513 | -0.31383 | 0.077657 | -2.8087 | -0.039934 | -0.23651 | 2.9983 | 0.020274 | 0.22657 | 128.5417 | -115.3235 | -125.465 | -51.4844 | 63.0714 | 52.2708 |  | 0.82696 | 1.2284 | 1.1982 | 0.89382 | 1.2271 | 1.163 | -8.9014 | -122.4439 | 124.2085 | -9.6666 | -120.6249 | 123.3513

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.4873 | 0.27231 | 0.28869 | 0.48679 | 0.27277 | 0.28909 | 5.6269 | 3.1444 | 3.3335 | 5.6209 | 3.1496 | 3.3382 | 4.8015 | -3.6792 | 3.0074 | -4.6079 | 3.7938 | -3.03 | 2.149 | 0.36655 | -2.5396 | -1.8718 | -0.3729 | 2.5208 | -30.3851 | 63.8826 | 163.4928 | 149.6637 | -116.0151 | -16.6117 |  | 0.93489 | 1.1759 | 1.1808 | 0.88483 | 1.2103 | 1.1807 | -6.2733 | -121.8068 | 123.3138 | -8.2289 | -121.6288 | 123.6299
Line_1 | 0.45254 | 0.14814 | 0.14226 | 0.45326 | 0.14758 | 0.14172 | 5.2255 | 1.7106 | 1.6426 | 5.2338 | 1.7041 | 1.6365 | -3.6901 | 2.0872 | -1.602 | 3.9238 | -2.0526 | 1.5564 | -2.2488 | -0.24336 | 1.1433 | 2.4596 | 0.20147 | -1.1451 | 139.7398 | -115.7934 | -20.2772 | -40.3107 | 63.9769 | 159.9731 |  | 0.82696 | 1.2284 | 1.1982 | 0.88483 | 1.2103 | 1.1807 | -8.9014 | -122.4439 | 124.2085 | -8.2289 | -121.6288 | 123.6299
Line_2 | 0.088354 | 0.12563 | 0.14834 | 0.088283 | 0.12519 | 0.14786 | 1.0202 | 1.4507 | 1.7129 | 1.0194 | 1.4455 | 1.7074 | -0.67136 | 1.7736 | -1.4547 | 0.6841 | -1.7411 | 1.4736 | 0.61711 | -0.1517 | 1.361 | -0.58789 | 0.17143 | -1.3757 | -147.0777 | -115.7362 | -13.5553 | 32.4455 | 63.9943 | 166.6615 |  | 0.89382 | 1.2271 | 1.163 | 0.88483 | 1.2103 | 1.1807 | -9.6666 | -120.6249 | 123.3513 | -8.2289 | -121.6288 | 123.6299
Line_3 | 0.43491 | 0.022713 | 0.01823 | 0.4357 | 0.022195 | 0.017835 | 5.0219 | 0.26226 | 0.2105 | 5.031 | 0.25629 | 0.20594 | -3.0591 | 0.31968 | -0.087612 | 3.3513 | -0.31383 | 0.077657 | -2.8087 | -0.039934 | -0.23651 | 2.9983 | 0.020274 | 0.22657 | 128.5417 | -115.3235 | -125.465 | -51.4844 | 63.0714 | 52.2708 |  | 0.82696 | 1.2284 | 1.1982 | 0.89382 | 1.2271 | 1.163 | -8.9014 | -122.4439 | 124.2085 | -9.6666 | -120.6249 | 123.3513

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.649 | 0.81289 | 0.67968 | 1.6477 | 0.8143 | 0.68107 | 19.0409 | 9.3864 | 7.8482 | 19.0259 | 9.4027 | 7.8644 | 7.5924 | -6.5292 | 8.1314 | -4.3235 | 7.243 | -7.7084 | 5.7889 | 6.8162 | 2.3999 | -2.4757 | -7.3212 | -2.8735 | -57.1288 | 102.2861 | 106.7435 | 122.8899 | -77.7173 | -73.2698 |  | 0.50142 | 1.0056 | 1.0803 | 0.26186 | 1.0953 | 1.0461 | -19.8048 | -123.9457 | 123.1868 | -27.3139 | -123.0248 | 127.1741
Line_1 | 1.3737 | 0.43926 | 0.36873 | 1.3755 | 0.43727 | 0.36675 | 15.8626 | 5.0721 | 4.2578 | 15.8834 | 5.0492 | 4.2349 | -3.7229e-11 | 4.1124 | -4.151 | 3.5214 | -4.2385 | 3.9559 | 4.0275e-12 | -3.9845 | -2.3532 | 2.2134 | 3.5524 | 1.9939 | 120.5693 | -83.0624 | -79.6001 | -59.4653 | 96.9426 | 100.4246 |  | 0 | 1.1289 | 1.1207 | 0.26186 | 1.0953 | 1.0461 | 0 | -127.1578 | 129.9493 | -27.3139 | -123.0248 | 127.1741
Line_2 | 0.27758 | 0.38277 | 0.32076 | 0.27909 | 0.3811 | 0.31909 | 3.2052 | 4.4198 | 3.7038 | 3.2226 | 4.4006 | 3.6846 | -0.94899 | 3.5242 | -3.37 | 0.80208 | -3.0045 | 3.7526 | -0.083551 | -3.7207 | -0.87205 | 0.26232 | 3.7688 | 0.87959 | 134.7203 | -71.5813 | -66.0395 | -45.424 | 108.4127 | 113.9823 |  | 0.29723 | 1.1595 | 0.93986 | 0.26186 | 1.0953 | 1.0461 | -40.2483 | -118.1348 | 128.4685 | -27.3139 | -123.0248 | 127.1741
Line_3 | 1.1058 | 0.09988 | 0.094607 | 1.1077 | 0.09878 | 0.093493 | 12.769 | 1.1533 | 1.0924 | 12.7908 | 1.1406 | 1.0796 | -3.0111e-11 | 1.2963 | -0.17148 | 3.5067 | -1.2757 | 0.15098 | 1.398e-12 | 0.12136 | -1.2122 | 1.4686 | -0.34899 | 1.0033 | 117.0531 | -132.5062 | -131.9988 | -62.972 | 46.565 | 47.026 |  | 0 | 1.1289 | 1.1207 | 0.29723 | 1.1595 | 0.93986 | 0 | -127.1578 | 129.9493 | -40.2483 | -118.1348 | 128.4685

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.649 | 0.81289 | 0.67968 | 1.6477 | 0.8143 | 0.68107 | 19.0409 | 9.3864 | 7.8482 | 19.0259 | 9.4027 | 7.8644 | 7.5924 | -6.5292 | 8.1314 | -4.3235 | 7.243 | -7.7084 | 5.7889 | 6.8162 | 2.3999 | -2.4757 | -7.3212 | -2.8735 | -57.1288 | 102.2861 | 106.7435 | 122.8899 | -77.7173 | -73.2698 |  | 0.50142 | 1.0056 | 1.0803 | 0.26186 | 1.0953 | 1.0461 | -19.8048 | -123.9457 | 123.1868 | -27.3139 | -123.0248 | 127.1741
Line_1 | 1.3737 | 0.43926 | 0.36873 | 1.3755 | 0.43727 | 0.36675 | 15.8626 | 5.0721 | 4.2578 | 15.8834 | 5.0492 | 4.2349 | -3.7229e-11 | 4.1124 | -4.151 | 3.5214 | -4.2385 | 3.9559 | 4.0275e-12 | -3.9845 | -2.3532 | 2.2134 | 3.5524 | 1.9939 | 120.5693 | -83.0624 | -79.6001 | -59.4653 | 96.9426 | 100.4246 |  | 0 | 1.1289 | 1.1207 | 0.26186 | 1.0953 | 1.0461 | 0 | -127.1578 | 129.9493 | -27.3139 | -123.0248 | 127.1741
Line_2 | 0.27758 | 0.38277 | 0.32076 | 0.27909 | 0.3811 | 0.31909 | 3.2052 | 4.4198 | 3.7038 | 3.2226 | 4.4006 | 3.6846 | -0.94899 | 3.5242 | -3.37 | 0.80208 | -3.0045 | 3.7526 | -0.083551 | -3.7207 | -0.87205 | 0.26232 | 3.7688 | 0.87959 | 134.7203 | -71.5813 | -66.0395 | -45.424 | 108.4127 | 113.9823 |  | 0.29723 | 1.1595 | 0.93986 | 0.26186 | 1.0953 | 1.0461 | -40.2483 | -118.1348 | 128.4685 | -27.3139 | -123.0248 | 127.1741
Line_3 | 1.1058 | 0.09988 | 0.094607 | 1.1077 | 0.09878 | 0.093493 | 12.769 | 1.1533 | 1.0924 | 12.7908 | 1.1406 | 1.0796 | -3.0111e-11 | 1.2963 | -0.17148 | 3.5067 | -1.2757 | 0.15098 | 1.398e-12 | 0.12136 | -1.2122 | 1.4686 | -0.34899 | 1.0033 | 117.0531 | -132.5062 | -131.9988 | -62.972 | 46.565 | 47.026 |  | 0 | 1.1289 | 1.1207 | 0.29723 | 1.1595 | 0.93986 | 0 | -127.1578 | 129.9493 | -40.2483 | -118.1348 | 128.4685

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53569 | 0.26408 | 0.2208 | 0.53527 | 0.26453 | 0.22125 | 6.1856 | 3.0493 | 2.5496 | 6.1807 | 3.0546 | 2.5548 | 4.3799 | -1.5527 | 2.5983 | -4.0329 | 1.6296 | -2.5573 | 2.9802 | 2.6508 | -0.065035 | -2.6275 | -2.7074 | 0.015308 | -40.9861 | 118.4288 | 122.8862 | 139.0327 | -61.5746 | -57.1271 |  | 0.85645 | 1.0075 | 1.0194 | 0.77876 | 1.0345 | 1.001 | -6.7541 | -121.2116 | 121.4524 | -7.8826 | -120.5299 | 122.53
Line_1 | 0.44627 | 0.1427 | 0.11979 | 0.44686 | 0.14205 | 0.11914 | 5.1531 | 1.6477 | 1.3832 | 5.1599 | 1.6403 | 1.3757 | -2.8997 | 0.99593 | -1.3954 | 3.2738 | -1.0066 | 1.3697 | -2.0919 | -1.4162 | -0.18103 | 2.33 | 1.3661 | 0.14305 | 136.712 | -66.9196 | -63.4573 | -43.3226 | 113.0853 | 116.5673 |  | 0.69385 | 1.0507 | 1.0173 | 0.77876 | 1.0345 | 1.001 | -7.4796 | -121.8023 | 123.9343 | -7.8826 | -120.5299 | 122.53
Line_2 | 0.090173 | 0.12435 | 0.1042 | 0.090665 | 0.1238 | 0.10366 | 1.0412 | 1.4358 | 1.2032 | 1.0469 | 1.4296 | 1.197 | -0.77161 | 0.6791 | -1.1515 | 0.75909 | -0.62302 | 1.1876 | -0.27545 | -1.3404 | 0.16016 | 0.29746 | 1.3413 | -0.15836 | 150.863 | -55.4386 | -49.8968 | -29.2812 | 124.5555 | 130.125 |  | 0.78686 | 1.0465 | 0.96624 | 0.77876 | 1.0345 | 1.001 | -9.4917 | -118.5694 | 122.1847 | -7.8826 | -120.5299 | 122.53
Line_3 | 0.35924 | 0.032447 | 0.030734 | 0.35985 | 0.03209 | 0.030372 | 4.1481 | 0.37466 | 0.35489 | 4.1552 | 0.37054 | 0.35071 | -2.2265 | 0.39189 | -0.18166 | 2.5996 | -0.38767 | 0.17445 | -1.8239 | -0.037313 | -0.312 | 1.983 | 0.0086427 | 0.29051 | 133.1958 | -116.3634 | -115.856 | -46.8292 | 62.7078 | 63.1687 |  | 0.69385 | 1.0507 | 1.0173 | 0.78686 | 1.0465 | 0.96624 | -7.4796 | -121.8023 | 123.9343 | -9.4917 | -118.5694 | 122.1847

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53569 | 0.26408 | 0.2208 | 0.53527 | 0.26453 | 0.22125 | 6.1856 | 3.0493 | 2.5496 | 6.1807 | 3.0546 | 2.5548 | 4.3799 | -1.5527 | 2.5983 | -4.0329 | 1.6296 | -2.5573 | 2.9802 | 2.6508 | -0.065035 | -2.6275 | -2.7074 | 0.015308 | -40.9861 | 118.4288 | 122.8862 | 139.0327 | -61.5746 | -57.1271 |  | 0.85645 | 1.0075 | 1.0194 | 0.77876 | 1.0345 | 1.001 | -6.7541 | -121.2116 | 121.4524 | -7.8826 | -120.5299 | 122.53
Line_1 | 0.44627 | 0.1427 | 0.11979 | 0.44686 | 0.14205 | 0.11914 | 5.1531 | 1.6477 | 1.3832 | 5.1599 | 1.6403 | 1.3757 | -2.8997 | 0.99593 | -1.3954 | 3.2738 | -1.0066 | 1.3697 | -2.0919 | -1.4162 | -0.18103 | 2.33 | 1.3661 | 0.14305 | 136.712 | -66.9196 | -63.4573 | -43.3226 | 113.0853 | 116.5673 |  | 0.69385 | 1.0507 | 1.0173 | 0.77876 | 1.0345 | 1.001 | -7.4796 | -121.8023 | 123.9343 | -7.8826 | -120.5299 | 122.53
Line_2 | 0.090173 | 0.12435 | 0.1042 | 0.090665 | 0.1238 | 0.10366 | 1.0412 | 1.4358 | 1.2032 | 1.0469 | 1.4296 | 1.197 | -0.77161 | 0.6791 | -1.1515 | 0.75909 | -0.62302 | 1.1876 | -0.27545 | -1.3404 | 0.16016 | 0.29746 | 1.3413 | -0.15836 | 150.863 | -55.4386 | -49.8968 | -29.2812 | 124.5555 | 130.125 |  | 0.78686 | 1.0465 | 0.96624 | 0.77876 | 1.0345 | 1.001 | -9.4917 | -118.5694 | 122.1847 | -7.8826 | -120.5299 | 122.53
Line_3 | 0.35924 | 0.032447 | 0.030734 | 0.35985 | 0.03209 | 0.030372 | 4.1481 | 0.37466 | 0.35489 | 4.1552 | 0.37054 | 0.35071 | -2.2265 | 0.39189 | -0.18166 | 2.5996 | -0.38767 | 0.17445 | -1.8239 | -0.037313 | -0.312 | 1.983 | 0.0086427 | 0.29051 | 133.1958 | -116.3634 | -115.856 | -46.8292 | 62.7078 | 63.1687 |  | 0.69385 | 1.0507 | 1.0173 | 0.78686 | 1.0465 | 0.96624 | -7.4796 | -121.8023 | 123.9343 | -9.4917 | -118.5694 | 122.1847

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53928 | 3.3522 | 2.988 | 0.54087 | 3.3525 | 2.9874 | 6.227 | 38.7083 | 34.5022 | 6.2454 | 38.7108 | 34.4956 | -2.6798 | 15.6063 | 3.7668 | 3.0717 | -7.1388 | -1.4472 | 7.6875 | 9.7921 | 11.6782 | -7.8908 | -2.9666 | -6.1022 | -109.1438 | -168.5423 | 23.1831 | 70.9282 | 11.4869 | -156.8482 |  | 1.3074 | 0.47597 | 0.35565 | 1.3558 | 0.1997 | 0.1818 | 0.074166 | -136.4364 | 95.306 | 2.1983 | -145.9473 | 99.8097
Line_1 | 0.295 | 2.5198 | 2.2659 | 0.29308 | 2.5197 | 2.2668 | 3.4063 | 29.0966 | 26.1645 | 3.3842 | 29.0953 | 26.1745 | 1.9047 | 6.3524e-11 | 7.4651e-11 | -1.8677 | 5.1579 | 1.4585 | -4.4241 | -5.5892e-11 | -3.8897e-12 | 4.1909 | 2.6754 | 4.5296 | 68.3547 | 6.6852 | -152.3913 | -111.8223 | -173.363 | 27.6578 |  | 1.414 | 0 | 0 | 1.3558 | 0.1997 | 0.1818 | 1.6474 | 0 | 0 | 2.1983 | -145.9473 | 99.8097
Line_2 | 0.25025 | 0.86881 | 0.74915 | 0.24853 | 0.86829 | 0.74912 | 2.8897 | 10.0321 | 8.6504 | 2.8697 | 10.0262 | 8.6501 | 1.3648 | -1.401 | 0.26031 | -1.204 | 1.981 | -0.011258 | -3.6485 | 0.60431 | -1.6567 | 3.6998 | 0.29123 | 1.5726 | 74.365 | 25.8114 | -170.7472 | -105.8277 | -154.3106 | 9.3995 |  | 1.348 | 0.15209 | 0.19387 | 1.3558 | 0.1997 | 0.1818 | 4.8749 | -177.5218 | 108.1822 | 2.1983 | -145.9473 | 99.8097
Line_3 | 0.05345 | 1.7224 | 1.5723 | 0.052351 | 1.7228 | 1.5733 | 0.61718 | 19.8884 | 18.1556 | 0.6045 | 19.8928 | 18.1674 | 0.68727 | 4.912e-11 | 5.0815e-11 | -0.68451 | 3.0123 | 1.0936 | -0.53786 | -3.053e-11 | -1.041e-11 | 0.44214 | 0.28173 | 3.3481 | 39.6942 | -2.7956 | -143.7963 | -142.2657 | 177.1351 | 36.2713 |  | 1.414 | 0 | 0 | 1.348 | 0.15209 | 0.19387 | 1.6474 | 0 | 0 | 4.8749 | -177.5218 | 108.1822

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53928 | 3.3522 | 2.988 | 0.54087 | 3.3525 | 2.9874 | 6.227 | 38.7083 | 34.5022 | 6.2454 | 38.7108 | 34.4956 | -2.6798 | 15.6063 | 3.7668 | 3.0717 | -7.1388 | -1.4472 | 7.6875 | 9.7921 | 11.6782 | -7.8908 | -2.9666 | -6.1022 | -109.1438 | -168.5423 | 23.1831 | 70.9282 | 11.4869 | -156.8482 |  | 1.3074 | 0.47597 | 0.35565 | 1.3558 | 0.1997 | 0.1818 | 0.074166 | -136.4364 | 95.306 | 2.1983 | -145.9473 | 99.8097
Line_1 | 0.295 | 2.5198 | 2.2659 | 0.29308 | 2.5197 | 2.2668 | 3.4063 | 29.0966 | 26.1645 | 3.3842 | 29.0953 | 26.1745 | 1.9047 | 6.3524e-11 | 7.4651e-11 | -1.8677 | 5.1579 | 1.4585 | -4.4241 | -5.5892e-11 | -3.8897e-12 | 4.1909 | 2.6754 | 4.5296 | 68.3547 | 6.6852 | -152.3913 | -111.8223 | -173.363 | 27.6578 |  | 1.414 | 0 | 0 | 1.3558 | 0.1997 | 0.1818 | 1.6474 | 0 | 0 | 2.1983 | -145.9473 | 99.8097
Line_2 | 0.25025 | 0.86881 | 0.74915 | 0.24853 | 0.86829 | 0.74912 | 2.8897 | 10.0321 | 8.6504 | 2.8697 | 10.0262 | 8.6501 | 1.3648 | -1.401 | 0.26031 | -1.204 | 1.981 | -0.011258 | -3.6485 | 0.60431 | -1.6567 | 3.6998 | 0.29123 | 1.5726 | 74.365 | 25.8114 | -170.7472 | -105.8277 | -154.3106 | 9.3995 |  | 1.348 | 0.15209 | 0.19387 | 1.3558 | 0.1997 | 0.1818 | 4.8749 | -177.5218 | 108.1822 | 2.1983 | -145.9473 | 99.8097
Line_3 | 0.05345 | 1.7224 | 1.5723 | 0.052351 | 1.7228 | 1.5733 | 0.61718 | 19.8884 | 18.1556 | 0.6045 | 19.8928 | 18.1674 | 0.68727 | 4.912e-11 | 5.0815e-11 | -0.68451 | 3.0123 | 1.0936 | -0.53786 | -3.053e-11 | -1.041e-11 | 0.44214 | 0.28173 | 3.3481 | 39.6942 | -2.7956 | -143.7963 | -142.2657 | 177.1351 | 36.2713 |  | 1.414 | 0 | 0 | 1.348 | 0.15209 | 0.19387 | 1.6474 | 0 | 0 | 4.8749 | -177.5218 | 108.1822

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.038815 | 0.80438 | 0.61382 | 0.039326 | 0.80459 | 0.61349 | 0.44819 | 9.2882 | 7.0878 | 0.4541 | 9.2907 | 7.084 | -0.14235 | 8.6693 | 3.5072 | 0.14825 | -8.1113 | -3.4677 | 0.51997 | 2.4592 | 5.8011 | -0.53493 | -2.1046 | -5.519 | -104.3266 | -139.5524 | 52.3785 | 76.1924 | 40.4893 | -127.6709 |  | 1.2028 | 0.97019 | 0.95642 | 1.2224 | 0.90197 | 0.9201 | 0.98344 | -123.7153 | 111.2219 | 1.6826 | -124.965 | 110.1872
Line_1 | 0.029802 | 0.61812 | 0.52845 | 0.029227 | 0.61799 | 0.52891 | 0.34412 | 7.1375 | 6.102 | 0.33749 | 7.1359 | 6.1073 | 0.16307 | -5.497 | -3.3054 | -0.16382 | 5.8425 | 3.3875 | -0.39723 | -2.5828 | -4.173 | 0.37863 | 2.7004 | 4.4835 | 69.268 | 30.2983 | -122.8059 | -111.7143 | -149.7715 | 57.2603 |  | 1.2478 | 0.85094 | 0.87242 | 1.2224 | 0.90197 | 0.9201 | 1.5869 | -124.5353 | 108.8123 | 1.6826 | -124.965 | 110.1872
Line_2 | 0.011782 | 0.2257 | 0.097787 | 0.011128 | 0.22523 | 0.097759 | 0.13605 | 2.6061 | 1.1291 | 0.1285 | 2.6007 | 1.1288 | -0.017313 | -2.2108 | -0.06955 | 0.015571 | 2.2688 | 0.080173 | -0.16461 | 0.66104 | -1.0503 | 0.1563 | -0.59579 | 1.0355 | 98.4885 | 69.8769 | -155.7902 | -82.6283 | -110.2514 | 24.6144 |  | 1.2166 | 0.88541 | 0.93221 | 1.2224 | 0.90197 | 0.9201 | 2.4844 | -126.7702 | 110.4213 | 1.6826 | -124.965 | 110.1872
Line_3 | 0.02048 | 0.46675 | 0.4494 | 0.020113 | 0.46691 | 0.44988 | 0.23648 | 5.3896 | 5.1892 | 0.23224 | 5.3914 | 5.1948 | 0.18101 | -3.3506 | -3.2093 | -0.18395 | 3.6069 | 3.3402 | -0.23305 | -3.1316 | -3.1931 | 0.21446 | 3.1269 | 3.5063 | 53.7506 | 12.3992 | -116.0426 | -128.1358 | -167.6924 | 64.0319 |  | 1.2478 | 0.85094 | 0.87242 | 1.2166 | 0.88541 | 0.93221 | 1.5869 | -124.5353 | 108.8123 | 2.4844 | -126.7702 | 110.4213

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.038815 | 0.80438 | 0.61382 | 0.039326 | 0.80459 | 0.61349 | 0.44819 | 9.2882 | 7.0878 | 0.4541 | 9.2907 | 7.084 | -0.14235 | 8.6693 | 3.5072 | 0.14825 | -8.1113 | -3.4677 | 0.51997 | 2.4592 | 5.8011 | -0.53493 | -2.1046 | -5.519 | -104.3266 | -139.5524 | 52.3785 | 76.1924 | 40.4893 | -127.6709 |  | 1.2028 | 0.97019 | 0.95642 | 1.2224 | 0.90197 | 0.9201 | 0.98344 | -123.7153 | 111.2219 | 1.6826 | -124.965 | 110.1872
Line_1 | 0.029802 | 0.61812 | 0.52845 | 0.029227 | 0.61799 | 0.52891 | 0.34412 | 7.1375 | 6.102 | 0.33749 | 7.1359 | 6.1073 | 0.16307 | -5.497 | -3.3054 | -0.16382 | 5.8425 | 3.3875 | -0.39723 | -2.5828 | -4.173 | 0.37863 | 2.7004 | 4.4835 | 69.268 | 30.2983 | -122.8059 | -111.7143 | -149.7715 | 57.2603 |  | 1.2478 | 0.85094 | 0.87242 | 1.2224 | 0.90197 | 0.9201 | 1.5869 | -124.5353 | 108.8123 | 1.6826 | -124.965 | 110.1872
Line_2 | 0.011782 | 0.2257 | 0.097787 | 0.011128 | 0.22523 | 0.097759 | 0.13605 | 2.6061 | 1.1291 | 0.1285 | 2.6007 | 1.1288 | -0.017313 | -2.2108 | -0.06955 | 0.015571 | 2.2688 | 0.080173 | -0.16461 | 0.66104 | -1.0503 | 0.1563 | -0.59579 | 1.0355 | 98.4885 | 69.8769 | -155.7902 | -82.6283 | -110.2514 | 24.6144 |  | 1.2166 | 0.88541 | 0.93221 | 1.2224 | 0.90197 | 0.9201 | 2.4844 | -126.7702 | 110.4213 | 1.6826 | -124.965 | 110.1872
Line_3 | 0.02048 | 0.46675 | 0.4494 | 0.020113 | 0.46691 | 0.44988 | 0.23648 | 5.3896 | 5.1892 | 0.23224 | 5.3914 | 5.1948 | 0.18101 | -3.3506 | -3.2093 | -0.18395 | 3.6069 | 3.3402 | -0.23305 | -3.1316 | -3.1931 | 0.21446 | 3.1269 | 3.5063 | 53.7506 | 12.3992 | -116.0426 | -128.1358 | -167.6924 | 64.0319 |  | 1.2478 | 0.85094 | 0.87242 | 1.2166 | 0.88541 | 0.93221 | 1.5869 | -124.5353 | 108.8123 | 2.4844 | -126.7702 | 110.4213

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.59571 | 2.6622 | 2.51 | 0.5969 | 2.6624 | 2.5095 | 6.8787 | 30.7401 | 28.9826 | 6.8924 | 30.7423 | 28.9768 | 0.16395 | 17.4517 | 7.1467 | 0.33017 | -7.9066 | -3.0479 | 7.3707 | 4.304 | 10.2284 | -7.713 | -0.32541 | -5.7072 | -88.4935 | -158.8953 | 36.4643 | 91.527 | 21.1303 | -143.5607 |  | 1.0718 | 0.58473 | 0.43053 | 1.1201 | 0.25741 | 0.22328 | 0.23229 | -145.0412 | 91.5217 | 3.9781 | -156.5129 | 98.3351
Line_1 | 0.32948 | 2.0099 | 1.8789 | 0.32781 | 2.0097 | 1.8798 | 3.8045 | 23.2088 | 21.6957 | 3.7852 | 23.2059 | 21.7062 | 0.53247 | -7.0642e-11 | -2.8231e-11 | -0.56732 | 5.9192 | 2.5067 | -4.5379 | -4.7605e-11 | -7.5324e-11 | 4.2016 | 0.80256 | 4.1481 | 86.3445 | 15.8137 | -140.564 | -93.7117 | -164.2344 | 39.4799 |  | 1.2009 | 0 | 0 | 1.1201 | 0.25741 | 0.22328 | 3.037 | 0 | 0 | 3.9781 | -156.5129 | 98.3351
Line_2 | 0.2735 | 0.68804 | 0.63996 | 0.27211 | 0.68765 | 0.64011 | 3.1581 | 7.9448 | 7.3896 | 3.1421 | 7.9402 | 7.3914 | 0.050776 | -1.3181 | -0.22717 | 0.23715 | 1.9874 | 0.54119 | -3.4523 | 1.2809 | -1.8262 | 3.5114 | -0.47715 | 1.5591 | 97.9107 | 37.102 | -152.6494 | -82.1581 | -143.0124 | 27.4777 |  | 1.0933 | 0.23135 | 0.24904 | 1.1201 | 0.25741 | 0.22328 | 8.7534 | 172.9214 | 110.2597 | 3.9781 | -156.5129 | 98.3351
Line_3 | 0.082617 | 1.3912 | 1.2601 | 0.081768 | 1.3914 | 1.2609 | 0.95398 | 16.0638 | 14.55 | 0.94418 | 16.0667 | 14.5601 | 0.85027 | -4.2205e-11 | -2.417e-11 | -0.84177 | 3.6287 | 1.5503 | -0.76787 | -4.1172e-11 | -4.8229e-11 | 0.59746 | -0.80511 | 3.2779 | 45.122 | 5.4989 | -134.4926 | -135.8808 | -174.5691 | 45.5722 |  | 1.2009 | 0 | 0 | 1.0933 | 0.23135 | 0.24904 | 3.037 | 0 | 0 | 8.7534 | 172.9214 | 110.2597

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.59571 | 2.6622 | 2.51 | 0.5969 | 2.6624 | 2.5095 | 6.8787 | 30.7401 | 28.9826 | 6.8924 | 30.7423 | 28.9768 | 0.16395 | 17.4517 | 7.1467 | 0.33017 | -7.9066 | -3.0479 | 7.3707 | 4.304 | 10.2284 | -7.713 | -0.32541 | -5.7072 | -88.4935 | -158.8953 | 36.4643 | 91.527 | 21.1303 | -143.5607 |  | 1.0718 | 0.58473 | 0.43053 | 1.1201 | 0.25741 | 0.22328 | 0.23229 | -145.0412 | 91.5217 | 3.9781 | -156.5129 | 98.3351
Line_1 | 0.32948 | 2.0099 | 1.8789 | 0.32781 | 2.0097 | 1.8798 | 3.8045 | 23.2088 | 21.6957 | 3.7852 | 23.2059 | 21.7062 | 0.53247 | -7.0642e-11 | -2.8231e-11 | -0.56732 | 5.9192 | 2.5067 | -4.5379 | -4.7605e-11 | -7.5324e-11 | 4.2016 | 0.80256 | 4.1481 | 86.3445 | 15.8137 | -140.564 | -93.7117 | -164.2344 | 39.4799 |  | 1.2009 | 0 | 0 | 1.1201 | 0.25741 | 0.22328 | 3.037 | 0 | 0 | 3.9781 | -156.5129 | 98.3351
Line_2 | 0.2735 | 0.68804 | 0.63996 | 0.27211 | 0.68765 | 0.64011 | 3.1581 | 7.9448 | 7.3896 | 3.1421 | 7.9402 | 7.3914 | 0.050776 | -1.3181 | -0.22717 | 0.23715 | 1.9874 | 0.54119 | -3.4523 | 1.2809 | -1.8262 | 3.5114 | -0.47715 | 1.5591 | 97.9107 | 37.102 | -152.6494 | -82.1581 | -143.0124 | 27.4777 |  | 1.0933 | 0.23135 | 0.24904 | 1.1201 | 0.25741 | 0.22328 | 8.7534 | 172.9214 | 110.2597 | 3.9781 | -156.5129 | 98.3351
Line_3 | 0.082617 | 1.3912 | 1.2601 | 0.081768 | 1.3914 | 1.2609 | 0.95398 | 16.0638 | 14.55 | 0.94418 | 16.0667 | 14.5601 | 0.85027 | -4.2205e-11 | -2.417e-11 | -0.84177 | 3.6287 | 1.5503 | -0.76787 | -4.1172e-11 | -4.8229e-11 | 0.59746 | -0.80511 | 3.2779 | 45.122 | 5.4989 | -134.4926 | -135.8808 | -174.5691 | 45.5722 |  | 1.2009 | 0 | 0 | 1.0933 | 0.23135 | 0.24904 | 3.037 | 0 | 0 | 8.7534 | 172.9214 | 110.2597

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.21745 | 0.74368 | 0.68621 | 0.21788 | 0.74374 | 0.686 | 2.5109 | 8.5873 | 7.9237 | 2.5159 | 8.588 | 7.9213 | 0.8308 | 7.1007 | 3.7339 | -0.77132 | -6.3023 | -3.4683 | 2.4347 | 2.5956 | 5.6745 | -2.4828 | -2.2821 | -5.3015 | -70.8772 | -145.7374 | 55.1105 | 109.1362 | 34.2956 | -124.921 |  | 1.0246 | 0.8804 | 0.85727 | 1.0334 | 0.78048 | 0.79977 | 0.28154 | -125.6578 | 111.7651 | 1.8778 | -125.7993 | 111.8859
Line_1 | 0.11968 | 0.56439 | 0.52072 | 0.11907 | 0.56432 | 0.52109 | 1.3819 | 6.517 | 6.0127 | 1.3749 | 6.5162 | 6.017 | -0.30145 | -4.051 | -2.7265 | 0.29204 | 4.5617 | 2.9217 | -1.4371 | -2.2091 | -3.4495 | 1.3905 | 2.2486 | 3.8238 | 103.7784 | 28.0226 | -120.7851 | -76.2607 | -152.0391 | 59.268 |  | 1.0626 | 0.70802 | 0.73127 | 1.0334 | 0.78048 | 0.79977 | 1.9316 | -123.3723 | 110.8911 | 1.8778 | -125.7993 | 111.8859
Line_2 | 0.10047 | 0.19334 | 0.17054 | 0.099966 | 0.19318 | 0.1706 | 1.1601 | 2.2325 | 1.9693 | 1.1543 | 2.2307 | 1.97 | -0.44353 | -1.6832 | -0.52281 | 0.47928 | 1.7407 | 0.54664 | -1.0889 | 0.044707 | -1.5101 | 1.0923 | 0.03349 | 1.4777 | 115.6181 | 53.2432 | -137.9837 | -64.4315 | -126.9015 | 42.1872 |  | 1.0135 | 0.75424 | 0.81149 | 1.0334 | 0.78048 | 0.79977 | 3.4569 | -128.2783 | 112.9199 | 1.8778 | -125.7993 | 111.8859
Line_3 | 0.029746 | 0.39798 | 0.36123 | 0.029433 | 0.39811 | 0.36161 | 0.34348 | 4.5955 | 4.1711 | 0.33986 | 4.5969 | 4.1755 | 0.19167 | -2.4736 | -2.2055 | -0.19358 | 2.8159 | 2.3687 | -0.31059 | -2.1138 | -2.107 | 0.28491 | 2.0229 | 2.4228 | 60.2526 | 16.1127 | -112.8005 | -120.7374 | -163.9716 | 67.2734 |  | 1.0626 | 0.70802 | 0.73127 | 1.0135 | 0.75424 | 0.81149 | 1.9316 | -123.3723 | 110.8911 | 3.4569 | -128.2783 | 112.9199

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.21745 | 0.74368 | 0.68621 | 0.21788 | 0.74374 | 0.686 | 2.5109 | 8.5873 | 7.9237 | 2.5159 | 8.588 | 7.9213 | 0.8308 | 7.1007 | 3.7339 | -0.77132 | -6.3023 | -3.4683 | 2.4347 | 2.5956 | 5.6745 | -2.4828 | -2.2821 | -5.3015 | -70.8772 | -145.7374 | 55.1105 | 109.1362 | 34.2956 | -124.921 |  | 1.0246 | 0.8804 | 0.85727 | 1.0334 | 0.78048 | 0.79977 | 0.28154 | -125.6578 | 111.7651 | 1.8778 | -125.7993 | 111.8859
Line_1 | 0.11968 | 0.56439 | 0.52072 | 0.11907 | 0.56432 | 0.52109 | 1.3819 | 6.517 | 6.0127 | 1.3749 | 6.5162 | 6.017 | -0.30145 | -4.051 | -2.7265 | 0.29204 | 4.5617 | 2.9217 | -1.4371 | -2.2091 | -3.4495 | 1.3905 | 2.2486 | 3.8238 | 103.7784 | 28.0226 | -120.7851 | -76.2607 | -152.0391 | 59.268 |  | 1.0626 | 0.70802 | 0.73127 | 1.0334 | 0.78048 | 0.79977 | 1.9316 | -123.3723 | 110.8911 | 1.8778 | -125.7993 | 111.8859
Line_2 | 0.10047 | 0.19334 | 0.17054 | 0.099966 | 0.19318 | 0.1706 | 1.1601 | 2.2325 | 1.9693 | 1.1543 | 2.2307 | 1.97 | -0.44353 | -1.6832 | -0.52281 | 0.47928 | 1.7407 | 0.54664 | -1.0889 | 0.044707 | -1.5101 | 1.0923 | 0.03349 | 1.4777 | 115.6181 | 53.2432 | -137.9837 | -64.4315 | -126.9015 | 42.1872 |  | 1.0135 | 0.75424 | 0.81149 | 1.0334 | 0.78048 | 0.79977 | 3.4569 | -128.2783 | 112.9199 | 1.8778 | -125.7993 | 111.8859
Line_3 | 0.029746 | 0.39798 | 0.36123 | 0.029433 | 0.39811 | 0.36161 | 0.34348 | 4.5955 | 4.1711 | 0.33986 | 4.5969 | 4.1755 | 0.19167 | -2.4736 | -2.2055 | -0.19358 | 2.8159 | 2.3687 | -0.31059 | -2.1138 | -2.107 | 0.28491 | 2.0229 | 2.4228 | 60.2526 | 16.1127 | -112.8005 | -120.7374 | -163.9716 | 67.2734 |  | 1.0626 | 0.70802 | 0.73127 | 1.0135 | 0.75424 | 0.81149 | 1.9316 | -123.3723 | 110.8911 | 3.4569 | -128.2783 | 112.9199