## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6358 | 3.6358 | 0 | 0 | 125.9486 | 125.9486 | 36.0342 | -15.4122 | 41.0034 | -17.6054 | -73.0863 | 106.9137 | 0.43341 | 0.18578 | -24.3956 | -24.2861
Line_1 | 2.7277 | 2.7277 | 5.405 | 0 | 94.4895 | 94.4895 | -1e-07 | 11.6068 | -1e-07 | 13.1692 | 107.1055 | -72.8945 | 0 | 0.18578 | 0 | -24.2861
Line_2 | 0.90821 | 0.90821 | 0 | 0 | 31.4612 | 31.4612 | -2.5187 | 3.8055 | -2.9762 | 4.4362 | 106.3378 | -73.6622 | 0.12393 | 0.18578 | -23.9029 | -24.2861
Line_3 | 1.8196 | 1.8196 | 3.5617 | 0 | 63.0325 | 63.0325 | -1e-07 | 5.165 | -1e-07 | 5.8603 | 107.4886 | -72.5114 | 0 | 0.12393 | 0 | -23.9029

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 3.6358 | 3.6358 | 0 | 0 | 125.9486 | 125.9486 | 36.0342 | -15.4122 | 41.0034 | -17.6054 | -73.0863 | 106.9137 | 0.43341 | 0.18578 | -24.3956 | -24.2861
Line_1 | 2.7277 | 2.7277 | 5.405 | 0 | 94.4895 | 94.4895 | -1e-07 | 11.6068 | -1e-07 | 13.1692 | 107.1055 | -72.8945 | 0 | 0.18578 | 0 | -24.2861
Line_2 | 0.90821 | 0.90821 | 0 | 0 | 31.4612 | 31.4612 | -2.5187 | 3.8055 | -2.9762 | 4.4362 | 106.3378 | -73.6622 | 0.12393 | 0.18578 | -23.9029 | -24.2861
Line_3 | 1.8196 | 1.8196 | 3.5617 | 0 | 63.0325 | 63.0325 | -1e-07 | 5.165 | -1e-07 | 5.8603 | 107.4886 | -72.5114 | 0 | 0.12393 | 0 | -23.9029

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79728 | 0.79728 | 0 | 0 | 27.6185 | 27.6185 | 20.9759 | -19.9843 | 17.3767 | -16.2516 | -45.7967 | 134.2033 | 0.98624 | 0.93264 | -6.158 | -6.6781
Line_1 | 0.63574 | 0.63574 | 1.3036 | 0 | 22.0228 | 22.0228 | -14.7741 | 15.4046 | -12.8701 | 13.5855 | 131.9124 | -48.0876 | 0.8897 | 0.93264 | -7.0275 | -6.6781
Line_2 | 0.16402 | 0.16402 | 0 | 0 | 5.6819 | 5.6819 | -4.5378 | 4.5797 | -2.6184 | 2.6661 | 143.1163 | -36.8837 | 0.92205 | 0.93264 | -6.8973 | -6.6781
Line_3 | 0.47591 | 0.47591 | 0.9321 | 0 | 16.4861 | 16.4861 | -10.3898 | 10.7431 | -10.3535 | 10.7544 | 128.0726 | -51.9274 | 0.8897 | 0.92205 | -7.0275 | -6.8973

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79728 | 0.79728 | 0 | 0 | 27.6185 | 27.6185 | 20.9759 | -19.9843 | 17.3767 | -16.2516 | -45.7967 | 134.2033 | 0.98624 | 0.93264 | -6.158 | -6.6781
Line_1 | 0.63574 | 0.63574 | 1.3036 | 0 | 22.0228 | 22.0228 | -14.7741 | 15.4046 | -12.8701 | 13.5855 | 131.9124 | -48.0876 | 0.8897 | 0.93264 | -7.0275 | -6.6781
Line_2 | 0.16402 | 0.16402 | 0 | 0 | 5.6819 | 5.6819 | -4.5378 | 4.5797 | -2.6184 | 2.6661 | 143.1163 | -36.8837 | 0.92205 | 0.93264 | -6.8973 | -6.6781
Line_3 | 0.47591 | 0.47591 | 0.9321 | 0 | 16.4861 | 16.4861 | -10.3898 | 10.7431 | -10.3535 | 10.7544 | 128.0726 | -51.9274 | 0.8897 | 0.92205 | -7.0275 | -6.8973

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 2.9516 | 2.9516 | 0 | 0 | 102.2474 | 102.2474 | 45.756 | -19.6615 | 26.7104 | -11.29 | -61.5111 | 118.4889 | 0.51817 | 0.22174 | -31.2365 | -31.6459
Line_1 | 2.2078 | 2.2078 | 3.9682 | 0 | 76.4821 | 76.4821 | -1e-07 | 14.6004 | -1e-07 | 8.628 | 117.7734 | -62.2266 | 0 | 0.22174 | 0 | -31.6459
Line_2 | 0.74446 | 0.74446 | 0 | 0 | 25.7889 | 25.7889 | -3.4011 | 5.0611 | -1.681 | 2.6619 | 120.6115 | -59.3885 | 0.14711 | 0.22174 | -33.0879 | -31.6459
Line_3 | 1.4648 | 1.4648 | 2.6326 | 0 | 50.7409 | 50.7409 | -1e-07 | 6.4263 | -1e-07 | 3.7976 | 116.3313 | -63.6687 | 0 | 0.14711 | 0 | -33.0879

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line_0 | 0.79717 | 0.79717 | 0 | 0 | 27.6148 | 27.6148 | 18.6059 | -16.7025 | 15.5964 | -14.4716 | -47.0211 | 132.9789 | 0.87917 | 0.80029 | -7.0497 | -6.1144
Line_1 | 0.59629 | 0.59629 | 1.0717 | 0 | 20.6561 | 20.6561 | -11.2925 | 12.3575 | -10.3507 | 10.9801 | 132.2633 | -47.7367 | 0.7416 | 0.80029 | -5.2282 | -6.1144
Line_2 | 0.20106 | 0.20106 | 0 | 0 | 6.965 | 6.965 | -4.2239 | 4.345 | -3.4199 | 3.4915 | 135.1015 | -44.8985 | 0.78031 | 0.80029 | -5.9028 | -6.1144
Line_3 | 0.3956 | 0.3956 | 0.71101 | 0 | 13.704 | 13.704 | -7.3166 | 7.7854 | -7.0534 | 7.3304 | 130.8213 | -49.1787 | 0.7416 | 0.78031 | -5.2282 | -5.9028

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36184 | 3.0849 | 3.2334 | 0.36184 | 3.0849 | 3.2334 | 4.1781 | 35.621 | 37.3363 | 4.1781 | 35.621 | 37.3363 | -3.0459 | 29.02 | -12.393 | 3.114 | -24.0714 | 17.8296 | -3.7564 | 3.1835 | 15.3596 | 3.8336 | 2.4312 | -9.1912 | 131.2748 | -159.9336 | 14.078 | -48.7252 | 20.0664 | -165.922 | 1.1575 | 0.81957 | 0.5286 | 1.1821 | 0.6792 | 0.53726 | 2.2371 | -153.6732 | 142.9765 | 2.188 | -165.7008 | 166.8068
Line_1 | 0.18371 | 2.3133 | 2.3918 | 0.18371 | 2.3133 | 2.3918 | 2.1213 | 26.7118 | 27.6179 | 2.1213 | 26.7118 | 27.6179 | 1.6145 | -15.3112 | 16.1185 | -1.597 | 18.0939 | -13.1438 | 1.9532 | 4.4866 | -3.51 | -1.9333 | -1.3293 | 6.8851 | -48.254 | 18.5008 | -165.5462 | 131.746 | -161.4992 | 14.4538 | 1.1946 | 0.5973 | 0.5973 | 1.1821 | 0.6792 | 0.53726 | 2.1688 | -177.8312 | -177.8312 | 2.188 | -165.7008 | 166.8068
Line_2 | 0.17814 | 0.77501 | 0.84184 | 0.17814 | 0.77501 | 0.84184 | 2.057 | 8.949 | 9.7207 | 2.057 | 8.949 | 9.7207 | 1.5335 | -5.6651 | 5.0543 | -1.517 | 5.9775 | -4.6858 | 1.919 | 1.4563 | -1.8879 | -1.9003 | -1.1019 | 2.306 | -49.2111 | 24.7439 | -166.9899 | 130.7889 | -155.2561 | 13.0101 | 1.1942 | 0.65363 | 0.55504 | 1.1821 | 0.6792 | 0.53726 | 2.1597 | -169.6723 | 172.5282 | 2.188 | -165.7008 | 166.8068
Line_3 | 0.006339 | 1.5452 | 1.5504 | 0.006339 | 1.5452 | 1.5504 | 0.073197 | 17.8424 | 17.902 | 0.073197 | 17.8424 | 17.902 | 0.080827 | -10.3755 | 10.4159 | -0.080806 | 11.6171 | -9.166 | 0.03336 | 2.4346 | -2.4179 | -0.033337 | -1.0259 | 3.836 | -20.2589 | 15.3742 | -164.7623 | 159.7411 | -164.6258 | 15.2377 | 1.1946 | 0.5973 | 0.5973 | 1.1942 | 0.65363 | 0.55504 | 2.1688 | -177.8312 | -177.8312 | 2.1597 | -169.6723 | 172.5282

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.36184 | 3.0849 | 3.2334 | 0.36184 | 3.0849 | 3.2334 | 4.1781 | 35.621 | 37.3363 | 4.1781 | 35.621 | 37.3363 | -3.0459 | 29.02 | -12.393 | 3.114 | -24.0714 | 17.8296 | -3.7564 | 3.1835 | 15.3596 | 3.8336 | 2.4312 | -9.1912 | 131.2748 | -159.9336 | 14.078 | -48.7252 | 20.0664 | -165.922 | 1.1575 | 0.81957 | 0.5286 | 1.1821 | 0.6792 | 0.53726 | 2.2371 | -153.6732 | 142.9765 | 2.188 | -165.7008 | 166.8068
Line_1 | 0.18371 | 2.3133 | 2.3918 | 0.18371 | 2.3133 | 2.3918 | 2.1213 | 26.7118 | 27.6179 | 2.1213 | 26.7118 | 27.6179 | 1.6145 | -15.3112 | 16.1185 | -1.597 | 18.0939 | -13.1438 | 1.9532 | 4.4866 | -3.51 | -1.9333 | -1.3293 | 6.8851 | -48.254 | 18.5008 | -165.5462 | 131.746 | -161.4992 | 14.4538 | 1.1946 | 0.5973 | 0.5973 | 1.1821 | 0.6792 | 0.53726 | 2.1688 | -177.8312 | -177.8312 | 2.188 | -165.7008 | 166.8068
Line_2 | 0.17814 | 0.77501 | 0.84184 | 0.17814 | 0.77501 | 0.84184 | 2.057 | 8.949 | 9.7207 | 2.057 | 8.949 | 9.7207 | 1.5335 | -5.6651 | 5.0543 | -1.517 | 5.9775 | -4.6858 | 1.919 | 1.4563 | -1.8879 | -1.9003 | -1.1019 | 2.306 | -49.2111 | 24.7439 | -166.9899 | 130.7889 | -155.2561 | 13.0101 | 1.1942 | 0.65363 | 0.55504 | 1.1821 | 0.6792 | 0.53726 | 2.1597 | -169.6723 | 172.5282 | 2.188 | -165.7008 | 166.8068
Line_3 | 0.006339 | 1.5452 | 1.5504 | 0.006339 | 1.5452 | 1.5504 | 0.073197 | 17.8424 | 17.902 | 0.073197 | 17.8424 | 17.902 | 0.080827 | -10.3755 | 10.4159 | -0.080806 | 11.6171 | -9.166 | 0.03336 | 2.4346 | -2.4179 | -0.033337 | -1.0259 | 3.836 | -20.2589 | 15.3742 | -164.7623 | 159.7411 | -164.6258 | 15.2377 | 1.1946 | 0.5973 | 0.5973 | 1.1942 | 0.65363 | 0.55504 | 2.1688 | -177.8312 | -177.8312 | 2.1597 | -169.6723 | 172.5282

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26649 | 1.2614 | 1.2336 | 0.26649 | 1.2614 | 1.2336 | 3.0772 | 14.5653 | 14.2444 | 3.0772 | 14.5653 | 14.2444 | -1.7911 | 15.2178 | 0.28699 | 1.8281 | -14.3904 | 0.50433 | -3.0409 | 0.78464 | 12.1494 | 3.0828 | 0.15412 | -11.2516 | 121.7957 | -136.1541 | 31.6491 | -58.2043 | 43.8459 | -148.3509 | 1.1469 | 1.0462 | 0.85317 | 1.1647 | 0.98805 | 0.79069 | 1.2969 | -133.2025 | 120.296 | 1.1282 | -136.7676 | 124.2156
Line_1 | 0.13441 | 0.95605 | 0.94778 | 0.13441 | 0.95605 | 0.94778 | 1.552 | 11.0395 | 10.944 | 1.552 | 11.0395 | 10.944 | 0.95258 | -10.4164 | 0.79274 | -0.94319 | 10.8917 | -0.32563 | 1.5527 | -0.049073 | -8.1172 | -1.542 | 0.58835 | 8.6472 | -57.42 | 40.1404 | -147.941 | 122.58 | -139.8596 | 32.059 | 1.1737 | 0.94357 | 0.74523 | 1.1647 | 0.98805 | 0.79069 | 1.051 | -139.5897 | 127.6369 | 1.1282 | -136.7676 | 124.2156
Line_2 | 0.13211 | 0.31349 | 0.28593 | 0.13211 | 0.31349 | 0.28593 | 1.5255 | 3.6199 | 3.3016 | 1.5255 | 3.6199 | 3.3016 | 0.89397 | -3.4476 | 0.22121 | -0.88489 | 3.4987 | -0.1787 | 1.5511 | 0.80045 | -2.5562 | -1.5408 | -0.74246 | 2.6044 | -59.0022 | 55.2134 | -149.7095 | 120.9978 | -124.7866 | 30.2905 | 1.1735 | 0.97774 | 0.77712 | 1.1647 | 0.98805 | 0.79069 | 1.0404 | -137.8576 | 125.2365 | 1.1282 | -136.7676 | 124.2156
Line_3 | 0.0043354 | 0.65841 | 0.66204 | 0.0043354 | 0.65841 | 0.66204 | 0.050061 | 7.6027 | 7.6446 | 0.050061 | 7.6027 | 7.6446 | 0.058746 | -7.1142 | 0.47813 | -0.058736 | 7.3396 | -0.25021 | 0.0012086 | -0.92175 | -5.6769 | -0.0011976 | 1.1775 | 5.9355 | -0.1276 | 33.0278 | -147.1774 | 179.8724 | -146.9722 | 32.8226 | 1.1737 | 0.94357 | 0.74523 | 1.1735 | 0.97774 | 0.77712 | 1.051 | -139.5897 | 127.6369 | 1.0404 | -137.8576 | 125.2365

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.26649 | 1.2614 | 1.2336 | 0.26649 | 1.2614 | 1.2336 | 3.0772 | 14.5653 | 14.2444 | 3.0772 | 14.5653 | 14.2444 | -1.7911 | 15.2178 | 0.28699 | 1.8281 | -14.3904 | 0.50433 | -3.0409 | 0.78464 | 12.1494 | 3.0828 | 0.15412 | -11.2516 | 121.7957 | -136.1541 | 31.6491 | -58.2043 | 43.8459 | -148.3509 | 1.1469 | 1.0462 | 0.85317 | 1.1647 | 0.98805 | 0.79069 | 1.2969 | -133.2025 | 120.296 | 1.1282 | -136.7676 | 124.2156
Line_1 | 0.13441 | 0.95605 | 0.94778 | 0.13441 | 0.95605 | 0.94778 | 1.552 | 11.0395 | 10.944 | 1.552 | 11.0395 | 10.944 | 0.95258 | -10.4164 | 0.79274 | -0.94319 | 10.8917 | -0.32563 | 1.5527 | -0.049073 | -8.1172 | -1.542 | 0.58835 | 8.6472 | -57.42 | 40.1404 | -147.941 | 122.58 | -139.8596 | 32.059 | 1.1737 | 0.94357 | 0.74523 | 1.1647 | 0.98805 | 0.79069 | 1.051 | -139.5897 | 127.6369 | 1.1282 | -136.7676 | 124.2156
Line_2 | 0.13211 | 0.31349 | 0.28593 | 0.13211 | 0.31349 | 0.28593 | 1.5255 | 3.6199 | 3.3016 | 1.5255 | 3.6199 | 3.3016 | 0.89397 | -3.4476 | 0.22121 | -0.88489 | 3.4987 | -0.1787 | 1.5511 | 0.80045 | -2.5562 | -1.5408 | -0.74246 | 2.6044 | -59.0022 | 55.2134 | -149.7095 | 120.9978 | -124.7866 | 30.2905 | 1.1735 | 0.97774 | 0.77712 | 1.1647 | 0.98805 | 0.79069 | 1.0404 | -137.8576 | 125.2365 | 1.1282 | -136.7676 | 124.2156
Line_3 | 0.0043354 | 0.65841 | 0.66204 | 0.0043354 | 0.65841 | 0.66204 | 0.050061 | 7.6027 | 7.6446 | 0.050061 | 7.6027 | 7.6446 | 0.058746 | -7.1142 | 0.47813 | -0.058736 | 7.3396 | -0.25021 | 0.0012086 | -0.92175 | -5.6769 | -0.0011976 | 1.1775 | 5.9355 | -0.1276 | 33.0278 | -147.1774 | 179.8724 | -146.9722 | 32.8226 | 1.1737 | 0.94357 | 0.74523 | 1.1735 | 0.97774 | 0.77712 | 1.051 | -139.5897 | 127.6369 | 1.0404 | -137.8576 | 125.2365

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.1573 | 2.5018 | 2.6288 | 0.1573 | 2.5018 | 2.6288 | 1.8163 | 28.8882 | 30.3543 | 1.8163 | 28.8882 | 30.3543 | -1.8033 | 24.2039 | -2.0881 | 1.828 | -17.955 | 8.9874 | -0.29968 | -0.52181 | 13.6286 | 0.31428 | 4.2146 | -9.5515 | 172.4103 | -150.363 | 27.5625 | -7.5897 | 29.637 | -152.4375 | 1.0064 | 0.83804 | 0.45422 | 1.0212 | 0.63843 | 0.43207 | 1.8461 | -151.598 | 126.2732 | 2.1658 | -163.5729 | 160.8196
Line_1 | 0.080807 | 1.868 | 1.9334 | 0.080807 | 1.868 | 1.9334 | 0.93307 | 21.5701 | 22.3245 | 0.93307 | 21.5701 | 22.3245 | 0.9414 | -10.0168 | 10.4875 | -0.93488 | 13.5007 | -6.7556 | 0.18797 | 4.7735 | -4.6795 | -0.18412 | -2.7146 | 6.8848 | -8.9755 | 27.7962 | -153.6375 | 171.0245 | -152.2038 | 26.3625 | 1.0288 | 0.51442 | 0.51442 | 1.0212 | 0.63843 | 0.43207 | 2.3162 | -177.6838 | -177.6838 | 2.1658 | -163.5729 | 160.8196
Line_2 | 0.07654 | 0.63756 | 0.697 | 0.07654 | 0.63756 | 0.697 | 0.88381 | 7.3619 | 8.0483 | 0.88381 | 7.3619 | 8.0483 | 0.89894 | -4.0484 | 2.7169 | -0.89309 | 4.4543 | -2.2318 | 0.13362 | 1.7398 | -2.3801 | -0.13017 | -1.4999 | 2.6667 | -6.1266 | 35.0378 | -149.1073 | 173.8734 | -144.9622 | 30.8927 | 1.0283 | 0.59855 | 0.44878 | 1.0212 | 0.63843 | 0.43207 | 2.3283 | -168.2174 | 169.6733 | 2.1658 | -163.5729 | 160.8196
Line_3 | 0.0057872 | 1.2382 | 1.2398 | 0.0057872 | 1.2382 | 1.2398 | 0.066825 | 14.2971 | 14.3155 | 0.066825 | 14.2971 | 14.3155 | 0.041958 | -6.8307 | 6.8517 | -0.041925 | 8.3613 | -5.3171 | 0.054463 | 2.7263 | -2.6991 | -0.054444 | -1.8218 | 3.6059 | -50.0733 | 24.0746 | -156.1827 | 129.9267 | -155.9254 | 23.8173 | 1.0288 | 0.51442 | 0.51442 | 1.0283 | 0.59855 | 0.44878 | 2.3162 | -177.6838 | -177.6838 | 2.3283 | -168.2174 | 169.6733

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.068597 | 1.091 | 1.1464 | 0.068597 | 1.091 | 1.1464 | 0.79209 | 12.5981 | 13.2375 | 0.79209 | 12.5981 | 13.2375 | -0.78949 | 11.8666 | 2.206 | 0.79419 | -10.6782 | -0.89388 | 0.059138 | 0.94684 | 9.8501 | -0.056362 | -0.24454 | -9.0747 | -174.893 | -137.6663 | 40.2592 | 5.107 | 42.3337 | -139.7408 | 0.99951 | 0.94493 | 0.76254 | 1.0052 | 0.84783 | 0.68885 | 0.82315 | -133.1043 | 117.6357 | 1.0476 | -136.3544 | 124.6336
Line_1 | 0.03524 | 0.81464 | 0.84313 | 0.03524 | 0.81464 | 0.84313 | 0.40691 | 9.4067 | 9.7357 | 0.40691 | 9.4067 | 9.7357 | 0.40981 | -7.3006 | 0.19224 | -0.40857 | 7.9632 | 0.5175 | -0.018346 | -0.047078 | -6.267 | 0.019079 | 0.43863 | 6.6864 | 3.7212 | 40.4929 | -140.9408 | -176.2788 | -139.5071 | 39.0592 | 1.0081 | 0.77612 | 0.64402 | 1.0052 | 0.84783 | 0.68885 | 1.1579 | -139.1377 | 130.8161 | 1.0476 | -136.3544 | 124.6336
Line_2 | 0.033379 | 0.27804 | 0.30396 | 0.033379 | 0.27804 | 0.30396 | 0.38543 | 3.2105 | 3.5098 | 0.38543 | 3.2105 | 3.5098 | 0.38673 | -2.6378 | -0.28414 | -0.38562 | 2.715 | 0.37638 | -0.036626 | 0.23969 | -2.3338 | 0.037283 | -0.19408 | 2.3883 | 6.5701 | 47.7344 | -136.4106 | -173.4299 | -132.2656 | 43.5894 | 1.0079 | 0.82502 | 0.66983 | 1.0052 | 0.84783 | 0.68885 | 1.1599 | -137.4576 | 126.6478 | 1.0476 | -136.3544 | 124.6336
Line_3 | 0.0025238 | 0.53996 | 0.54066 | 0.0025238 | 0.53996 | 0.54066 | 0.029142 | 6.2349 | 6.243 | 0.029142 | 6.2349 | 6.243 | 0.022981 | -4.8268 | 0.30161 | -0.022975 | 5.1178 | -0.0097645 | 0.018303 | -0.34522 | -4.0093 | -0.018299 | 0.51724 | 4.1817 | -37.3766 | 36.7713 | -143.486 | 142.6234 | -143.2287 | 36.514 | 1.0081 | 0.77612 | 0.64402 | 1.0079 | 0.82502 | 0.66983 | 1.1579 | -139.1377 | 130.8161 | 1.1599 | -137.4576 | 126.6478

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.199 | 0.8141 | 0.6294 | 2.1969 | 0.81593 | 0.63142 | 25.3917 | 9.4005 | 7.2677 | 25.3678 | 9.4216 | 7.2911 | 9.0315 | -11.4368 | 8.1829 | -4.6392 | 11.3039 | -8.591 | 7.1429 | 5.0551 | 1.149 | -3.3805 | -5.2783 | -1.0237 | -73.4363 | 82.5299 | 122.7994 | 106.5601 | -97.4021 | -57.2408 |  | 0.45348 | 1.3302 | 1.137 | 0.22628 | 1.3241 | 1.1866 | -35.0963 | -121.3157 | 130.792 | -37.3603 | -122.4321 | 129.5548
Line_1 | 1.8275 | 0.43623 | 0.32135 | 1.8299 | 0.43398 | 0.31911 | 21.1023 | 5.0372 | 3.7107 | 21.1294 | 5.0112 | 3.6848 | 9.9246e-11 | 5.9213 | -4.6367 | 3.8474 | -6.1523 | 4.2705 | -6.7649e-11 | -2.8064 | -0.97476 | 2.8384 | 2.4859 | 0.93885 | 106.2328 | -100.3314 | -62.9827 | -73.7778 | 79.5698 | 117.1557 |  | 0 | 1.3009 | 1.2769 | 0.22628 | 1.3241 | 1.1866 | 0 | -125.6901 | 128.8896 | -37.3603 | -122.4321 | 129.5548
Line_2 | 0.36508 | 0.38527 | 0.3174 | 0.36725 | 0.38324 | 0.31538 | 4.2156 | 4.4487 | 3.665 | 4.2407 | 4.4253 | 3.6417 | -0.8324 | 5.3559 | -4.1972 | 0.79179 | -5.1516 | 4.3205 | -0.47657 | -2.6684 | -0.057585 | 0.54207 | 2.7924 | 0.084887 | 108.2516 | -93.8578 | -51.7148 | -71.7565 | 86.0273 | 128.4292 |  | 0.22753 | 1.3451 | 1.1453 | 0.22628 | 1.3241 | 1.1866 | -41.9558 | -120.3411 | 129.0713 | -37.3603 | -122.4321 | 129.5548
Line_3 | 1.4616 | 0.069252 | 0.063158 | 1.464 | 0.068059 | 0.062121 | 16.8776 | 0.79965 | 0.72929 | 16.9044 | 0.78588 | 0.71731 | 7.9851e-11 | 1.0139 | 0.027956 | 3.2501 | -0.99356 | -0.054722 | -5.3402e-11 | 0.23279 | -0.9308 | 2.0568 | -0.36083 | 0.81971 | 105.7266 | -138.6215 | -142.8308 | -74.2827 | 39.6996 | 35.252 |  | 0 | 1.3009 | 1.2769 | 0.22753 | 1.3451 | 1.1453 | 0 | -125.6901 | 128.8896 | -41.9558 | -120.3411 | 129.0713

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 2.199 | 0.8141 | 0.6294 | 2.1969 | 0.81593 | 0.63142 | 25.3917 | 9.4005 | 7.2677 | 25.3678 | 9.4216 | 7.2911 | 9.0315 | -11.4368 | 8.1829 | -4.6392 | 11.3039 | -8.591 | 7.1429 | 5.0551 | 1.149 | -3.3805 | -5.2783 | -1.0237 | -73.4363 | 82.5299 | 122.7994 | 106.5601 | -97.4021 | -57.2408 |  | 0.45348 | 1.3302 | 1.137 | 0.22628 | 1.3241 | 1.1866 | -35.0963 | -121.3157 | 130.792 | -37.3603 | -122.4321 | 129.5548
Line_1 | 1.8275 | 0.43623 | 0.32135 | 1.8299 | 0.43398 | 0.31911 | 21.1023 | 5.0372 | 3.7107 | 21.1294 | 5.0112 | 3.6848 | 9.9246e-11 | 5.9213 | -4.6367 | 3.8474 | -6.1523 | 4.2705 | -6.7649e-11 | -2.8064 | -0.97476 | 2.8384 | 2.4859 | 0.93885 | 106.2328 | -100.3314 | -62.9827 | -73.7778 | 79.5698 | 117.1557 |  | 0 | 1.3009 | 1.2769 | 0.22628 | 1.3241 | 1.1866 | 0 | -125.6901 | 128.8896 | -37.3603 | -122.4321 | 129.5548
Line_2 | 0.36508 | 0.38527 | 0.3174 | 0.36725 | 0.38324 | 0.31538 | 4.2156 | 4.4487 | 3.665 | 4.2407 | 4.4253 | 3.6417 | -0.8324 | 5.3559 | -4.1972 | 0.79179 | -5.1516 | 4.3205 | -0.47657 | -2.6684 | -0.057585 | 0.54207 | 2.7924 | 0.084887 | 108.2516 | -93.8578 | -51.7148 | -71.7565 | 86.0273 | 128.4292 |  | 0.22753 | 1.3451 | 1.1453 | 0.22628 | 1.3241 | 1.1866 | -41.9558 | -120.3411 | 129.0713 | -37.3603 | -122.4321 | 129.5548
Line_3 | 1.4616 | 0.069252 | 0.063158 | 1.464 | 0.068059 | 0.062121 | 16.8776 | 0.79965 | 0.72929 | 16.9044 | 0.78588 | 0.71731 | 7.9851e-11 | 1.0139 | 0.027956 | 3.2501 | -0.99356 | -0.054722 | -5.3402e-11 | 0.23279 | -0.9308 | 2.0568 | -0.36083 | 0.81971 | 105.7266 | -138.6215 | -142.8308 | -74.2827 | 39.6996 | 35.252 |  | 0 | 1.3009 | 1.2769 | 0.22753 | 1.3451 | 1.1453 | 0 | -125.6901 | 128.8896 | -41.9558 | -120.3411 | 129.0713

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53515 | 0.19489 | 0.30104 | 0.53452 | 0.19508 | 0.30148 | 6.1794 | 2.2504 | 3.4761 | 6.1721 | 2.2526 | 3.4812 | 5.1407 | -2.7094 | 2.193 | -4.8368 | 2.7361 | -2.2339 | 3.1115 | -0.020838 | -3.203 | -2.897 | -0.021614 | 3.2933 | -40.5084 | 60.5377 | 178.906 | 139.4992 | -119.2846 | -1.1805 |  | 0.97243 | 1.204 | 1.1167 | 0.91347 | 1.2147 | 1.1431 | -9.3228 | -119.0216 | 123.3041 | -9.5812 | -119.7372 | 122.9693
Line_1 | 0.48785 | 0.10937 | 0.14596 | 0.48856 | 0.109 | 0.14554 | 5.6333 | 1.2628 | 1.6854 | 5.6414 | 1.2586 | 1.6806 | -3.8561 | 1.5398 | -1.2083 | 4.1632 | -1.5286 | 1.1591 | -2.837 | -0.063347 | 1.5674 | 3.0371 | 0.019778 | -1.5321 | 134.3274 | -118.6673 | -4.3746 | -45.6928 | 61.004 | 175.8598 |  | 0.84983 | 1.2203 | 1.1743 | 0.91347 | 1.2147 | 1.1431 | -9.3301 | -121.0232 | 123.255 | -9.5812 | -119.7372 | 122.9693
Line_2 | 0.064831 | 0.086328 | 0.15672 | 0.065232 | 0.086089 | 0.15631 | 0.7486 | 0.99683 | 1.8097 | 0.75324 | 0.99407 | 1.8049 | -0.67072 | 1.2164 | -1.0595 | 0.67365 | -1.2075 | 1.0748 | 0.15153 | 0.002045 | 1.7665 | -0.14011 | 0.0018368 | -1.7612 | -177.3641 | -119.2374 | 1.3832 | 2.1681 | 60.3499 | -178.4248 |  | 0.91854 | 1.2202 | 1.1383 | 0.91347 | 1.2147 | 1.1431 | -10.095 | -119.1411 | 122.3384 | -9.5812 | -119.7372 | 122.9693
Line_3 | 0.44703 | 0.023182 | 0.018687 | 0.44775 | 0.022813 | 0.018433 | 5.1619 | 0.26768 | 0.21578 | 5.1701 | 0.26342 | 0.21285 | -3.2313 | 0.32529 | -0.090721 | 3.5401 | -0.32127 | 0.082175 | -2.9669 | -0.02987 | -0.23658 | 3.1654 | 0.010283 | 0.22792 | 128.1123 | -115.7766 | -125.765 | -51.8967 | 62.6921 | 52.1651 |  | 0.84983 | 1.2203 | 1.1743 | 0.91854 | 1.2202 | 1.1383 | -9.3301 | -121.0232 | 123.255 | -10.095 | -119.1411 | 122.3384

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.53515 | 0.19489 | 0.30104 | 0.53452 | 0.19508 | 0.30148 | 6.1794 | 2.2504 | 3.4761 | 6.1721 | 2.2526 | 3.4812 | 5.1407 | -2.7094 | 2.193 | -4.8368 | 2.7361 | -2.2339 | 3.1115 | -0.020838 | -3.203 | -2.897 | -0.021614 | 3.2933 | -40.5084 | 60.5377 | 178.906 | 139.4992 | -119.2846 | -1.1805 |  | 0.97243 | 1.204 | 1.1167 | 0.91347 | 1.2147 | 1.1431 | -9.3228 | -119.0216 | 123.3041 | -9.5812 | -119.7372 | 122.9693
Line_1 | 0.48785 | 0.10937 | 0.14596 | 0.48856 | 0.109 | 0.14554 | 5.6333 | 1.2628 | 1.6854 | 5.6414 | 1.2586 | 1.6806 | -3.8561 | 1.5398 | -1.2083 | 4.1632 | -1.5286 | 1.1591 | -2.837 | -0.063347 | 1.5674 | 3.0371 | 0.019778 | -1.5321 | 134.3274 | -118.6673 | -4.3746 | -45.6928 | 61.004 | 175.8598 |  | 0.84983 | 1.2203 | 1.1743 | 0.91347 | 1.2147 | 1.1431 | -9.3301 | -121.0232 | 123.255 | -9.5812 | -119.7372 | 122.9693
Line_2 | 0.064831 | 0.086328 | 0.15672 | 0.065232 | 0.086089 | 0.15631 | 0.7486 | 0.99683 | 1.8097 | 0.75324 | 0.99407 | 1.8049 | -0.67072 | 1.2164 | -1.0595 | 0.67365 | -1.2075 | 1.0748 | 0.15153 | 0.002045 | 1.7665 | -0.14011 | 0.0018368 | -1.7612 | -177.3641 | -119.2374 | 1.3832 | 2.1681 | 60.3499 | -178.4248 |  | 0.91854 | 1.2202 | 1.1383 | 0.91347 | 1.2147 | 1.1431 | -10.095 | -119.1411 | 122.3384 | -9.5812 | -119.7372 | 122.9693
Line_3 | 0.44703 | 0.023182 | 0.018687 | 0.44775 | 0.022813 | 0.018433 | 5.1619 | 0.26768 | 0.21578 | 5.1701 | 0.26342 | 0.21285 | -3.2313 | 0.32529 | -0.090721 | 3.5401 | -0.32127 | 0.082175 | -2.9669 | -0.02987 | -0.23658 | 3.1654 | 0.010283 | 0.22792 | 128.1123 | -115.7766 | -125.765 | -51.8967 | 62.6921 | 52.1651 |  | 0.84983 | 1.2203 | 1.1743 | 0.91854 | 1.2202 | 1.1383 | -9.3301 | -121.0232 | 123.255 | -10.095 | -119.1411 | 122.3384

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.8556 | 0.71482 | 0.58253 | 1.8541 | 0.71622 | 0.58398 | 21.4264 | 8.254 | 6.7265 | 21.4095 | 8.2702 | 6.7432 | 11.3688 | -6.6153 | 6.0483 | -5.8715 | 6.4326 | -6.3452 | 5.7226 | 6.5185 | 1.3381 | -2.6899 | -6.766 | -1.5008 | -61.5573 | 107.2141 | 114.0813 | 118.4383 | -72.7519 | -65.8937 |  | 0.59403 | 1.1252 | 0.92092 | 0.30166 | 1.1288 | 0.96695 | -34.8386 | -117.3638 | 126.5561 | -36.948 | -119.1988 | 127.4134
Line_1 | 1.5089 | 0.38802 | 0.31621 | 1.5107 | 0.38616 | 0.31435 | 17.4234 | 4.4805 | 3.6513 | 17.4441 | 4.459 | 3.6298 | -4.0904e-11 | 3.5059 | -3.6487 | 4.7511 | -3.8755 | 3.262 | -6.0001e-13 | -3.5512 | -1.5396 | 2.2622 | 3.2118 | 1.2954 | 117.6103 | -79.5422 | -74.2687 | -62.4088 | 100.4511 | 105.7542 |  | 0 | 1.1138 | 1.0846 | 0.30166 | 1.1288 | 0.96695 | 0 | -124.9102 | 128.6097 | -36.948 | -119.1988 | 127.4134
Line_2 | 0.34271 | 0.33749 | 0.27834 | 0.3443 | 0.3359 | 0.27675 | 3.9573 | 3.8971 | 3.214 | 3.9756 | 3.8787 | 3.1956 | -1.188 | 2.8671 | -2.8692 | 1.1204 | -2.557 | 3.0832 | -0.35862 | -3.4791 | -0.16404 | 0.42771 | 3.5541 | 0.20535 | 122.1731 | -64.914 | -56.4241 | -57.8422 | 115.0681 | 123.603 |  | 0.31359 | 1.1568 | 0.89417 | 0.30166 | 1.1288 | 0.96695 | -41.0296 | -115.4226 | 126.8482 | -36.948 | -119.1988 | 127.4134
Line_3 | 1.1668 | 0.10526 | 0.099692 | 1.1686 | 0.10434 | 0.098764 | 13.4733 | 1.2154 | 1.1511 | 13.4939 | 1.2048 | 1.1404 | -3.1611e-11 | 1.3391 | -0.1861 | 3.9033 | -1.3198 | 0.16718 | -1.2053e-12 | 0.19807 | -1.2346 | 1.6343 | -0.44815 | 1.0059 | 116.2673 | -133.3241 | -132.8181 | -63.7487 | 45.8218 | 46.2844 |  | 0 | 1.1138 | 1.0846 | 0.31359 | 1.1568 | 0.89417 | 0 | -124.9102 | 128.6097 | -41.0296 | -115.4226 | 126.8482

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 1.8556 | 0.71482 | 0.58253 | 1.8541 | 0.71622 | 0.58398 | 21.4264 | 8.254 | 6.7265 | 21.4095 | 8.2702 | 6.7432 | 11.3688 | -6.6153 | 6.0483 | -5.8715 | 6.4326 | -6.3452 | 5.7226 | 6.5185 | 1.3381 | -2.6899 | -6.766 | -1.5008 | -61.5573 | 107.2141 | 114.0813 | 118.4383 | -72.7519 | -65.8937 |  | 0.59403 | 1.1252 | 0.92092 | 0.30166 | 1.1288 | 0.96695 | -34.8386 | -117.3638 | 126.5561 | -36.948 | -119.1988 | 127.4134
Line_1 | 1.5089 | 0.38802 | 0.31621 | 1.5107 | 0.38616 | 0.31435 | 17.4234 | 4.4805 | 3.6513 | 17.4441 | 4.459 | 3.6298 | -4.0904e-11 | 3.5059 | -3.6487 | 4.7511 | -3.8755 | 3.262 | -6.0001e-13 | -3.5512 | -1.5396 | 2.2622 | 3.2118 | 1.2954 | 117.6103 | -79.5422 | -74.2687 | -62.4088 | 100.4511 | 105.7542 |  | 0 | 1.1138 | 1.0846 | 0.30166 | 1.1288 | 0.96695 | 0 | -124.9102 | 128.6097 | -36.948 | -119.1988 | 127.4134
Line_2 | 0.34271 | 0.33749 | 0.27834 | 0.3443 | 0.3359 | 0.27675 | 3.9573 | 3.8971 | 3.214 | 3.9756 | 3.8787 | 3.1956 | -1.188 | 2.8671 | -2.8692 | 1.1204 | -2.557 | 3.0832 | -0.35862 | -3.4791 | -0.16404 | 0.42771 | 3.5541 | 0.20535 | 122.1731 | -64.914 | -56.4241 | -57.8422 | 115.0681 | 123.603 |  | 0.31359 | 1.1568 | 0.89417 | 0.30166 | 1.1288 | 0.96695 | -41.0296 | -115.4226 | 126.8482 | -36.948 | -119.1988 | 127.4134
Line_3 | 1.1668 | 0.10526 | 0.099692 | 1.1686 | 0.10434 | 0.098764 | 13.4733 | 1.2154 | 1.1511 | 13.4939 | 1.2048 | 1.1404 | -3.1611e-11 | 1.3391 | -0.1861 | 3.9033 | -1.3198 | 0.16718 | -1.2053e-12 | 0.19807 | -1.2346 | 1.6343 | -0.44815 | 1.0059 | 116.2673 | -133.3241 | -132.8181 | -63.7487 | 45.8218 | 46.2844 |  | 0 | 1.1138 | 1.0846 | 0.31359 | 1.1568 | 0.89417 | 0 | -124.9102 | 128.6097 | -41.0296 | -115.4226 | 126.8482

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.58151 | 0.22401 | 0.18255 | 0.58105 | 0.22445 | 0.18301 | 6.7147 | 2.5867 | 2.108 | 6.7094 | 2.5917 | 2.1132 | 4.8959 | -1.2257 | 2.0058 | -4.3528 | 1.2079 | -2.0383 | 3.4259 | 2.3737 | -0.34057 | -3.1261 | -2.4017 | 0.32638 | -44.5931 | 124.1782 | 131.0454 | 135.4025 | -55.7877 | -48.9296 |  | 0.88992 | 1.0328 | 0.96517 | 0.79874 | 1.0373 | 0.97684 | -9.6108 | -118.5103 | 121.4092 | -8.9124 | -119.0884 | 121.9733
Line_1 | 0.47287 | 0.1216 | 0.099096 | 0.47343 | 0.12102 | 0.098513 | 5.4602 | 1.4041 | 1.1443 | 5.4667 | 1.3974 | 1.1375 | -3.0391 | 0.76554 | -1.1538 | 3.5086 | -0.79993 | 1.1111 | -2.3732 | -1.2464 | -0.0090138 | 2.5992 | 1.2087 | -0.01445 | 134.5745 | -62.578 | -57.3045 | -45.4447 | 117.4152 | 122.7184 |  | 0.7062 | 1.0418 | 1.0084 | 0.79874 | 1.0373 | 0.97684 | -7.4394 | -121.0201 | 123.1431 | -8.9124 | -119.0884 | 121.9733
Line_2 | 0.1074 | 0.10577 | 0.087227 | 0.1079 | 0.10527 | 0.086729 | 1.2401 | 1.2213 | 1.0072 | 1.2459 | 1.2155 | 1.0015 | -0.84762 | 0.4389 | -0.90993 | 0.84425 | -0.40797 | 0.9272 | -0.51762 | -1.1897 | 0.3176 | 0.52684 | 1.193 | -0.31193 | 139.1372 | -47.9498 | -39.4599 | -40.878 | 132.0322 | 140.5672 |  | 0.80086 | 1.0383 | 0.95686 | 0.79874 | 1.0373 | 0.97684 | -9.4515 | -117.6996 | 121.2994 | -8.9124 | -119.0884 | 121.9733
Line_3 | 0.36566 | 0.032986 | 0.031242 | 0.36622 | 0.032699 | 0.030951 | 4.2223 | 0.38088 | 0.36075 | 4.2288 | 0.37757 | 0.35739 | -2.3065 | 0.39548 | -0.18737 | 2.6928 | -0.39202 | 0.18096 | -1.8898 | -0.032237 | -0.3118 | 2.0538 | 0.0033226 | 0.29017 | 133.2314 | -116.3599 | -115.8539 | -46.7846 | 62.786 | 63.2485 |  | 0.7062 | 1.0418 | 1.0084 | 0.80086 | 1.0383 | 0.95686 | -7.4394 | -121.0201 | 123.1431 | -9.4515 | -117.6996 | 121.2994

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.58151 | 0.22401 | 0.18255 | 0.58105 | 0.22445 | 0.18301 | 6.7147 | 2.5867 | 2.108 | 6.7094 | 2.5917 | 2.1132 | 4.8959 | -1.2257 | 2.0058 | -4.3528 | 1.2079 | -2.0383 | 3.4259 | 2.3737 | -0.34057 | -3.1261 | -2.4017 | 0.32638 | -44.5931 | 124.1782 | 131.0454 | 135.4025 | -55.7877 | -48.9296 |  | 0.88992 | 1.0328 | 0.96517 | 0.79874 | 1.0373 | 0.97684 | -9.6108 | -118.5103 | 121.4092 | -8.9124 | -119.0884 | 121.9733
Line_1 | 0.47287 | 0.1216 | 0.099096 | 0.47343 | 0.12102 | 0.098513 | 5.4602 | 1.4041 | 1.1443 | 5.4667 | 1.3974 | 1.1375 | -3.0391 | 0.76554 | -1.1538 | 3.5086 | -0.79993 | 1.1111 | -2.3732 | -1.2464 | -0.0090138 | 2.5992 | 1.2087 | -0.01445 | 134.5745 | -62.578 | -57.3045 | -45.4447 | 117.4152 | 122.7184 |  | 0.7062 | 1.0418 | 1.0084 | 0.79874 | 1.0373 | 0.97684 | -7.4394 | -121.0201 | 123.1431 | -8.9124 | -119.0884 | 121.9733
Line_2 | 0.1074 | 0.10577 | 0.087227 | 0.1079 | 0.10527 | 0.086729 | 1.2401 | 1.2213 | 1.0072 | 1.2459 | 1.2155 | 1.0015 | -0.84762 | 0.4389 | -0.90993 | 0.84425 | -0.40797 | 0.9272 | -0.51762 | -1.1897 | 0.3176 | 0.52684 | 1.193 | -0.31193 | 139.1372 | -47.9498 | -39.4599 | -40.878 | 132.0322 | 140.5672 |  | 0.80086 | 1.0383 | 0.95686 | 0.79874 | 1.0373 | 0.97684 | -9.4515 | -117.6996 | 121.2994 | -8.9124 | -119.0884 | 121.9733
Line_3 | 0.36566 | 0.032986 | 0.031242 | 0.36622 | 0.032699 | 0.030951 | 4.2223 | 0.38088 | 0.36075 | 4.2288 | 0.37757 | 0.35739 | -2.3065 | 0.39548 | -0.18737 | 2.6928 | -0.39202 | 0.18096 | -1.8898 | -0.032237 | -0.3118 | 2.0538 | 0.0033226 | 0.29017 | 133.2314 | -116.3599 | -115.8539 | -46.7846 | 62.786 | 63.2485 |  | 0.7062 | 1.0418 | 1.0084 | 0.80086 | 1.0383 | 0.95686 | -7.4394 | -121.0201 | 123.1431 | -9.4515 | -117.6996 | 121.2994

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.42544 | 3.1659 | 3.2378 | 0.42693 | 3.1655 | 3.2376 | 4.9126 | 36.5568 | 37.3864 | 4.9298 | 36.5516 | 37.3844 | -2.2342 | 12.9398 | 7.7075 | 2.1273 | -6.1731 | -3.0086 | 5.9323 | 5.1058 | 17.0996 | -6.1462 | -1.2984 | -8.3448 | -103.3714 | -173.1187 | 26.8569 | 76.7668 | 6.913 | -153.1749 |  | 1.2904 | 0.38052 | 0.50169 | 1.3193 | 0.17258 | 0.23728 | 7.2656 | -151.5854 | 92.594 | 5.8582 | -161.2088 | 96.9992
Line_1 | 0.23821 | 2.4226 | 2.4303 | 0.23636 | 2.4228 | 2.4311 | 2.7506 | 27.9732 | 28.063 | 2.7292 | 27.9759 | 28.0719 | 1.3494 | 6.4856e-11 | 8.7823e-11 | -1.4619 | 4.6343 | 2.672 | -3.507 | -6.5049e-11 | -2.1771e-11 | 3.2906 | 1.3546 | 6.1015 | 72.1308 | 2.5461 | -149.3962 | -108.0959 | -177.5027 | 30.6493 |  | 1.3661 | 0 | 0 | 1.3193 | 0.17258 | 0.23728 | 3.176 | 0 | 0 | 5.8582 | -161.2088 | 96.9992
Line_2 | 0.19419 | 0.77283 | 0.82801 | 0.19247 | 0.77272 | 0.82793 | 2.2424 | 8.9238 | 9.561 | 2.2225 | 8.9226 | 9.5602 | 0.72347 | -1.2518 | 0.072407 | -0.66537 | 1.5389 | 0.33656 | -2.8313 | 0.62527 | -2.0644 | 2.8556 | -0.056185 | 2.2433 | 82.9788 | 21.0227 | -164.6 | -97.258 | -159.1178 | 15.5313 |  | 1.3032 | 0.1568 | 0.21605 | 1.3193 | 0.17258 | 0.23728 | 7.3126 | 174.4806 | 107.4088 | 5.8582 | -161.2088 | 96.9992
Line_3 | 0.060167 | 1.7068 | 1.6454 | 0.059342 | 1.7074 | 1.6463 | 0.69474 | 19.7086 | 18.9994 | 0.68523 | 19.7153 | 19.0102 | 0.8028 | 5.1777e-11 | 5.7006e-11 | -0.80054 | 3.0914 | 1.4591 | -0.50626 | -3.8827e-11 | -2.2425e-11 | 0.39572 | 0.01188 | 3.8392 | 35.4121 | -5.6737 | -141.845 | -146.3831 | 174.2604 | 38.2182 |  | 1.3661 | 0 | 0 | 1.3032 | 0.1568 | 0.21605 | 3.176 | 0 | 0 | 7.3126 | 174.4806 | 107.4088

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.42544 | 3.1659 | 3.2378 | 0.42693 | 3.1655 | 3.2376 | 4.9126 | 36.5568 | 37.3864 | 4.9298 | 36.5516 | 37.3844 | -2.2342 | 12.9398 | 7.7075 | 2.1273 | -6.1731 | -3.0086 | 5.9323 | 5.1058 | 17.0996 | -6.1462 | -1.2984 | -8.3448 | -103.3714 | -173.1187 | 26.8569 | 76.7668 | 6.913 | -153.1749 |  | 1.2904 | 0.38052 | 0.50169 | 1.3193 | 0.17258 | 0.23728 | 7.2656 | -151.5854 | 92.594 | 5.8582 | -161.2088 | 96.9992
Line_1 | 0.23821 | 2.4226 | 2.4303 | 0.23636 | 2.4228 | 2.4311 | 2.7506 | 27.9732 | 28.063 | 2.7292 | 27.9759 | 28.0719 | 1.3494 | 6.4856e-11 | 8.7823e-11 | -1.4619 | 4.6343 | 2.672 | -3.507 | -6.5049e-11 | -2.1771e-11 | 3.2906 | 1.3546 | 6.1015 | 72.1308 | 2.5461 | -149.3962 | -108.0959 | -177.5027 | 30.6493 |  | 1.3661 | 0 | 0 | 1.3193 | 0.17258 | 0.23728 | 3.176 | 0 | 0 | 5.8582 | -161.2088 | 96.9992
Line_2 | 0.19419 | 0.77283 | 0.82801 | 0.19247 | 0.77272 | 0.82793 | 2.2424 | 8.9238 | 9.561 | 2.2225 | 8.9226 | 9.5602 | 0.72347 | -1.2518 | 0.072407 | -0.66537 | 1.5389 | 0.33656 | -2.8313 | 0.62527 | -2.0644 | 2.8556 | -0.056185 | 2.2433 | 82.9788 | 21.0227 | -164.6 | -97.258 | -159.1178 | 15.5313 |  | 1.3032 | 0.1568 | 0.21605 | 1.3193 | 0.17258 | 0.23728 | 7.3126 | 174.4806 | 107.4088 | 5.8582 | -161.2088 | 96.9992
Line_3 | 0.060167 | 1.7068 | 1.6454 | 0.059342 | 1.7074 | 1.6463 | 0.69474 | 19.7086 | 18.9994 | 0.68523 | 19.7153 | 19.0102 | 0.8028 | 5.1777e-11 | 5.7006e-11 | -0.80054 | 3.0914 | 1.4591 | -0.50626 | -3.8827e-11 | -2.2425e-11 | 0.39572 | 0.01188 | 3.8392 | 35.4121 | -5.6737 | -141.845 | -146.3831 | 174.2604 | 38.2182 |  | 1.3661 | 0 | 0 | 1.3032 | 0.1568 | 0.21605 | 3.176 | 0 | 0 | 7.3126 | 174.4806 | 107.4088

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.031083 | 0.73702 | 0.69398 | 0.03089 | 0.73695 | 0.69383 | 0.35892 | 8.5103 | 8.0134 | 0.35668 | 8.5096 | 8.0117 | 0.2243 | 7.6671 | 4.5742 | -0.22954 | -7.2891 | -4.3457 | -0.35627 | 2.3627 | 6.7313 | 0.35899 | -2.2167 | -6.2587 | 61.3241 | -143.9956 | 55.7745 | -119.7412 | 36.0514 | -124.2743 |  | 1.173 | 0.94272 | 1.0156 | 1.1946 | 0.89531 | 0.95104 | 3.5174 | -126.8684 | 111.577 | 2.8537 | -127.0333 | 110.9518
Line_1 | 0.0046632 | 0.58938 | 0.57322 | 0.0051467 | 0.58942 | 0.57356 | 0.053846 | 6.8056 | 6.6189 | 0.059429 | 6.8061 | 6.6229 | -0.023882 | -5.1504 | -3.744 | 0.019844 | 5.4484 | 3.919 | 0.06129 | -2.6962 | -4.5285 | -0.068166 | 2.7287 | 4.931 | -109.2488 | 26.4318 | -120.6316 | 76.6228 | -153.6358 | 59.429 |  | 1.2216 | 0.85422 | 0.88772 | 1.1946 | 0.89531 | 0.95104 | 2.0403 | -125.9363 | 109.7855 | 2.8537 | -127.0333 | 110.9518
Line_2 | 0.025798 | 0.18512 | 0.12699 | 0.025992 | 0.1848 | 0.12699 | 0.29788 | 2.1376 | 1.4664 | 0.30013 | 2.1339 | 1.4664 | -0.21481 | -1.8184 | -0.40958 | 0.2097 | 1.8406 | 0.42664 | 0.2817 | 0.5547 | -1.332 | -0.29083 | -0.51195 | 1.3277 | -124.2835 | 68.6809 | -141.5223 | 57.0607 | -111.4903 | 38.7654 |  | 1.1892 | 0.88939 | 0.95033 | 1.1946 | 0.89531 | 0.95104 | 3.0438 | -128.2831 | 111.3854 | 2.8537 | -127.0333 | 110.9518
Line_3 | 0.021395 | 0.469 | 0.45669 | 0.021151 | 0.46925 | 0.45707 | 0.24704 | 5.4156 | 5.2734 | 0.24423 | 5.4184 | 5.2778 | 0.18889 | -3.3843 | -3.3238 | -0.19238 | 3.6527 | 3.4657 | -0.23537 | -3.154 | -3.2966 | 0.2176 | 3.1434 | 3.6257 | 53.2935 | 11.0807 | -114.9787 | -128.437 | -168.9979 | 65.0933 |  | 1.2216 | 0.85422 | 0.88772 | 1.1892 | 0.88939 | 0.95033 | 2.0403 | -125.9363 | 109.7855 | 3.0438 | -128.2831 | 111.3854

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.031083 | 0.73702 | 0.69398 | 0.03089 | 0.73695 | 0.69383 | 0.35892 | 8.5103 | 8.0134 | 0.35668 | 8.5096 | 8.0117 | 0.2243 | 7.6671 | 4.5742 | -0.22954 | -7.2891 | -4.3457 | -0.35627 | 2.3627 | 6.7313 | 0.35899 | -2.2167 | -6.2587 | 61.3241 | -143.9956 | 55.7745 | -119.7412 | 36.0514 | -124.2743 |  | 1.173 | 0.94272 | 1.0156 | 1.1946 | 0.89531 | 0.95104 | 3.5174 | -126.8684 | 111.577 | 2.8537 | -127.0333 | 110.9518
Line_1 | 0.0046632 | 0.58938 | 0.57322 | 0.0051467 | 0.58942 | 0.57356 | 0.053846 | 6.8056 | 6.6189 | 0.059429 | 6.8061 | 6.6229 | -0.023882 | -5.1504 | -3.744 | 0.019844 | 5.4484 | 3.919 | 0.06129 | -2.6962 | -4.5285 | -0.068166 | 2.7287 | 4.931 | -109.2488 | 26.4318 | -120.6316 | 76.6228 | -153.6358 | 59.429 |  | 1.2216 | 0.85422 | 0.88772 | 1.1946 | 0.89531 | 0.95104 | 2.0403 | -125.9363 | 109.7855 | 2.8537 | -127.0333 | 110.9518
Line_2 | 0.025798 | 0.18512 | 0.12699 | 0.025992 | 0.1848 | 0.12699 | 0.29788 | 2.1376 | 1.4664 | 0.30013 | 2.1339 | 1.4664 | -0.21481 | -1.8184 | -0.40958 | 0.2097 | 1.8406 | 0.42664 | 0.2817 | 0.5547 | -1.332 | -0.29083 | -0.51195 | 1.3277 | -124.2835 | 68.6809 | -141.5223 | 57.0607 | -111.4903 | 38.7654 |  | 1.1892 | 0.88939 | 0.95033 | 1.1946 | 0.89531 | 0.95104 | 3.0438 | -128.2831 | 111.3854 | 2.8537 | -127.0333 | 110.9518
Line_3 | 0.021395 | 0.469 | 0.45669 | 0.021151 | 0.46925 | 0.45707 | 0.24704 | 5.4156 | 5.2734 | 0.24423 | 5.4184 | 5.2778 | 0.18889 | -3.3843 | -3.3238 | -0.19238 | 3.6527 | 3.4657 | -0.23537 | -3.154 | -3.2966 | 0.2176 | 3.1434 | 3.6257 | 53.2935 | 11.0807 | -114.9787 | -128.437 | -168.9979 | 65.0933 |  | 1.2216 | 0.85422 | 0.88772 | 1.1892 | 0.88939 | 0.95033 | 2.0403 | -125.9363 | 109.7855 | 3.0438 | -128.2831 | 111.3854

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.5201 | 2.592 | 2.6273 | 0.52124 | 2.5917 | 2.6272 | 6.0056 | 29.9304 | 30.338 | 6.0188 | 29.926 | 30.3368 | -0.30129 | 15.8785 | 10.4341 | 0.19554 | -7.4417 | -4.3178 | 6.2623 | 0.85787 | 14.1155 | -6.5513 | 0.8597 | -7.2771 | -84.5828 | -162.41 | 39.3744 | 95.4876 | 17.6176 | -140.654 |  | 1.0439 | 0.53129 | 0.57859 | 1.089 | 0.25033 | 0.27892 | 8.1717 | -159.3175 | 92.9028 | 7.1972 | -168.9723 | 98.6638
Line_1 | 0.29208 | 1.9831 | 1.9507 | 0.29047 | 1.9831 | 1.9516 | 3.3727 | 22.8994 | 22.5253 | 3.3541 | 22.8993 | 22.5346 | 0.34526 | -7.1593e-11 | -3.8896e-11 | -0.5532 | 5.7297 | 3.4512 | -3.9285 | -4.6114e-11 | -7.5308e-11 | 3.6103 | -0.17119 | 5.2532 | 88.5648 | 12.7869 | -138.075 | -91.5143 | -167.261 | 41.9674 |  | 1.1693 | 0 | 0 | 1.089 | 0.25033 | 0.27892 | 3.5875 | 0 | 0 | 7.1972 | -168.9723 | 98.6638
Line_2 | 0.23698 | 0.63847 | 0.68353 | 0.23561 | 0.63839 | 0.68358 | 2.7364 | 7.3724 | 7.8927 | 2.7206 | 7.3715 | 7.8933 | -0.19831 | -1.3069 | -0.3846 | 0.35766 | 1.712 | 0.8666 | -2.8855 | 1.2474 | -2.0864 | 2.9409 | -0.68851 | 2.0239 | 104.2226 | 33.0631 | -148.2754 | -75.8688 | -147.0639 | 31.8433 |  | 1.057 | 0.24505 | 0.26879 | 1.089 | 0.25033 | 0.27892 | 10.291 | 169.398 | 111.2798 | 7.1972 | -168.9723 | 98.6638
Line_3 | 0.09052 | 1.4014 | 1.2836 | 0.089792 | 1.4018 | 1.2844 | 1.0452 | 16.1825 | 14.8216 | 1.0368 | 16.1867 | 14.831 | 0.93087 | -4.4833e-11 | -3.0127e-11 | -0.92143 | 3.8442 | 1.753 | -0.79198 | -4.0145e-11 | -4.6934e-11 | 0.59327 | -0.97758 | 3.5804 | 43.9785 | 3.7301 | -132.695 | -136.9332 | -176.334 | 47.3667 |  | 1.1693 | 0 | 0 | 1.057 | 0.24505 | 0.26879 | 3.5875 | 0 | 0 | 10.291 | 169.398 | 111.2798

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.5201 | 2.592 | 2.6273 | 0.52124 | 2.5917 | 2.6272 | 6.0056 | 29.9304 | 30.338 | 6.0188 | 29.926 | 30.3368 | -0.30129 | 15.8785 | 10.4341 | 0.19554 | -7.4417 | -4.3178 | 6.2623 | 0.85787 | 14.1155 | -6.5513 | 0.8597 | -7.2771 | -84.5828 | -162.41 | 39.3744 | 95.4876 | 17.6176 | -140.654 |  | 1.0439 | 0.53129 | 0.57859 | 1.089 | 0.25033 | 0.27892 | 8.1717 | -159.3175 | 92.9028 | 7.1972 | -168.9723 | 98.6638
Line_1 | 0.29208 | 1.9831 | 1.9507 | 0.29047 | 1.9831 | 1.9516 | 3.3727 | 22.8994 | 22.5253 | 3.3541 | 22.8993 | 22.5346 | 0.34526 | -7.1593e-11 | -3.8896e-11 | -0.5532 | 5.7297 | 3.4512 | -3.9285 | -4.6114e-11 | -7.5308e-11 | 3.6103 | -0.17119 | 5.2532 | 88.5648 | 12.7869 | -138.075 | -91.5143 | -167.261 | 41.9674 |  | 1.1693 | 0 | 0 | 1.089 | 0.25033 | 0.27892 | 3.5875 | 0 | 0 | 7.1972 | -168.9723 | 98.6638
Line_2 | 0.23698 | 0.63847 | 0.68353 | 0.23561 | 0.63839 | 0.68358 | 2.7364 | 7.3724 | 7.8927 | 2.7206 | 7.3715 | 7.8933 | -0.19831 | -1.3069 | -0.3846 | 0.35766 | 1.712 | 0.8666 | -2.8855 | 1.2474 | -2.0864 | 2.9409 | -0.68851 | 2.0239 | 104.2226 | 33.0631 | -148.2754 | -75.8688 | -147.0639 | 31.8433 |  | 1.057 | 0.24505 | 0.26879 | 1.089 | 0.25033 | 0.27892 | 10.291 | 169.398 | 111.2798 | 7.1972 | -168.9723 | 98.6638
Line_3 | 0.09052 | 1.4014 | 1.2836 | 0.089792 | 1.4018 | 1.2844 | 1.0452 | 16.1825 | 14.8216 | 1.0368 | 16.1867 | 14.831 | 0.93087 | -4.4833e-11 | -3.0127e-11 | -0.92143 | 3.8442 | 1.753 | -0.79198 | -4.0145e-11 | -4.6934e-11 | 0.59327 | -0.97758 | 3.5804 | 43.9785 | 3.7301 | -132.695 | -136.9332 | -176.334 | 47.3667 |  | 1.1693 | 0 | 0 | 1.057 | 0.24505 | 0.26879 | 3.5875 | 0 | 0 | 10.291 | 169.398 | 111.2798

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.17897 | 0.7213 | 0.72528 | 0.17936 | 0.72115 | 0.72522 | 2.0665 | 8.3289 | 8.3748 | 2.0711 | 8.3271 | 8.3741 | 0.75408 | 6.6961 | 4.4399 | -0.77164 | -6.0041 | -3.9713 | 1.9212 | 2.5167 | 6.1878 | -1.9539 | -2.4103 | -5.6171 | -65.7354 | -149.4056 | 57.8209 | 114.327 | 30.6275 | -122.2138 |  | 0.99871 | 0.85887 | 0.90938 | 1.0143 | 0.77696 | 0.82148 | 2.8341 | -128.8069 | 112.1609 | 2.7772 | -127.4998 | 112.526
Line_1 | 0.099883 | 0.5565 | 0.54205 | 0.099331 | 0.55653 | 0.54235 | 1.1533 | 6.426 | 6.259 | 1.147 | 6.4263 | 6.2625 | -0.31746 | -3.9448 | -2.9331 | 0.28877 | 4.4365 | 3.2161 | -1.1656 | -2.3309 | -3.5575 | 1.127 | 2.2906 | 4.0153 | 107.2108 | 25.2502 | -118.8302 | -72.8512 | -154.8076 | 61.2196 |  | 1.0474 | 0.71304 | 0.73665 | 1.0143 | 0.77696 | 0.82148 | 1.9754 | -124.1717 | 111.6651 | 2.7772 | -127.4998 | 112.526
Line_2 | 0.082228 | 0.17526 | 0.18667 | 0.081758 | 0.17524 | 0.18669 | 0.94948 | 2.0237 | 2.1555 | 0.94406 | 2.0235 | 2.1557 | -0.46673 | -1.538 | -0.71523 | 0.48287 | 1.5676 | 0.75515 | -0.82327 | -0.068015 | -1.6142 | 0.82693 | 0.11969 | 1.6018 | 123.13 | 48.2911 | -132.3805 | -56.9408 | -131.8659 | 47.7669 |  | 0.99672 | 0.76071 | 0.81909 | 1.0143 | 0.77696 | 0.82148 | 3.5798 | -129.1767 | 113.7216 | 2.7772 | -127.4998 | 112.526
Line_3 | 0.030727 | 0.401 | 0.36314 | 0.030474 | 0.40116 | 0.36346 | 0.35481 | 4.6303 | 4.1932 | 0.35189 | 4.6321 | 4.1969 | 0.1949 | -2.5144 | -2.2364 | -0.19684 | 2.8699 | 2.4051 | -0.31643 | -2.1397 | -2.1308 | 0.29029 | 2.0445 | 2.4562 | 60.3449 | 15.4319 | -111.9499 | -120.5602 | -164.6426 | 68.1199 |  | 1.0474 | 0.71304 | 0.73665 | 0.99672 | 0.76071 | 0.81909 | 1.9754 | -124.1717 | 111.6651 | 3.5798 | -129.1767 | 113.7216

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line_0 | 0.17897 | 0.7213 | 0.72528 | 0.17936 | 0.72115 | 0.72522 | 2.0665 | 8.3289 | 8.3748 | 2.0711 | 8.3271 | 8.3741 | 0.75408 | 6.6961 | 4.4399 | -0.77164 | -6.0041 | -3.9713 | 1.9212 | 2.5167 | 6.1878 | -1.9539 | -2.4103 | -5.6171 | -65.7354 | -149.4056 | 57.8209 | 114.327 | 30.6275 | -122.2138 |  | 0.99871 | 0.85887 | 0.90938 | 1.0143 | 0.77696 | 0.82148 | 2.8341 | -128.8069 | 112.1609 | 2.7772 | -127.4998 | 112.526
Line_1 | 0.099883 | 0.5565 | 0.54205 | 0.099331 | 0.55653 | 0.54235 | 1.1533 | 6.426 | 6.259 | 1.147 | 6.4263 | 6.2625 | -0.31746 | -3.9448 | -2.9331 | 0.28877 | 4.4365 | 3.2161 | -1.1656 | -2.3309 | -3.5575 | 1.127 | 2.2906 | 4.0153 | 107.2108 | 25.2502 | -118.8302 | -72.8512 | -154.8076 | 61.2196 |  | 1.0474 | 0.71304 | 0.73665 | 1.0143 | 0.77696 | 0.82148 | 1.9754 | -124.1717 | 111.6651 | 2.7772 | -127.4998 | 112.526
Line_2 | 0.082228 | 0.17526 | 0.18667 | 0.081758 | 0.17524 | 0.18669 | 0.94948 | 2.0237 | 2.1555 | 0.94406 | 2.0235 | 2.1557 | -0.46673 | -1.538 | -0.71523 | 0.48287 | 1.5676 | 0.75515 | -0.82327 | -0.068015 | -1.6142 | 0.82693 | 0.11969 | 1.6018 | 123.13 | 48.2911 | -132.3805 | -56.9408 | -131.8659 | 47.7669 |  | 0.99672 | 0.76071 | 0.81909 | 1.0143 | 0.77696 | 0.82148 | 3.5798 | -129.1767 | 113.7216 | 2.7772 | -127.4998 | 112.526
Line_3 | 0.030727 | 0.401 | 0.36314 | 0.030474 | 0.40116 | 0.36346 | 0.35481 | 4.6303 | 4.1932 | 0.35189 | 4.6321 | 4.1969 | 0.1949 | -2.5144 | -2.2364 | -0.19684 | 2.8699 | 2.4051 | -0.31643 | -2.1397 | -2.1308 | 0.29029 | 2.0445 | 2.4562 | 60.3449 | 15.4319 | -111.9499 | -120.5602 | -164.6426 | 68.1199 |  | 1.0474 | 0.71304 | 0.73665 | 0.99672 | 0.76071 | 0.81909 | 1.9754 | -124.1717 | 111.6651 | 3.5798 | -129.1767 | 113.7216