## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.67127 | 0.67127 | 0 | 0 | 0.46507 | 0.46507 | -0.011121 | 0.024639 | -0.12747 | 0.15451 | 104.0538 | -75.9462 | 0.27513 | 0.33642 | 9.0679 | 4.9933
Line10_11_12 | 0.59764 | 0.59764 | 0 | 0 | 0.41406 | 0.41406 | -0.032715 | 0.043431 | -0.15622 | 0.17765 | 104.7529 | -75.2471 | 0.38548 | 0.44168 | 2.9251 | 1.0152
Line11_12_13 | 0.59764 | 0.59764 | 0 | 0 | 0.41406 | 0.41406 | -0.043431 | 0.054146 | -0.17765 | 0.19908 | 104.7529 | -75.2471 | 0.44168 | 0.49827 | 1.0152 | -0.46229
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49827 | 0.49827 | -0.46229 | -0.46229
Line13_13_14 | 0.59764 | 0.59764 | 0 | 0 | 0.41406 | 0.41406 | -0.054146 | 0.064861 | -0.19908 | 0.22051 | 104.7529 | -75.2471 | 0.49827 | 0.55512 | -0.46229 | -1.6378
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49827 | 0.49827 | -0.46229 | -0.46229
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49827 | 0.49827 | -0.46229 | -0.46229
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34476 | 0.34476 | 4.3555 | 4.3555
Line17_5_19 | 0.71524 | 0.71524 | 0 | 0 | 0.49553 | 0.49553 | -0.026205 | 0.041551 | -0.1666 | 0.19729 | 103.6358 | -76.3642 | 0.34033 | 0.40687 | 4.6967 | 1.7424
Line1_1_3 | 0.59764 | 0.59764 | 0 | 0 | 0.41406 | 0.41406 | -0.011285 | 0.022 | -0.11336 | 0.13479 | 104.7529 | -75.2471 | 0.27513 | 0.32984 | 9.0679 | 5.483
Line2_1_4 | 0.76527 | 0.76527 | 0 | 0 | 0.5302 | 0.5302 | -0.010408 | 0.027977 | -0.1455 | 0.18064 | 103.1595 | -76.8405 | 0.27513 | 0.34476 | 9.0679 | 4.3555
Line3_1_5 | 0.71524 | 0.71524 | 0 | 0 | 0.49553 | 0.49553 | -0.010858 | 0.026205 | -0.1359 | 0.1666 | 103.6358 | -76.3642 | 0.27513 | 0.34033 | 9.0679 | 4.6967
Line4_2_6 | 0.67127 | 0.67127 | 0 | 0 | 0.46507 | 0.46507 | -0.024639 | 0.038157 | -0.15451 | 0.18154 | 104.0538 | -75.9462 | 0.33642 | 0.39888 | 4.9933 | 2.1841
Line5_6_7 | 0.67127 | 0.67127 | 0 | 0 | 0.46507 | 0.46507 | -0.038157 | 0.051675 | -0.18154 | 0.20858 | 104.0538 | -75.9462 | 0.39888 | 0.46205 | 2.1841 | 0.1391
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46205 | 0.46205 | 0.1391 | 0.1391
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46205 | 0.46205 | 0.1391 | 0.1391
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46205 | 0.46205 | 0.1391 | 0.1391
Line9_3_11 | 0.59764 | 0.59764 | 0 | 0 | 0.41406 | 0.41406 | -0.022 | 0.032715 | -0.13479 | 0.15622 | 104.7529 | -75.2471 | 0.32984 | 0.38548 | 5.483 | 2.9251

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.6503 | 0.6503 | 0 | 0 | 0.45054 | 0.45054 | -0.010894 | 0.02358 | -0.12518 | 0.15055 | 103.9276 | -76.0724 | 0.27889 | 0.33823 | 8.9539 | 5.0259
Line10_11_12 | 0.58136 | 0.58136 | 0 | 0 | 0.40278 | 0.40278 | -0.031334 | 0.041473 | -0.15235 | 0.17262 | 104.6016 | -75.3984 | 0.38615 | 0.44078 | 2.9793 | 1.0922
Line11_12_13 | 0.58136 | 0.58136 | 0 | 0 | 0.40278 | 0.40278 | -0.041473 | 0.051613 | -0.17262 | 0.1929 | 104.6016 | -75.3984 | 0.44078 | 0.49578 | 1.0922 | -0.37747
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49578 | 0.49578 | -0.37747 | -0.37746
Line13_13_14 | 0.58136 | 0.58136 | 0 | 0 | 0.40278 | 0.40278 | -0.051613 | 0.061752 | -0.1929 | 0.21318 | 104.6016 | -75.3984 | 0.49578 | 0.55104 | -0.37747 | -1.553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49578 | 0.49578 | -0.37746 | -0.37746
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49578 | 0.49578 | -0.37746 | -0.37746
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34597 | 0.34597 | 4.4341 | 4.4341
Line17_5_19 | 0.69119 | 0.69119 | 0 | 0 | 0.47887 | 0.47887 | -0.024981 | 0.039314 | -0.16179 | 0.19046 | 103.5273 | -76.4727 | 0.34187 | 0.40611 | 4.75 | 1.8643
Line1_1_3 | 0.58136 | 0.58136 | 0 | 0 | 0.40278 | 0.40278 | -0.011055 | 0.021194 | -0.11179 | 0.13207 | 104.6016 | -75.3984 | 0.27889 | 0.33208 | 8.9539 | 5.4844
Line2_1_4 | 0.73749 | 0.73749 | 0 | 0 | 0.51095 | 0.51095 | -0.010237 | 0.026554 | -0.14213 | 0.17477 | 103.0734 | -76.9266 | 0.27889 | 0.34597 | 8.9539 | 4.4341
Line3_1_5 | 0.69119 | 0.69119 | 0 | 0 | 0.47887 | 0.47887 | -0.010649 | 0.024981 | -0.13313 | 0.16179 | 103.5273 | -76.4727 | 0.27889 | 0.34187 | 8.9539 | 4.75
Line4_2_6 | 0.6503 | 0.6503 | 0 | 0 | 0.45054 | 0.45054 | -0.02358 | 0.036267 | -0.15055 | 0.17593 | 103.9276 | -76.0724 | 0.33823 | 0.39869 | 5.0259 | 2.2793
Line5_6_7 | 0.6503 | 0.6503 | 0 | 0 | 0.45054 | 0.45054 | -0.036267 | 0.048954 | -0.17593 | 0.2013 | 103.9276 | -76.0724 | 0.39869 | 0.45982 | 2.2793 | 0.25926
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45982 | 0.45982 | 0.25926 | 0.25926
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45982 | 0.45982 | 0.25926 | 0.25926
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45982 | 0.45982 | 0.25926 | 0.25926
Line9_3_11 | 0.58136 | 0.58136 | 0 | 0 | 0.40278 | 0.40278 | -0.021194 | 0.031334 | -0.13207 | 0.15235 | 104.6016 | -75.3984 | 0.33208 | 0.38615 | 5.4844 | 2.9793

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.11823 | 0.11823 | 0 | 0 | 0.081914 | 0.081914 | -0.014777 | 0.015197 | -0.091835 | 0.092674 | 98.7809 | -81.2191 | 1.1355 | 1.1465 | -0.36018 | -0.5315
Line10_11_12 | 0.10529 | 0.10529 | 0 | 0 | 0.07295 | 0.07295 | -0.013578 | 0.01391 | -0.083155 | 0.08382 | 98.6076 | -81.3924 | 1.155 | 1.1647 | -0.66598 | -0.81505
Line11_12_13 | 0.10529 | 0.10529 | 0 | 0 | 0.07295 | 0.07295 | -0.01391 | 0.014243 | -0.08382 | 0.084485 | 98.6076 | -81.3924 | 1.1647 | 1.1745 | -0.81505 | -0.96165
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1745 | 1.1745 | -0.96165 | -0.96165
Line13_13_14 | 0.10529 | 0.10529 | 0 | 0 | 0.07295 | 0.07295 | -0.014243 | 0.014576 | -0.084485 | 0.085151 | 98.6076 | -81.3924 | 1.1745 | 1.1842 | -0.96165 | -1.1058
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1745 | 1.1745 | -0.96165 | -0.96165
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1745 | 1.1745 | -0.96165 | -0.96165
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.148 | 1.148 | -0.55278 | -0.55278
Line17_5_19 | 0.12596 | 0.12596 | 0 | 0 | 0.087269 | 0.087269 | -0.016396 | 0.016872 | -0.098762 | 0.099714 | 98.8846 | -81.1154 | 1.1472 | 1.1588 | -0.54153 | -0.71923
Line1_1_3 | 0.10529 | 0.10529 | 0 | 0 | 0.07295 | 0.07295 | -0.012913 | 0.013245 | -0.081825 | 0.08249 | 98.6076 | -81.3924 | 1.1355 | 1.1453 | -0.36018 | -0.51438
Line2_1_4 | 0.13476 | 0.13476 | 0 | 0 | 0.093365 | 0.093365 | -0.017248 | 0.017793 | -0.10461 | 0.1057 | 99.0026 | -80.9974 | 1.1355 | 1.148 | -0.36018 | -0.55278
Line3_1_5 | 0.12596 | 0.12596 | 0 | 0 | 0.087269 | 0.087269 | -0.01592 | 0.016396 | -0.09781 | 0.098762 | 98.8846 | -81.1154 | 1.1355 | 1.1472 | -0.36018 | -0.54153
Line4_2_6 | 0.11823 | 0.11823 | 0 | 0 | 0.081914 | 0.081914 | -0.015197 | 0.015616 | -0.092674 | 0.093513 | 98.7809 | -81.2191 | 1.1465 | 1.1574 | -0.5315 | -0.69957
Line5_6_7 | 0.11823 | 0.11823 | 0 | 0 | 0.081914 | 0.081914 | -0.015616 | 0.016035 | -0.093513 | 0.094351 | 98.7809 | -81.2191 | 1.1574 | 1.1683 | -0.69957 | -0.8645
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1683 | 1.1683 | -0.8645 | -0.8645
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1683 | 1.1683 | -0.8645 | -0.8645
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1683 | 1.1683 | -0.8645 | -0.8645
Line9_3_11 | 0.10529 | 0.10529 | 0 | 0 | 0.07295 | 0.07295 | -0.013245 | 0.013578 | -0.08249 | 0.083155 | 98.6076 | -81.3924 | 1.1453 | 1.155 | -0.51438 | -0.66598

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.11879 | 0.11879 | 0 | 0 | 0.082299 | 0.082299 | -0.014653 | 0.015076 | -0.092505 | 0.093351 | 98.6444 | -81.3556 | 1.138 | 1.149 | -0.35676 | -0.52983
Line10_11_12 | 0.10623 | 0.10623 | 0 | 0 | 0.073598 | 0.073598 | -0.013532 | 0.01387 | -0.084118 | 0.084796 | 98.4716 | -81.5284 | 1.1576 | 1.1675 | -0.66693 | -0.81811
Line11_12_13 | 0.10623 | 0.10623 | 0 | 0 | 0.073598 | 0.073598 | -0.01387 | 0.014209 | -0.084796 | 0.085473 | 98.4716 | -81.5284 | 1.1675 | 1.1773 | -0.81811 | -0.96677
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1773 | 1.1773 | -0.96677 | -0.96677
Line13_13_14 | 0.10623 | 0.10623 | 0 | 0 | 0.073598 | 0.073598 | -0.014209 | 0.014547 | -0.085473 | 0.08615 | 98.4716 | -81.5284 | 1.1773 | 1.1871 | -0.96677 | -1.113
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1773 | 1.1773 | -0.96677 | -0.96677
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1773 | 1.1773 | -0.96677 | -0.96677
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1505 | 1.1505 | -0.55037 | -0.55037
Line17_5_19 | 0.12624 | 0.12624 | 0 | 0 | 0.087462 | 0.087462 | -0.016227 | 0.016705 | -0.099236 | 0.10019 | 98.747 | -81.253 | 1.1497 | 1.1614 | -0.53954 | -0.71865
Line1_1_3 | 0.10623 | 0.10623 | 0 | 0 | 0.073598 | 0.073598 | -0.012854 | 0.013193 | -0.082764 | 0.083441 | 98.4716 | -81.5284 | 1.138 | 1.1478 | -0.35676 | -0.51317
Line2_1_4 | 0.13468 | 0.13468 | 0 | 0 | 0.093309 | 0.093309 | -0.017014 | 0.017558 | -0.10482 | 0.1059 | 98.8633 | -81.1367 | 1.138 | 1.1505 | -0.35676 | -0.55037
Line3_1_5 | 0.12624 | 0.12624 | 0 | 0 | 0.087462 | 0.087462 | -0.015748 | 0.016227 | -0.09828 | 0.099236 | 98.747 | -81.253 | 1.138 | 1.1497 | -0.35676 | -0.53954
Line4_2_6 | 0.11879 | 0.11879 | 0 | 0 | 0.082299 | 0.082299 | -0.015076 | 0.0155 | -0.093351 | 0.094198 | 98.6444 | -81.3556 | 1.149 | 1.16 | -0.52983 | -0.69964
Line5_6_7 | 0.11879 | 0.11879 | 0 | 0 | 0.082299 | 0.082299 | -0.0155 | 0.015923 | -0.094198 | 0.095044 | 98.6444 | -81.3556 | 1.16 | 1.171 | -0.69964 | -0.86625
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.171 | 1.171 | -0.86625 | -0.86625
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.171 | 1.171 | -0.86625 | -0.86625
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.171 | 1.171 | -0.86625 | -0.86625
Line9_3_11 | 0.10623 | 0.10623 | 0 | 0 | 0.073598 | 0.073598 | -0.013193 | 0.013532 | -0.083441 | 0.084118 | 98.4716 | -81.5284 | 1.1478 | 1.1576 | -0.51317 | -0.66693

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.016264 | 0.016264 | 0 | 0 | 0.011268 | 0.011268 | -6.3685e-06 | 2.1604e-05 | -7.5945e-05 | 9.1816e-05 | 106.7727 | -73.2273 | 0.0067637 | 0.008371 | 11.9792 | 3.5319
Line10_11_12 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -3.6739e-05 | 5.1869e-05 | -0.00010719 | 0.00012295 | 106.8745 | -73.1255 | 0.010091 | 0.011884 | -2.045 | -5.9993
Line11_12_13 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -5.1869e-05 | 6.6998e-05 | -0.00012295 | 0.00013871 | 106.8744 | -73.1256 | 0.011884 | 0.013719 | -5.9993 | -8.9069
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013719 | 0.013719 | -8.9069 | -8.9069
Line13_13_14 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -6.6997e-05 | 8.2127e-05 | -0.00013871 | 0.00015447 | 106.8742 | -73.1258 | 0.013719 | 0.01558 | -8.9069 | -11.1243
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013719 | 0.013719 | -8.9069 | -8.9069
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013719 | 0.013719 | -8.9069 | -8.9068
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083751 | 0.0083751 | 3.4873 | 3.4873
Line17_5_19 | 0.016292 | 0.016292 | 0 | 0 | 0.011288 | 0.011288 | -2.16e-05 | 3.6889e-05 | -9.201e-05 | 0.00010794 | 106.7212 | -73.2788 | 0.0083731 | 0.010105 | 3.5096 | -2.1477
Line1_1_3 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -6.4809e-06 | 2.161e-05 | -7.5669e-05 | 9.1428e-05 | 106.8746 | -73.1254 | 0.0067637 | 0.0083669 | 11.9792 | 3.576
Line2_1_4 | 0.016321 | 0.016321 | 0 | 0 | 0.011307 | 0.011307 | -6.2542e-06 | 2.1597e-05 | -7.6223e-05 | 9.2205e-05 | 106.6699 | -73.3301 | 0.0067637 | 0.0083751 | 11.9792 | 3.4873
Line3_1_5 | 0.016292 | 0.016292 | 0 | 0 | 0.011288 | 0.011288 | -6.3114e-06 | 2.1601e-05 | -7.6084e-05 | 9.201e-05 | 106.7213 | -73.2787 | 0.0067637 | 0.0083731 | 11.9792 | 3.5096
Line4_2_6 | 0.016264 | 0.016264 | 0 | 0 | 0.011268 | 0.011268 | -2.1604e-05 | 3.684e-05 | -9.1816e-05 | 0.00010769 | 106.7726 | -73.2274 | 0.008371 | 0.010101 | 3.5319 | -2.1133
Line5_6_7 | 0.016264 | 0.016264 | 0 | 0 | 0.011268 | 0.011268 | -3.6839e-05 | 5.2075e-05 | -0.00010769 | 0.00012356 | 106.7726 | -73.2274 | 0.010101 | 0.0119 | -2.1133 | -6.0813
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0119 | 0.0119 | -6.0813 | -6.0813
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0119 | 0.0119 | -6.0813 | -6.0813
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0119 | 0.0119 | -6.0813 | -6.0813
Line9_3_11 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -2.161e-05 | 3.674e-05 | -9.1428e-05 | 0.00010719 | 106.8745 | -73.1255 | 0.0083669 | 0.010091 | 3.576 | -2.045

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.016264 | 0.016264 | 0 | 0 | 0.011268 | 0.011268 | -6.3685e-06 | 2.1604e-05 | -7.5945e-05 | 9.1816e-05 | 106.7727 | -73.2273 | 0.0067637 | 0.008371 | 11.9792 | 3.5319
Line10_11_12 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -3.6739e-05 | 5.1869e-05 | -0.00010719 | 0.00012295 | 106.8745 | -73.1255 | 0.010091 | 0.011884 | -2.045 | -5.9993
Line11_12_13 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -5.1869e-05 | 6.6998e-05 | -0.00012295 | 0.00013871 | 106.8744 | -73.1256 | 0.011884 | 0.013719 | -5.9993 | -8.9069
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013719 | 0.013719 | -8.9069 | -8.9069
Line13_13_14 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -6.6997e-05 | 8.2127e-05 | -0.00013871 | 0.00015447 | 106.8742 | -73.1258 | 0.013719 | 0.01558 | -8.9069 | -11.1243
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013719 | 0.013719 | -8.9069 | -8.9069
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013719 | 0.013719 | -8.9069 | -8.9068
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083751 | 0.0083751 | 3.4873 | 3.4873
Line17_5_19 | 0.016292 | 0.016292 | 0 | 0 | 0.011288 | 0.011288 | -2.16e-05 | 3.6889e-05 | -9.201e-05 | 0.00010794 | 106.7212 | -73.2788 | 0.0083731 | 0.010105 | 3.5096 | -2.1477
Line1_1_3 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -6.4809e-06 | 2.161e-05 | -7.5669e-05 | 9.1428e-05 | 106.8746 | -73.1254 | 0.0067637 | 0.0083669 | 11.9792 | 3.576
Line2_1_4 | 0.016321 | 0.016321 | 0 | 0 | 0.011307 | 0.011307 | -6.2542e-06 | 2.1597e-05 | -7.6223e-05 | 9.2205e-05 | 106.6699 | -73.3301 | 0.0067637 | 0.0083751 | 11.9792 | 3.4873
Line3_1_5 | 0.016292 | 0.016292 | 0 | 0 | 0.011288 | 0.011288 | -6.3114e-06 | 2.1601e-05 | -7.6084e-05 | 9.201e-05 | 106.7213 | -73.2787 | 0.0067637 | 0.0083731 | 11.9792 | 3.5096
Line4_2_6 | 0.016264 | 0.016264 | 0 | 0 | 0.011268 | 0.011268 | -2.1604e-05 | 3.684e-05 | -9.1816e-05 | 0.00010769 | 106.7726 | -73.2274 | 0.008371 | 0.010101 | 3.5319 | -2.1133
Line5_6_7 | 0.016264 | 0.016264 | 0 | 0 | 0.011268 | 0.011268 | -3.6839e-05 | 5.2075e-05 | -0.00010769 | 0.00012356 | 106.7726 | -73.2274 | 0.010101 | 0.0119 | -2.1133 | -6.0813
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0119 | 0.0119 | -6.0813 | -6.0813
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0119 | 0.0119 | -6.0813 | -6.0813
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0119 | 0.0119 | -6.0813 | -6.0813
Line9_3_11 | 0.016207 | 0.016207 | 0 | 0 | 0.011228 | 0.011228 | -2.161e-05 | 3.674e-05 | -9.1428e-05 | 0.00010719 | 106.8745 | -73.1255 | 0.0083669 | 0.010091 | 3.576 | -2.045

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.00028359 | 0.00028359 | 0 | 0 | 0.00019648 | 0.00019648 | -0.0001608 | 0.0001608 | -0.00010823 | 0.00010823 | 145.4288 | -34.5712 | 0.98652 | 0.98655 | -0.62731 | -0.62689
Line10_11_12 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016044 | 0.00016044 | -0.00010758 | 0.00010758 | 145.5306 | -34.4694 | 0.98658 | 0.98662 | -0.62647 | -0.62605
Line11_12_13 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016044 | 0.00016044 | -0.00010758 | 0.00010759 | 145.5306 | -34.4694 | 0.98662 | 0.98665 | -0.62605 | -0.62563
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98665 | 0.98665 | -0.62563 | -0.62563
Line13_13_14 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016044 | 0.00016045 | -0.00010759 | 0.00010759 | 145.5303 | -34.4697 | 0.98665 | 0.98668 | -0.62563 | -0.62521
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98665 | 0.98665 | -0.62563 | -0.62563
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98665 | 0.98665 | -0.62563 | -0.62563
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98655 | 0.98655 | -0.62689 | -0.62689
Line17_5_19 | 0.00028409 | 0.00028409 | 0 | 0 | 0.00019682 | 0.00019682 | -0.00016099 | 0.00016099 | -0.00010857 | 0.00010857 | 145.3774 | -34.6226 | 0.98655 | 0.98658 | -0.62689 | -0.62647
Line1_1_3 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016043 | 0.00016043 | -0.00010757 | 0.00010757 | 145.5307 | -34.4693 | 0.98652 | 0.98655 | -0.62731 | -0.62689
Line2_1_4 | 0.00028459 | 0.00028459 | 0 | 0 | 0.00019717 | 0.00019717 | -0.00016117 | 0.00016117 | -0.0001089 | 0.0001089 | 145.3261 | -34.6739 | 0.98652 | 0.98655 | -0.62731 | -0.62689
Line3_1_5 | 0.00028409 | 0.00028409 | 0 | 0 | 0.00019682 | 0.00019682 | -0.00016098 | 0.00016099 | -0.00010856 | 0.00010857 | 145.3774 | -34.6226 | 0.98652 | 0.98655 | -0.62731 | -0.62689
Line4_2_6 | 0.00028359 | 0.00028359 | 0 | 0 | 0.00019648 | 0.00019648 | -0.0001608 | 0.00016081 | -0.00010823 | 0.00010824 | 145.4287 | -34.5713 | 0.98655 | 0.98658 | -0.62689 | -0.62647
Line5_6_7 | 0.00028359 | 0.00028359 | 0 | 0 | 0.00019648 | 0.00019648 | -0.00016081 | 0.00016081 | -0.00010824 | 0.00010824 | 145.4287 | -34.5713 | 0.98658 | 0.98662 | -0.62647 | -0.62605
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98662 | 0.98662 | -0.62605 | -0.62605
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98662 | 0.98662 | -0.62605 | -0.62605
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98662 | 0.98662 | -0.62605 | -0.62605
Line9_3_11 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016043 | 0.00016044 | -0.00010757 | 0.00010758 | 145.5307 | -34.4693 | 0.98655 | 0.98658 | -0.62689 | -0.62647

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.00028359 | 0.00028359 | 0 | 0 | 0.00019648 | 0.00019648 | -0.0001608 | 0.0001608 | -0.00010823 | 0.00010823 | 145.4288 | -34.5712 | 0.98652 | 0.98655 | -0.62731 | -0.62689
Line10_11_12 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016044 | 0.00016044 | -0.00010758 | 0.00010758 | 145.5306 | -34.4694 | 0.98658 | 0.98662 | -0.62647 | -0.62605
Line11_12_13 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016044 | 0.00016044 | -0.00010758 | 0.00010759 | 145.5306 | -34.4694 | 0.98662 | 0.98665 | -0.62605 | -0.62563
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98665 | 0.98665 | -0.62563 | -0.62563
Line13_13_14 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016044 | 0.00016045 | -0.00010759 | 0.00010759 | 145.5303 | -34.4697 | 0.98665 | 0.98668 | -0.62563 | -0.62521
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98665 | 0.98665 | -0.62563 | -0.62563
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98665 | 0.98665 | -0.62563 | -0.62563
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98655 | 0.98655 | -0.62689 | -0.62689
Line17_5_19 | 0.00028409 | 0.00028409 | 0 | 0 | 0.00019682 | 0.00019682 | -0.00016099 | 0.00016099 | -0.00010857 | 0.00010857 | 145.3774 | -34.6226 | 0.98655 | 0.98658 | -0.62689 | -0.62647
Line1_1_3 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016043 | 0.00016043 | -0.00010757 | 0.00010757 | 145.5307 | -34.4693 | 0.98652 | 0.98655 | -0.62731 | -0.62689
Line2_1_4 | 0.00028459 | 0.00028459 | 0 | 0 | 0.00019717 | 0.00019717 | -0.00016117 | 0.00016117 | -0.0001089 | 0.0001089 | 145.3261 | -34.6739 | 0.98652 | 0.98655 | -0.62731 | -0.62689
Line3_1_5 | 0.00028409 | 0.00028409 | 0 | 0 | 0.00019682 | 0.00019682 | -0.00016098 | 0.00016099 | -0.00010856 | 0.00010857 | 145.3774 | -34.6226 | 0.98652 | 0.98655 | -0.62731 | -0.62689
Line4_2_6 | 0.00028359 | 0.00028359 | 0 | 0 | 0.00019648 | 0.00019648 | -0.0001608 | 0.00016081 | -0.00010823 | 0.00010824 | 145.4287 | -34.5713 | 0.98655 | 0.98658 | -0.62689 | -0.62647
Line5_6_7 | 0.00028359 | 0.00028359 | 0 | 0 | 0.00019648 | 0.00019648 | -0.00016081 | 0.00016081 | -0.00010824 | 0.00010824 | 145.4287 | -34.5713 | 0.98658 | 0.98662 | -0.62647 | -0.62605
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98662 | 0.98662 | -0.62605 | -0.62605
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98662 | 0.98662 | -0.62605 | -0.62605
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98662 | 0.98662 | -0.62605 | -0.62605
Line9_3_11 | 0.0002826 | 0.0002826 | 0 | 0 | 0.00019579 | 0.00019579 | -0.00016043 | 0.00016044 | -0.00010757 | 0.00010758 | 145.5307 | -34.4693 | 0.98655 | 0.98658 | -0.62689 | -0.62647

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.14042 | 0.58778 | 0.543 | 0.14042 | 0.58778 | 0.543 | 0.032428 | 0.13574 | 0.1254 | 0.032428 | 0.13574 | 0.1254 | -0.017045 | -0.077532 | 0.063715 | 0.017243 | 0.080987 | -0.060766 | -0.033318 | -0.0286 | -0.047355 | 0.033712 | 0.035509 | 0.053252 | 118.2725 | 3.0454 | -163.4262 | -61.7275 | -176.9546 | 16.5738 | 1.1541 | 0.60879 | 0.63305 | 1.1677 | 0.65145 | 0.64431 | 1.1783 | -156.7069 | 159.953 | 1.1845 | -153.2792 | 155.3446
Line10_11_12 | 0.11899 | 0.52296 | 0.49065 | 0.11899 | 0.52296 | 0.49065 | 0.02748 | 0.12077 | 0.11331 | 0.02748 | 0.12077 | 0.11331 | -0.013896 | -0.075055 | 0.052109 | 0.014038 | 0.07779 | -0.049702 | -0.029212 | -0.034686 | -0.053276 | 0.029495 | 0.040156 | 0.05809 | 116.5967 | 4.4508 | -162.5679 | -63.4033 | -175.5492 | 17.4321 | 1.1771 | 0.68461 | 0.65769 | 1.1887 | 0.72485 | 0.67471 | 1.1558 | -150.7457 | 151.798 | 1.145 | -148.2462 | 147.9823
Line11_12_13 | 0.11899 | 0.52296 | 0.49065 | 0.11899 | 0.52296 | 0.49065 | 0.02748 | 0.12077 | 0.11331 | 0.02748 | 0.12077 | 0.11331 | -0.014038 | -0.07779 | 0.049702 | 0.014179 | 0.080525 | -0.047295 | -0.029495 | -0.040156 | -0.05809 | 0.029778 | 0.045625 | 0.062905 | 116.5967 | 4.4508 | -162.5679 | -63.4033 | -175.5492 | 17.4321 | 1.1887 | 0.72485 | 0.67471 | 1.2002 | 0.76633 | 0.69456 | 1.145 | -148.2462 | 147.9823 | 1.1343 | -146.0133 | 144.3695
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3255e-09 | -1.8733e-09 | -2.3488e-09 | -1.3255e-09 | 1.8733e-09 | 2.3488e-09 | -2.8747e-10 | 4.0668e-09 | -3.4677e-09 | 2.8747e-10 | -4.0668e-09 | 3.4677e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2002 | 0.76633 | 0.69456 | 1.2002 | 0.76633 | 0.69456 | 1.1343 | -146.0133 | 144.3695 | 1.1343 | -146.0133 | 144.3695
Line13_13_14 | 0.11899 | 0.52296 | 0.49065 | 0.11899 | 0.52296 | 0.49065 | 0.02748 | 0.12077 | 0.11331 | 0.02748 | 0.12077 | 0.11331 | -0.014179 | -0.080525 | 0.047295 | 0.014321 | 0.08326 | -0.044887 | -0.029778 | -0.045625 | -0.062905 | 0.030061 | 0.051095 | 0.06772 | 116.5967 | 4.4508 | -162.568 | -63.4033 | -175.5492 | 17.432 | 1.2002 | 0.76633 | 0.69456 | 1.2117 | 0.80885 | 0.71702 | 1.1343 | -146.0133 | 144.3695 | 1.1238 | -144.0124 | 140.9701
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8367e-10 | -1.2489e-09 | -1.5659e-09 | -8.8367e-10 | 1.2489e-09 | 1.5659e-09 | -1.9165e-10 | 2.7112e-09 | -2.3118e-09 | 1.9165e-10 | -2.7112e-09 | 2.3118e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2002 | 0.76633 | 0.69456 | 1.2002 | 0.76633 | 0.69456 | 1.1343 | -146.0133 | 144.3695 | 1.1343 | -146.0133 | 144.3695
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4183e-10 | -6.2444e-10 | -7.8294e-10 | -4.4183e-10 | 6.2444e-10 | 7.8294e-10 | -9.5824e-11 | 1.3556e-09 | -1.1559e-09 | 9.5824e-11 | -1.3556e-09 | 1.1559e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2002 | 0.76633 | 0.69456 | 1.2002 | 0.76633 | 0.69456 | 1.1343 | -146.0133 | 144.3695 | 1.1343 | -146.0133 | 144.3695
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0405e-10 | -6.3778e-10 | -6.1127e-10 | -3.0405e-10 | 6.3778e-10 | 6.1127e-10 | -9.9413e-11 | 1.4461e-09 | -1.484e-09 | 9.9413e-11 | -1.4461e-09 | 1.484e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1706 | 0.65882 | 0.64492 | 1.1706 | 0.65882 | 0.64492 | 1.2065 | -152.9716 | 154.7858 | 1.2065 | -152.9716 | 154.7858
Line17_5_19 | 0.15407 | 0.62628 | 0.57347 | 0.15407 | 0.62628 | 0.57347 | 0.035581 | 0.14463 | 0.13244 | 0.035581 | 0.14463 | 0.13244 | -0.019433 | -0.086084 | 0.064421 | 0.019671 | 0.090006 | -0.061132 | -0.036777 | -0.039506 | -0.056019 | 0.037251 | 0.04735 | 0.062596 | 119.0473 | 2.2187 | -163.9097 | -60.9527 | -177.7813 | 16.0903 | 1.169 | 0.65487 | 0.64461 | 1.1839 | 0.70317 | 0.66066 | 1.1949 | -153.1298 | 155.0805 | 1.2111 | -150.0333 | 150.4121
Line1_1_3 | 0.11899 | 0.52296 | 0.49065 | 0.11899 | 0.52296 | 0.49065 | 0.02748 | 0.12077 | 0.11331 | 0.02748 | 0.12077 | 0.11331 | -0.013613 | -0.069585 | 0.056924 | 0.013755 | 0.07232 | -0.054517 | -0.028645 | -0.023746 | -0.043646 | 0.028928 | 0.029216 | 0.048461 | 116.5967 | 4.4508 | -162.5679 | -63.4033 | -175.5492 | 17.4321 | 1.1541 | 0.60879 | 0.63305 | 1.1656 | 0.64583 | 0.64374 | 1.1783 | -156.7069 | 159.953 | 1.167 | -153.5514 | 155.7975
Line2_1_4 | 0.17037 | 0.66986 | 0.60744 | 0.17037 | 0.66986 | 0.60744 | 0.039346 | 0.1547 | 0.14028 | 0.039346 | 0.1547 | 0.14028 | -0.021714 | -0.087319 | 0.072197 | 0.022005 | 0.091806 | -0.068507 | -0.039881 | -0.035285 | -0.051712 | 0.040461 | 0.044259 | 0.059092 | 119.7457 | 1.2899 | -164.4344 | -60.2543 | -178.7101 | 15.5656 | 1.1541 | 0.60879 | 0.63305 | 1.1706 | 0.65882 | 0.64492 | 1.1783 | -156.7069 | 159.953 | 1.2065 | -152.9716 | 154.7858
Line3_1_5 | 0.15407 | 0.62628 | 0.57347 | 0.15407 | 0.62628 | 0.57347 | 0.035581 | 0.14463 | 0.13244 | 0.035581 | 0.14463 | 0.13244 | -0.019196 | -0.082162 | 0.067709 | 0.019433 | 0.086084 | -0.064421 | -0.036302 | -0.031661 | -0.049442 | 0.036777 | 0.039506 | 0.056019 | 119.0473 | 2.2187 | -163.9097 | -60.9527 | -177.7813 | 16.0903 | 1.1541 | 0.60879 | 0.63305 | 1.169 | 0.65487 | 0.64461 | 1.1783 | -156.7069 | 159.953 | 1.1949 | -153.1298 | 155.0805
Line4_2_6 | 0.14042 | 0.58778 | 0.543 | 0.14042 | 0.58778 | 0.543 | 0.032428 | 0.13574 | 0.1254 | 0.032428 | 0.13574 | 0.1254 | -0.017243 | -0.080987 | 0.060766 | 0.01744 | 0.084442 | -0.057818 | -0.033712 | -0.035509 | -0.053252 | 0.034106 | 0.042419 | 0.059149 | 118.2725 | 3.0454 | -163.4262 | -61.7275 | -176.9546 | 16.5738 | 1.1677 | 0.65145 | 0.64431 | 1.1813 | 0.69615 | 0.65959 | 1.1845 | -153.2792 | 155.3446 | 1.1905 | -150.282 | 150.9219
Line5_6_7 | 0.14042 | 0.58778 | 0.543 | 0.14042 | 0.58778 | 0.543 | 0.032428 | 0.13574 | 0.1254 | 0.032428 | 0.13574 | 0.1254 | -0.01744 | -0.084442 | 0.057818 | 0.017637 | 0.087897 | -0.054869 | -0.034106 | -0.042419 | -0.059149 | 0.034501 | 0.049329 | 0.065046 | 118.2725 | 3.0454 | -163.4262 | -61.7275 | -176.9546 | 16.5738 | 1.1813 | 0.69615 | 0.65959 | 1.1949 | 0.74253 | 0.6786 | 1.1905 | -150.282 | 150.9219 | 1.1964 | -147.6528 | 146.7231
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2504e-09 | -1.8935e-09 | -2.2686e-09 | -1.2504e-09 | 1.8935e-09 | 2.2686e-09 | -3.0187e-10 | 4.1699e-09 | -3.6924e-09 | 3.0187e-10 | -4.1699e-09 | 3.6924e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1949 | 0.74253 | 0.6786 | 1.1949 | 0.74253 | 0.6786 | 1.1964 | -147.6528 | 146.7231 | 1.1964 | -147.6528 | 146.7231
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1681e-10 | -6.3117e-10 | -7.5618e-10 | -4.1681e-10 | 6.3117e-10 | 7.5618e-10 | -1.0062e-10 | 1.39e-09 | -1.2308e-09 | 1.0062e-10 | -1.39e-09 | 1.2308e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1949 | 0.74253 | 0.6786 | 1.1949 | 0.74253 | 0.6786 | 1.1964 | -147.6528 | 146.7231 | 1.1964 | -147.6528 | 146.7231
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1681e-10 | -6.3117e-10 | -7.5618e-10 | -4.1681e-10 | 6.3117e-10 | 7.5618e-10 | -1.0062e-10 | 1.39e-09 | -1.2308e-09 | 1.0062e-10 | -1.39e-09 | 1.2308e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1949 | 0.74253 | 0.6786 | 1.1949 | 0.74253 | 0.6786 | 1.1964 | -147.6528 | 146.7231 | 1.1964 | -147.6528 | 146.7231
Line9_3_11 | 0.11899 | 0.52296 | 0.49065 | 0.11899 | 0.52296 | 0.49065 | 0.02748 | 0.12077 | 0.11331 | 0.02748 | 0.12077 | 0.11331 | -0.013755 | -0.07232 | 0.054517 | 0.013896 | 0.075055 | -0.052109 | -0.028928 | -0.029216 | -0.048461 | 0.029212 | 0.034686 | 0.053276 | 116.5967 | 4.4508 | -162.5679 | -63.4033 | -175.5492 | 17.4321 | 1.1656 | 0.64583 | 0.64374 | 1.1771 | 0.68461 | 0.65769 | 1.167 | -153.5514 | 155.7975 | 1.1558 | -150.7457 | 151.798

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.14011 | 0.56954 | 0.52635 | 0.14011 | 0.56954 | 0.52635 | 0.032357 | 0.13153 | 0.12156 | 0.032357 | 0.13153 | 0.12156 | -0.016601 | -0.075173 | 0.061694 | 0.016797 | 0.078417 | -0.058923 | -0.033545 | -0.028575 | -0.046426 | 0.033938 | 0.035063 | 0.051967 | 117.5177 | 2.7103 | -163.307 | -62.4823 | -177.2897 | 16.693 | 1.1567 | 0.61143 | 0.63519 | 1.1703 | 0.65308 | 0.64633 | 1.188 | -156.4767 | 159.7305 | 1.1853 | -153.1988 | 155.2824
Line10_11_12 | 0.11962 | 0.50882 | 0.47736 | 0.11962 | 0.50882 | 0.47736 | 0.027625 | 0.11751 | 0.11024 | 0.027625 | 0.11751 | 0.11024 | -0.01366 | -0.072922 | 0.050787 | 0.013803 | 0.075511 | -0.048508 | -0.029593 | -0.034291 | -0.052016 | 0.029879 | 0.039469 | 0.056574 | 115.9297 | 4.0646 | -162.4879 | -64.0703 | -175.9354 | 17.5121 | 1.1799 | 0.68576 | 0.65944 | 1.1915 | 0.72509 | 0.67599 | 1.1522 | -150.7509 | 151.827 | 1.1348 | -148.34 | 148.1229
Line11_12_13 | 0.11962 | 0.50882 | 0.47736 | 0.11962 | 0.50882 | 0.47736 | 0.027625 | 0.11751 | 0.11024 | 0.027625 | 0.11751 | 0.11024 | -0.013803 | -0.075511 | 0.048508 | 0.013946 | 0.0781 | -0.046229 | -0.029879 | -0.039469 | -0.056574 | 0.030165 | 0.044647 | 0.061131 | 115.9297 | 4.0645 | -162.4879 | -64.0703 | -175.9355 | 17.5121 | 1.1915 | 0.72509 | 0.67599 | 1.203 | 0.76557 | 0.69522 | 1.1348 | -148.34 | 148.1229 | 1.1178 | -146.1806 | 144.6098
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3662e-09 | -1.8659e-09 | -2.3314e-09 | -1.3662e-09 | 1.8659e-09 | 2.3314e-09 | -2.8397e-10 | 4.0871e-09 | -3.5031e-09 | 2.8397e-10 | -4.0871e-09 | 3.5031e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.203 | 0.76557 | 0.69522 | 1.203 | 0.76557 | 0.69522 | 1.1178 | -146.1806 | 144.6098 | 1.1178 | -146.1806 | 144.6098
Line13_13_14 | 0.11962 | 0.50882 | 0.47736 | 0.11962 | 0.50882 | 0.47736 | 0.027625 | 0.11751 | 0.11024 | 0.027625 | 0.11751 | 0.11024 | -0.013946 | -0.0781 | 0.046229 | 0.014089 | 0.080689 | -0.04395 | -0.030165 | -0.044647 | -0.061131 | 0.030452 | 0.049825 | 0.065689 | 115.9297 | 4.0645 | -162.4879 | -64.0703 | -175.9355 | 17.5121 | 1.203 | 0.76557 | 0.69522 | 1.2146 | 0.80703 | 0.71693 | 1.1178 | -146.1806 | 144.6098 | 1.1011 | -144.2406 | 141.2975
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1079e-10 | -1.244e-09 | -1.5543e-09 | -9.1079e-10 | 1.244e-09 | 1.5543e-09 | -1.8931e-10 | 2.7247e-09 | -2.3354e-09 | 1.8931e-10 | -2.7247e-09 | 2.3354e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.203 | 0.76557 | 0.69522 | 1.203 | 0.76557 | 0.69522 | 1.1178 | -146.1806 | 144.6098 | 1.1178 | -146.1806 | 144.6098
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.554e-10 | -6.2198e-10 | -7.7713e-10 | -4.554e-10 | 6.2198e-10 | 7.7713e-10 | -9.4655e-11 | 1.3624e-09 | -1.1677e-09 | 9.4655e-11 | -1.3624e-09 | 1.1677e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.203 | 0.76557 | 0.69522 | 1.203 | 0.76557 | 0.69522 | 1.1178 | -146.1806 | 144.6098 | 1.1178 | -146.1806 | 144.6098
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1512e-10 | -6.3754e-10 | -6.0894e-10 | -3.1512e-10 | 6.3754e-10 | 6.0893e-10 | -9.9442e-11 | 1.4464e-09 | -1.4879e-09 | 9.9442e-11 | -1.4464e-09 | 1.4879e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.173 | 0.65993 | 0.64693 | 1.173 | 0.65993 | 0.64693 | 1.2043 | -152.917 | 154.7658 | 1.2043 | -152.917 | 154.7658
Line17_5_19 | 0.15304 | 0.60537 | 0.5547 | 0.15304 | 0.60537 | 0.5547 | 0.035343 | 0.1398 | 0.1281 | 0.035343 | 0.1398 | 0.1281 | -0.018839 | -0.083141 | 0.062329 | 0.019073 | 0.086805 | -0.059252 | -0.036873 | -0.038804 | -0.054558 | 0.037341 | 0.046133 | 0.060712 | 118.2574 | 1.9186 | -163.766 | -61.7426 | -178.0814 | 16.234 | 1.1715 | 0.65627 | 0.64663 | 1.1864 | 0.70314 | 0.66224 | 1.1944 | -153.0618 | 155.0377 | 1.2006 | -150.0927 | 150.537
Line1_1_3 | 0.11962 | 0.50882 | 0.47736 | 0.11962 | 0.50882 | 0.47736 | 0.027625 | 0.11751 | 0.11024 | 0.027625 | 0.11751 | 0.11024 | -0.013374 | -0.067744 | 0.055344 | 0.013517 | 0.070333 | -0.053066 | -0.029021 | -0.023935 | -0.042901 | 0.029307 | 0.029113 | 0.047459 | 115.9297 | 4.0646 | -162.4879 | -64.0703 | -175.9354 | 17.5121 | 1.1567 | 0.61143 | 0.63519 | 1.1683 | 0.64779 | 0.64577 | 1.188 | -156.4767 | 159.7305 | 1.1699 | -153.4496 | 155.7046
Line2_1_4 | 0.16836 | 0.64574 | 0.58617 | 0.16836 | 0.64574 | 0.58617 | 0.03888 | 0.14913 | 0.13537 | 0.03888 | 0.14913 | 0.13537 | -0.020936 | -0.084247 | 0.069557 | 0.021219 | 0.088417 | -0.066121 | -0.039804 | -0.034879 | -0.05055 | 0.040371 | 0.043218 | 0.057422 | 118.9311 | 1.0335 | -164.2618 | -61.0689 | -178.9665 | 15.7382 | 1.1567 | 0.61143 | 0.63519 | 1.173 | 0.65993 | 0.64693 | 1.188 | -156.4767 | 159.7305 | 1.2043 | -152.917 | 154.7658
Line3_1_5 | 0.15304 | 0.60537 | 0.5547 | 0.15304 | 0.60537 | 0.5547 | 0.035343 | 0.1398 | 0.1281 | 0.035343 | 0.1398 | 0.1281 | -0.018604 | -0.079476 | 0.065406 | 0.018839 | 0.083141 | -0.062329 | -0.036404 | -0.031474 | -0.048404 | 0.036873 | 0.038804 | 0.054558 | 118.2574 | 1.9186 | -163.766 | -61.7426 | -178.0814 | 16.234 | 1.1567 | 0.61143 | 0.63519 | 1.1715 | 0.65627 | 0.64663 | 1.188 | -156.4767 | 159.7305 | 1.1944 | -153.0618 | 155.0377
Line4_2_6 | 0.14011 | 0.56954 | 0.52635 | 0.14011 | 0.56954 | 0.52635 | 0.032357 | 0.13153 | 0.12156 | 0.032357 | 0.13153 | 0.12156 | -0.016797 | -0.078417 | 0.058923 | 0.016993 | 0.081661 | -0.056153 | -0.033938 | -0.035063 | -0.051967 | 0.03433 | 0.04155 | 0.057508 | 117.5177 | 2.7103 | -163.3071 | -62.4823 | -177.2897 | 16.6929 | 1.1703 | 0.65308 | 0.64633 | 1.1839 | 0.6966 | 0.66123 | 1.1853 | -153.1988 | 155.2824 | 1.1826 | -150.3221 | 151.0098
Line5_6_7 | 0.14011 | 0.56954 | 0.52635 | 0.14011 | 0.56954 | 0.52635 | 0.032357 | 0.13153 | 0.12156 | 0.032357 | 0.13153 | 0.12156 | -0.016993 | -0.081661 | 0.056153 | 0.01719 | 0.084905 | -0.053382 | -0.03433 | -0.04155 | -0.057508 | 0.034723 | 0.048038 | 0.063049 | 117.5177 | 2.7103 | -163.3071 | -62.4823 | -177.2897 | 16.6929 | 1.1839 | 0.6966 | 0.66123 | 1.1974 | 0.74168 | 0.67963 | 1.1826 | -150.3221 | 151.0098 | 1.18 | -147.7892 | 146.9469
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2863e-09 | -1.8884e-09 | -2.2498e-09 | -1.2863e-09 | 1.8884e-09 | 2.2498e-09 | -2.9837e-10 | 4.184e-09 | -3.7266e-09 | 2.9837e-10 | -4.184e-09 | 3.7266e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1974 | 0.74168 | 0.67963 | 1.1974 | 0.74168 | 0.67963 | 1.18 | -147.7892 | 146.9469 | 1.18 | -147.7892 | 146.9469
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2876e-10 | -6.2945e-10 | -7.4994e-10 | -4.2876e-10 | 6.2945e-10 | 7.4993e-10 | -9.9457e-11 | 1.3947e-09 | -1.2422e-09 | 9.9457e-11 | -1.3947e-09 | 1.2422e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1974 | 0.74168 | 0.67963 | 1.1974 | 0.74168 | 0.67963 | 1.18 | -147.7892 | 146.9469 | 1.18 | -147.7892 | 146.9469
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2876e-10 | -6.2945e-10 | -7.4993e-10 | -4.2876e-10 | 6.2945e-10 | 7.4993e-10 | -9.9457e-11 | 1.3947e-09 | -1.2422e-09 | 9.9457e-11 | -1.3947e-09 | 1.2422e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1974 | 0.74168 | 0.67963 | 1.1974 | 0.74168 | 0.67963 | 1.18 | -147.7892 | 146.9469 | 1.18 | -147.7892 | 146.9469
Line9_3_11 | 0.11962 | 0.50882 | 0.47736 | 0.11962 | 0.50882 | 0.47736 | 0.027625 | 0.11751 | 0.11024 | 0.027625 | 0.11751 | 0.11024 | -0.013517 | -0.070333 | 0.053066 | 0.01366 | 0.072922 | -0.050787 | -0.029307 | -0.029113 | -0.047459 | 0.029593 | 0.034291 | 0.052016 | 115.9297 | 4.0646 | -162.4879 | -64.0703 | -175.9354 | 17.5121 | 1.1683 | 0.64779 | 0.64577 | 1.1799 | 0.68576 | 0.65944 | 1.1699 | -153.4496 | 155.7046 | 1.1522 | -150.7509 | 151.827

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1118 | 0.11793 | 0.12532 | 0.1118 | 0.11793 | 0.12532 | 0.025819 | 0.027235 | 0.028941 | 0.025819 | 0.027235 | 0.028941 | -0.0032973 | -0.0072571 | -0.0040997 | 0.0034223 | 0.0073962 | 0.0042567 | -0.029409 | -0.030124 | -0.032242 | 0.029659 | 0.030402 | 0.032556 | 96.469 | -17.4769 | -142.8542 | -83.531 | 162.5231 | 37.1458 | 1.1461 | 1.1377 | 1.123 | 1.1563 | 1.1488 | 1.1345 | 0.071775 | -121.0218 | 119.8993 | -0.11316 | -121.1501 | 119.6966
Line10_11_12 | 0.099658 | 0.10473 | 0.11182 | 0.099658 | 0.10473 | 0.11182 | 0.023015 | 0.024187 | 0.025825 | 0.023015 | 0.024187 | 0.025825 | -0.0029792 | -0.0066102 | -0.0038791 | 0.0030785 | 0.0067199 | 0.0040041 | -0.026629 | -0.027204 | -0.029274 | 0.026827 | 0.027424 | 0.029524 | 96.1225 | -17.5927 | -142.9125 | -83.8775 | 162.4073 | 37.0875 | 1.1642 | 1.1575 | 1.1435 | 1.1733 | 1.1674 | 1.1537 | -0.26106 | -121.25 | 119.5393 | -0.42362 | -121.3611 | 119.3641
Line11_12_13 | 0.099658 | 0.10473 | 0.11182 | 0.099658 | 0.10473 | 0.11182 | 0.023015 | 0.024187 | 0.025825 | 0.023015 | 0.024187 | 0.025825 | -0.0030785 | -0.0067199 | -0.0040041 | 0.0031778 | 0.0068295 | 0.0041292 | -0.026827 | -0.027424 | -0.029524 | 0.027026 | 0.027643 | 0.029775 | 96.1225 | -17.5927 | -142.9125 | -83.8775 | 162.4073 | 37.0875 | 1.1733 | 1.1674 | 1.1537 | 1.1824 | 1.1773 | 1.164 | -0.42362 | -121.3611 | 119.3641 | -0.58369 | -121.4705 | 119.192
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0721e-09 | 1.0051e-09 | 8.205e-10 | -1.0721e-09 | -1.0051e-09 | -8.205e-10 | 1.4574e-10 | 3.6554e-10 | 1.9862e-10 | -1.4574e-10 | -3.6554e-10 | -1.9862e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1824 | 1.1773 | 1.164 | 1.1824 | 1.1773 | 1.164 | -0.58369 | -121.4705 | 119.192 | -0.58369 | -121.4705 | 119.192
Line13_13_14 | 0.099658 | 0.10473 | 0.11182 | 0.099658 | 0.10473 | 0.11182 | 0.023015 | 0.024187 | 0.025825 | 0.023015 | 0.024187 | 0.025825 | -0.0031778 | -0.0068295 | -0.0041292 | 0.0032771 | 0.0069392 | 0.0042542 | -0.027026 | -0.027643 | -0.029775 | 0.027225 | 0.027862 | 0.030025 | 96.1225 | -17.5927 | -142.9125 | -83.8775 | 162.4073 | 37.0875 | 1.1824 | 1.1773 | 1.164 | 1.1915 | 1.1872 | 1.1742 | -0.58369 | -121.4705 | 119.192 | -0.74132 | -121.5779 | 119.0228
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1472e-10 | 6.701e-10 | 5.47e-10 | -7.1472e-10 | -6.701e-10 | -5.47e-10 | 9.7163e-11 | 2.4369e-10 | 1.3241e-10 | -9.7163e-11 | -2.4369e-10 | -1.3241e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1824 | 1.1773 | 1.164 | 1.1824 | 1.1773 | 1.164 | -0.58369 | -121.4705 | 119.192 | -0.58369 | -121.4705 | 119.192
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5736e-10 | 3.3505e-10 | 2.735e-10 | -3.5736e-10 | -3.3505e-10 | -2.735e-10 | 4.8581e-11 | 1.2185e-10 | 6.6206e-11 | -4.8581e-11 | -1.2185e-10 | -6.6206e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1824 | 1.1773 | 1.164 | 1.1824 | 1.1773 | 1.164 | -0.58369 | -121.4705 | 119.192 | -0.58369 | -121.4705 | 119.192
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.452e-10 | 2.1379e-10 | 1.503e-10 | -2.452e-10 | -2.1379e-10 | -1.503e-10 | 1.0935e-11 | 9.449e-11 | 2.6374e-11 | -1.0935e-11 | -9.449e-11 | -2.6374e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1578 | 1.1505 | 1.1361 | 1.1578 | 1.1505 | 1.1361 | -0.13418 | -121.1668 | 119.6702 | -0.13418 | -121.1668 | 119.6702
Line17_5_19 | 0.11906 | 0.12584 | 0.13335 | 0.11906 | 0.12584 | 0.13335 | 0.027496 | 0.029062 | 0.030795 | 0.027496 | 0.029062 | 0.030795 | -0.0037657 | -0.0079386 | -0.0045643 | 0.0039075 | 0.0080969 | 0.0047421 | -0.031588 | -0.032452 | -0.03466 | 0.031872 | 0.032769 | 0.035016 | 96.6752 | -17.412 | -142.8139 | -83.3248 | 162.588 | 37.1861 | 1.157 | 1.1496 | 1.1352 | 1.1678 | 1.1615 | 1.1474 | -0.12312 | -121.1579 | 119.6842 | -0.31439 | -121.2913 | 119.4736
Line1_1_3 | 0.099658 | 0.10473 | 0.11182 | 0.099658 | 0.10473 | 0.11182 | 0.023015 | 0.024187 | 0.025825 | 0.023015 | 0.024187 | 0.025825 | -0.0027805 | -0.0063908 | -0.003629 | 0.0028799 | 0.0065005 | 0.003754 | -0.026232 | -0.026765 | -0.028774 | 0.02643 | 0.026985 | 0.029024 | 96.1225 | -17.5927 | -142.9125 | -83.8775 | 162.4073 | 37.0875 | 1.1461 | 1.1377 | 1.123 | 1.1552 | 1.1476 | 1.1332 | 0.071775 | -121.0218 | 119.8993 | -0.095944 | -121.1369 | 119.7177
Line2_1_4 | 0.12733 | 0.13486 | 0.14246 | 0.12733 | 0.13486 | 0.14246 | 0.029405 | 0.031146 | 0.0329 | 0.029405 | 0.031146 | 0.0329 | -0.004012 | -0.0083805 | -0.0047189 | 0.0041741 | 0.0085624 | 0.0049218 | -0.033463 | -0.03443 | -0.036645 | 0.033787 | 0.034793 | 0.037051 | 96.9085 | -17.3415 | -142.7629 | -83.0915 | 162.6585 | 37.2371 | 1.1461 | 1.1377 | 1.123 | 1.1578 | 1.1505 | 1.1361 | 0.071775 | -121.0218 | 119.8993 | -0.13418 | -121.1668 | 119.6702
Line3_1_5 | 0.11906 | 0.12584 | 0.13335 | 0.11906 | 0.12584 | 0.13335 | 0.027496 | 0.029062 | 0.030795 | 0.027496 | 0.029062 | 0.030795 | -0.003624 | -0.0077802 | -0.0043865 | 0.0037657 | 0.0079386 | 0.0045643 | -0.031305 | -0.032135 | -0.034305 | 0.031588 | 0.032452 | 0.03466 | 96.6752 | -17.412 | -142.8139 | -83.3248 | 162.588 | 37.1861 | 1.1461 | 1.1377 | 1.123 | 1.157 | 1.1496 | 1.1352 | 0.071775 | -121.0218 | 119.8993 | -0.12312 | -121.1579 | 119.6842
Line4_2_6 | 0.1118 | 0.11793 | 0.12532 | 0.1118 | 0.11793 | 0.12532 | 0.025819 | 0.027235 | 0.028941 | 0.025819 | 0.027235 | 0.028941 | -0.0034223 | -0.0073962 | -0.0042567 | 0.0035473 | 0.0075353 | 0.0044137 | -0.029659 | -0.030402 | -0.032556 | 0.029909 | 0.03068 | 0.03287 | 96.469 | -17.4769 | -142.8542 | -83.531 | 162.5231 | 37.1458 | 1.1563 | 1.1488 | 1.1345 | 1.1665 | 1.16 | 1.146 | -0.11316 | -121.1501 | 119.6966 | -0.29486 | -121.2759 | 119.4979
Line5_6_7 | 0.1118 | 0.11793 | 0.12532 | 0.1118 | 0.11793 | 0.12532 | 0.025819 | 0.027235 | 0.028941 | 0.025819 | 0.027235 | 0.028941 | -0.0035473 | -0.0075353 | -0.0044137 | 0.0036723 | 0.0076743 | 0.0045708 | -0.029909 | -0.03068 | -0.03287 | 0.030159 | 0.030958 | 0.033184 | 96.469 | -17.4769 | -142.8542 | -83.531 | 162.5231 | 37.1458 | 1.1665 | 1.16 | 1.146 | 1.1767 | 1.1711 | 1.1574 | -0.29486 | -121.2759 | 119.4979 | -0.47342 | -121.3994 | 119.3032
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9303e-10 | 9.2041e-10 | 7.324e-10 | -9.9303e-10 | -9.2041e-10 | -7.324e-10 | 1.1764e-10 | 3.4607e-10 | 1.7032e-10 | -1.1764e-10 | -3.4607e-10 | -1.7032e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1767 | 1.1711 | 1.1574 | 1.1767 | 1.1711 | 1.1574 | -0.47342 | -121.3994 | 119.3032 | -0.47342 | -121.3994 | 119.3032
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3101e-10 | 3.068e-10 | 2.4413e-10 | -3.3101e-10 | -3.068e-10 | -2.4413e-10 | 3.9214e-11 | 1.1536e-10 | 5.6775e-11 | -3.9214e-11 | -1.1536e-10 | -5.6775e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1767 | 1.1711 | 1.1574 | 1.1767 | 1.1711 | 1.1574 | -0.47342 | -121.3994 | 119.3032 | -0.47342 | -121.3994 | 119.3032
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3101e-10 | 3.0681e-10 | 2.4413e-10 | -3.3101e-10 | -3.068e-10 | -2.4413e-10 | 3.9214e-11 | 1.1536e-10 | 5.6775e-11 | -3.9214e-11 | -1.1536e-10 | -5.6775e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1767 | 1.1711 | 1.1574 | 1.1767 | 1.1711 | 1.1574 | -0.47342 | -121.3994 | 119.3032 | -0.47342 | -121.3994 | 119.3032
Line9_3_11 | 0.099658 | 0.10473 | 0.11182 | 0.099658 | 0.10473 | 0.11182 | 0.023015 | 0.024187 | 0.025825 | 0.023015 | 0.024187 | 0.025825 | -0.0028799 | -0.0065005 | -0.003754 | 0.0029792 | 0.0066102 | 0.0038791 | -0.02643 | -0.026985 | -0.029024 | 0.026629 | 0.027204 | 0.029274 | 96.1225 | -17.5927 | -142.9125 | -83.8775 | 162.4073 | 37.0875 | 1.1552 | 1.1476 | 1.1332 | 1.1642 | 1.1575 | 1.1435 | -0.095944 | -121.1369 | 119.7177 | -0.26106 | -121.25 | 119.5393

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11261 | 0.11849 | 0.12559 | 0.11261 | 0.11849 | 0.12559 | 0.026006 | 0.027364 | 0.029004 | 0.026006 | 0.027364 | 0.029004 | -0.0033122 | -0.0071442 | -0.0040777 | 0.003439 | 0.0072846 | 0.0042354 | -0.029686 | -0.030371 | -0.032389 | 0.02994 | 0.030652 | 0.032704 | 96.4403 | -17.7792 | -142.9227 | -83.5597 | 162.2208 | 37.0773 | 1.1486 | 1.1402 | 1.1255 | 1.1589 | 1.1514 | 1.137 | 0.074002 | -121.0162 | 119.9016 | -0.11213 | -121.1478 | 119.6982
Line10_11_12 | 0.10079 | 0.10569 | 0.11252 | 0.10079 | 0.10569 | 0.11252 | 0.023276 | 0.024407 | 0.025986 | 0.023276 | 0.024407 | 0.025986 | -0.0030128 | -0.0065392 | -0.0038733 | 0.0031144 | 0.0066509 | 0.0039999 | -0.026993 | -0.02755 | -0.029529 | 0.027197 | 0.027773 | 0.029782 | 96.1065 | -17.8986 | -142.9884 | -83.8935 | 162.1014 | 37.0116 | 1.1669 | 1.1601 | 1.1461 | 1.1761 | 1.1701 | 1.1564 | -0.26212 | -121.2512 | 119.5388 | -0.42625 | -121.3657 | 119.3622
Line11_12_13 | 0.10079 | 0.10569 | 0.11252 | 0.10079 | 0.10569 | 0.11252 | 0.023276 | 0.024407 | 0.025986 | 0.023276 | 0.024407 | 0.025986 | -0.0031144 | -0.0066509 | -0.0039999 | 0.003216 | 0.0067626 | 0.0041265 | -0.027197 | -0.027773 | -0.029782 | 0.0274 | 0.027997 | 0.030035 | 96.1065 | -17.8986 | -142.9884 | -83.8935 | 162.1014 | 37.0116 | 1.1761 | 1.1701 | 1.1564 | 1.1853 | 1.1801 | 1.1667 | -0.42625 | -121.3657 | 119.3622 | -0.58785 | -121.4783 | 119.1888
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1122e-09 | 1.044e-09 | 8.5756e-10 | -1.1122e-09 | -1.044e-09 | -8.5756e-10 | 1.4714e-10 | 3.6838e-10 | 1.9988e-10 | -1.4714e-10 | -3.6838e-10 | -1.9988e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1853 | 1.1801 | 1.1667 | 1.1853 | 1.1801 | 1.1667 | -0.58785 | -121.4783 | 119.1888 | -0.58785 | -121.4783 | 119.1888
Line13_13_14 | 0.10079 | 0.10569 | 0.11252 | 0.10079 | 0.10569 | 0.11252 | 0.023276 | 0.024407 | 0.025986 | 0.023276 | 0.024407 | 0.025986 | -0.003216 | -0.0067626 | -0.0041265 | 0.0033176 | 0.0068743 | 0.0042531 | -0.0274 | -0.027997 | -0.030035 | 0.027603 | 0.02822 | 0.030289 | 96.1065 | -17.8986 | -142.9884 | -83.8935 | 162.1014 | 37.0116 | 1.1853 | 1.1801 | 1.1667 | 1.1944 | 1.19 | 1.177 | -0.58785 | -121.4783 | 119.1888 | -0.74696 | -121.589 | 119.0184
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.415e-10 | 6.9597e-10 | 5.717e-10 | -7.415e-10 | -6.9597e-10 | -5.717e-10 | 9.8093e-11 | 2.4558e-10 | 1.3325e-10 | -9.8093e-11 | -2.4558e-10 | -1.3325e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1853 | 1.1801 | 1.1667 | 1.1853 | 1.1801 | 1.1667 | -0.58785 | -121.4783 | 119.1888 | -0.58785 | -121.4783 | 119.1888
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7075e-10 | 3.4799e-10 | 2.8585e-10 | -3.7075e-10 | -3.4799e-10 | -2.8585e-10 | 4.9046e-11 | 1.2279e-10 | 6.6625e-11 | -4.9046e-11 | -1.2279e-10 | -6.6625e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1853 | 1.1801 | 1.1667 | 1.1853 | 1.1801 | 1.1667 | -0.58785 | -121.4783 | 119.1888 | -0.58785 | -121.4783 | 119.1888
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5633e-10 | 2.2466e-10 | 1.6087e-10 | -2.5633e-10 | -2.2466e-10 | -1.6087e-10 | 1.0815e-11 | 9.447e-11 | 2.6213e-11 | -1.0815e-11 | -9.447e-11 | -2.6213e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1602 | 1.1529 | 1.1385 | 1.1602 | 1.1529 | 1.1385 | -0.13242 | -121.1641 | 119.6729 | -0.13242 | -121.1641 | 119.6729
Line17_5_19 | 0.11963 | 0.12611 | 0.13332 | 0.11963 | 0.12611 | 0.13332 | 0.027626 | 0.029123 | 0.030788 | 0.027626 | 0.029123 | 0.030788 | -0.0037703 | -0.0078004 | -0.0045327 | 0.0039134 | 0.0079594 | 0.0047105 | -0.03181 | -0.032633 | -0.034734 | 0.032096 | 0.032951 | 0.035089 | 96.6376 | -17.7122 | -142.8787 | -83.3624 | 162.2878 | 37.1213 | 1.1595 | 1.1521 | 1.1377 | 1.1704 | 1.164 | 1.1499 | -0.12177 | -121.1554 | 119.6862 | -0.31389 | -121.2919 | 119.4755
Line1_1_3 | 0.10079 | 0.10569 | 0.11252 | 0.10079 | 0.10569 | 0.11252 | 0.023276 | 0.024407 | 0.025986 | 0.023276 | 0.024407 | 0.025986 | -0.0028097 | -0.0063158 | -0.0036201 | 0.0029113 | 0.0064275 | 0.0037467 | -0.026587 | -0.027103 | -0.029023 | 0.02679 | 0.027326 | 0.029276 | 96.1065 | -17.8986 | -142.9884 | -83.8935 | 162.1014 | 37.0116 | 1.1486 | 1.1402 | 1.1255 | 1.1578 | 1.1502 | 1.1358 | 0.074002 | -121.0162 | 119.9016 | -0.095385 | -121.1347 | 119.7185
Line2_1_4 | 0.12758 | 0.13475 | 0.14204 | 0.12758 | 0.13475 | 0.14204 | 0.029463 | 0.03112 | 0.032804 | 0.029463 | 0.03112 | 0.032804 | -0.0039987 | -0.0082092 | -0.0046749 | 0.0041615 | 0.0083908 | 0.0048766 | -0.033605 | -0.03452 | -0.036624 | 0.03393 | 0.034884 | 0.037028 | 96.86 | -17.6393 | -142.8243 | -83.14 | 162.3607 | 37.1757 | 1.1486 | 1.1402 | 1.1255 | 1.1602 | 1.1529 | 1.1385 | 0.074002 | -121.0162 | 119.9016 | -0.13242 | -121.1641 | 119.6729
Line3_1_5 | 0.11963 | 0.12611 | 0.13332 | 0.11963 | 0.12611 | 0.13332 | 0.027626 | 0.029123 | 0.030788 | 0.027626 | 0.029123 | 0.030788 | -0.0036272 | -0.0076414 | -0.004355 | 0.0037703 | 0.0078004 | 0.0045327 | -0.031524 | -0.032315 | -0.034378 | 0.03181 | 0.032633 | 0.034734 | 96.6376 | -17.7122 | -142.8787 | -83.3624 | 162.2878 | 37.1213 | 1.1486 | 1.1402 | 1.1255 | 1.1595 | 1.1521 | 1.1377 | 0.074002 | -121.0162 | 119.9016 | -0.12177 | -121.1554 | 119.6862
Line4_2_6 | 0.11261 | 0.11849 | 0.12559 | 0.11261 | 0.11849 | 0.12559 | 0.026006 | 0.027364 | 0.029004 | 0.026006 | 0.027364 | 0.029004 | -0.003439 | -0.0072846 | -0.0042354 | 0.0035658 | 0.007425 | 0.0043931 | -0.02994 | -0.030652 | -0.032704 | 0.030194 | 0.030933 | 0.03302 | 96.4403 | -17.7792 | -142.9227 | -83.5597 | 162.2208 | 37.0773 | 1.1589 | 1.1514 | 1.137 | 1.1691 | 1.1625 | 1.1485 | -0.11213 | -121.1478 | 119.6982 | -0.295 | -121.2768 | 119.4988
Line5_6_7 | 0.11261 | 0.11849 | 0.12559 | 0.11261 | 0.11849 | 0.12559 | 0.026006 | 0.027364 | 0.029004 | 0.026006 | 0.027364 | 0.029004 | -0.0035658 | -0.007425 | -0.0043931 | 0.0036926 | 0.0075654 | 0.0045509 | -0.030194 | -0.030933 | -0.03302 | 0.030447 | 0.031214 | 0.033335 | 96.4403 | -17.7792 | -142.9227 | -83.5597 | 162.2208 | 37.0773 | 1.1691 | 1.1625 | 1.1485 | 1.1794 | 1.1737 | 1.16 | -0.295 | -121.2768 | 119.4988 | -0.47468 | -121.4035 | 119.3034
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0302e-09 | 9.5616e-10 | 7.6668e-10 | -1.0302e-09 | -9.5616e-10 | -7.6668e-10 | 1.1823e-10 | 3.4785e-10 | 1.7065e-10 | -1.1823e-10 | -3.4785e-10 | -1.7065e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1794 | 1.1737 | 1.16 | 1.1794 | 1.1737 | 1.16 | -0.47468 | -121.4035 | 119.3034 | -0.47468 | -121.4035 | 119.3034
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4338e-10 | 3.1872e-10 | 2.5556e-10 | -3.4338e-10 | -3.1872e-10 | -2.5556e-10 | 3.9408e-11 | 1.1595e-10 | 5.6883e-11 | -3.9409e-11 | -1.1595e-10 | -5.6883e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1794 | 1.1737 | 1.16 | 1.1794 | 1.1737 | 1.16 | -0.47468 | -121.4035 | 119.3034 | -0.47468 | -121.4035 | 119.3034
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4338e-10 | 3.1872e-10 | 2.5556e-10 | -3.4338e-10 | -3.1872e-10 | -2.5556e-10 | 3.9408e-11 | 1.1595e-10 | 5.6883e-11 | -3.9408e-11 | -1.1595e-10 | -5.6883e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1794 | 1.1737 | 1.16 | 1.1794 | 1.1737 | 1.16 | -0.47468 | -121.4035 | 119.3034 | -0.47468 | -121.4035 | 119.3034
Line9_3_11 | 0.10079 | 0.10569 | 0.11252 | 0.10079 | 0.10569 | 0.11252 | 0.023276 | 0.024407 | 0.025986 | 0.023276 | 0.024407 | 0.025986 | -0.0029113 | -0.0064275 | -0.0037467 | 0.0030128 | 0.0065392 | 0.0038733 | -0.02679 | -0.027326 | -0.029276 | 0.026993 | 0.02755 | 0.029529 | 96.1065 | -17.8986 | -142.9884 | -83.8935 | 162.1014 | 37.0116 | 1.1578 | 1.1502 | 1.1358 | 1.1669 | 1.1601 | 1.1461 | -0.095385 | -121.1347 | 119.7185 | -0.26212 | -121.2512 | 119.5388

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0024038 | 0.014198 | 0.012011 | 0.0024038 | 0.014198 | 0.012011 | 0.00055514 | 0.0032789 | 0.0027739 | 0.00055514 | 0.0032789 | 0.0027739 | -0.00053524 | -0.0016287 | 0.0013584 | 0.00053535 | 0.0016326 | -0.0013556 | -0.00014805 | 0.0001814 | -0.00028824 | 0.00014816 | -0.00017736 | 0.00029113 | 164.5927 | 7.0317 | -168.5871 | -15.4073 | -172.9683 | 11.4129 | 1.0003 | 0.49981 | 0.5006 | 1.0006 | 0.50084 | 0.49984 | 0.054192 | -179.3232 | 179.4326 | 0.062631 | -179.1685 | 179.2922
Line10_11_12 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032686 | 0.0027661 | 0.00055181 | 0.0032686 | 0.0027661 | -0.00053285 | -0.0016309 | 0.0013486 | 0.00053296 | 0.0016347 | -0.0013458 | -0.00014517 | 0.00017647 | -0.00029541 | 0.00014528 | -0.00017246 | 0.00029828 | 164.8314 | 7.1608 | -168.4924 | -15.1686 | -172.8392 | 11.5076 | 1.0008 | 0.50187 | 0.49909 | 1.0011 | 0.50291 | 0.49835 | 0.071081 | -179.0148 | 179.1519 | 0.079519 | -178.8615 | 179.0109
Line11_12_13 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032686 | 0.0027661 | 0.00055181 | 0.0032686 | 0.0027661 | -0.00053296 | -0.0016347 | 0.0013458 | 0.00053307 | 0.0016386 | -0.001343 | -0.00014528 | 0.00017246 | -0.00029828 | 0.0001454 | -0.00016845 | 0.00030114 | 164.8314 | 7.1608 | -168.4924 | -15.1686 | -172.8392 | 11.5076 | 1.0011 | 0.50291 | 0.49835 | 1.0013 | 0.50396 | 0.4976 | 0.079519 | -178.8615 | 179.0109 | 0.087954 | -178.7089 | 178.8694
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4699e-11 | -8.5526e-11 | -1.0614e-10 | -1.4699e-11 | 8.5526e-11 | 1.0614e-10 | -1.6909e-11 | 4.7372e-09 | -4.6853e-09 | 1.6909e-11 | -4.7372e-09 | 4.6853e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0013 | 0.50396 | 0.4976 | 1.0013 | 0.50396 | 0.4976 | 0.087954 | -178.7089 | 178.8694 | 0.087954 | -178.7089 | 178.8694
Line13_13_14 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032685 | 0.0027661 | 0.00055181 | 0.0032685 | 0.0027661 | -0.00053307 | -0.0016386 | 0.001343 | 0.00053318 | 0.0016424 | -0.0013403 | -0.0001454 | 0.00016845 | -0.00030114 | 0.00014551 | -0.00016444 | 0.00030401 | 164.8314 | 7.1605 | -168.4927 | -15.1686 | -172.8395 | 11.5073 | 1.0013 | 0.50396 | 0.4976 | 1.0016 | 0.505 | 0.49686 | 0.087954 | -178.7089 | 178.8694 | 0.096383 | -178.5569 | 178.7276
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7992e-12 | -5.7018e-11 | -7.0758e-11 | -9.7991e-12 | 5.7018e-11 | 7.0759e-11 | -1.1272e-11 | 3.1581e-09 | -3.1236e-09 | 1.1272e-11 | -3.1581e-09 | 3.1236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0013 | 0.50396 | 0.4976 | 1.0013 | 0.50396 | 0.4976 | 0.087954 | -178.7089 | 178.8694 | 0.087954 | -178.7089 | 178.8694
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8997e-12 | -2.8509e-11 | -3.5379e-11 | -4.8996e-12 | 2.8509e-11 | 3.5379e-11 | -5.6363e-12 | 1.5791e-09 | -1.5618e-09 | 5.6363e-12 | -1.5791e-09 | 1.5618e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0013 | 0.50396 | 0.4976 | 1.0013 | 0.50396 | 0.4976 | 0.087954 | -178.7089 | 178.8694 | 0.087954 | -178.7089 | 178.8694
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2011e-12 | -2.1427e-11 | -1.9841e-11 | -2.2011e-12 | 2.1427e-11 | 1.9841e-11 | -4.0101e-12 | 1.5769e-09 | -1.5758e-09 | 4.0101e-12 | -1.5769e-09 | 1.5758e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0006 | 0.50085 | 0.49984 | 1.0006 | 0.50085 | 0.49984 | 0.062622 | -179.1682 | 179.2919 | 0.062622 | -179.1682 | 179.2919
Line17_5_19 | 0.0024111 | 0.01422 | 0.012028 | 0.0024111 | 0.01422 | 0.012028 | 0.00055682 | 0.0032841 | 0.0027778 | 0.00055682 | 0.0032841 | 0.0027778 | -0.00053665 | -0.0016354 | 0.0013577 | 0.00053676 | 0.0016393 | -0.001355 | -0.00014973 | 0.00017578 | -0.0002904 | 0.00014985 | -0.00017174 | 0.0002933 | 164.4729 | 6.9667 | -168.635 | -15.5271 | -173.0333 | 11.365 | 1.0006 | 0.50085 | 0.49984 | 1.0008 | 0.50189 | 0.49908 | 0.062626 | -179.1684 | 179.2921 | 0.071056 | -179.0141 | 179.1511
Line1_1_3 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032686 | 0.0027661 | 0.00055181 | 0.0032686 | 0.0027661 | -0.00053263 | -0.0016232 | 0.0013541 | 0.00053274 | 0.001627 | -0.0013513 | -0.00014494 | 0.00018448 | -0.00028967 | 0.00014506 | -0.00018048 | 0.00029254 | 164.8314 | 7.1609 | -168.4923 | -15.1686 | -172.8391 | 11.5077 | 1.0003 | 0.49981 | 0.5006 | 1.0006 | 0.50084 | 0.49985 | 0.054192 | -179.3232 | 179.4326 | 0.062639 | -179.1687 | 179.2924
Line2_1_4 | 0.0024184 | 0.014243 | 0.012045 | 0.0024184 | 0.014243 | 0.012045 | 0.0005585 | 0.0032893 | 0.0027817 | 0.0005585 | 0.0032893 | 0.0027817 | -0.00053784 | -0.0016343 | 0.0013627 | 0.00053796 | 0.0016382 | -0.0013599 | -0.0001512 | 0.00017826 | -0.00028678 | 0.00015131 | -0.0001742 | 0.00028969 | 164.3526 | 6.9017 | -168.6826 | -15.6474 | -173.0983 | 11.3174 | 1.0003 | 0.49981 | 0.5006 | 1.0006 | 0.50085 | 0.49984 | 0.054192 | -179.3232 | 179.4326 | 0.062622 | -179.1682 | 179.2919
Line3_1_5 | 0.0024111 | 0.01422 | 0.012028 | 0.0024111 | 0.01422 | 0.012028 | 0.00055682 | 0.0032841 | 0.0027778 | 0.00055682 | 0.0032841 | 0.0027778 | -0.00053654 | -0.0016315 | 0.0013605 | 0.00053665 | 0.0016354 | -0.0013577 | -0.00014962 | 0.00017983 | -0.00028751 | 0.00014973 | -0.00017579 | 0.0002904 | 164.4729 | 6.9667 | -168.635 | -15.5271 | -173.0333 | 11.365 | 1.0003 | 0.49981 | 0.5006 | 1.0006 | 0.50085 | 0.49984 | 0.054192 | -179.3232 | 179.4326 | 0.062626 | -179.1684 | 179.2921
Line4_2_6 | 0.0024038 | 0.014198 | 0.012011 | 0.0024038 | 0.014198 | 0.012011 | 0.00055514 | 0.0032789 | 0.0027739 | 0.00055514 | 0.0032789 | 0.0027739 | -0.00053535 | -0.0016326 | 0.0013556 | 0.00053546 | 0.0016365 | -0.0013528 | -0.00014816 | 0.00017736 | -0.00029112 | 0.00014828 | -0.00017333 | 0.00029401 | 164.5927 | 7.0317 | -168.5872 | -15.4073 | -172.9683 | 11.4128 | 1.0006 | 0.50084 | 0.49984 | 1.0008 | 0.50189 | 0.49909 | 0.062631 | -179.1685 | 179.2922 | 0.071065 | -179.0144 | 179.1514
Line5_6_7 | 0.0024038 | 0.014198 | 0.012011 | 0.0024038 | 0.014198 | 0.012011 | 0.00055514 | 0.0032789 | 0.0027739 | 0.00055514 | 0.0032789 | 0.0027739 | -0.00053546 | -0.0016365 | 0.0013528 | 0.00053557 | 0.0016403 | -0.0013501 | -0.00014828 | 0.00017333 | -0.00029401 | 0.00014839 | -0.0001693 | 0.00029689 | 164.5927 | 7.0316 | -168.5873 | -15.4073 | -172.9684 | 11.4127 | 1.0008 | 0.50189 | 0.49909 | 1.0011 | 0.50293 | 0.49833 | 0.071065 | -179.0144 | 179.1514 | 0.079495 | -178.8609 | 179.0101
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2052e-11 | -7.847e-11 | -9.0744e-11 | -1.2052e-11 | 7.847e-11 | 9.0744e-11 | -1.5278e-11 | 4.7351e-09 | -4.6992e-09 | 1.5279e-11 | -4.7351e-09 | 4.6992e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 0.50293 | 0.49833 | 1.0011 | 0.50293 | 0.49833 | 0.079495 | -178.8609 | 179.0101 | 0.079495 | -178.8609 | 179.0101
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0174e-12 | -2.6156e-11 | -3.0248e-11 | -4.0174e-12 | 2.6156e-11 | 3.0248e-11 | -5.0928e-12 | 1.5784e-09 | -1.5664e-09 | 5.0929e-12 | -1.5784e-09 | 1.5664e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 0.50293 | 0.49833 | 1.0011 | 0.50293 | 0.49833 | 0.079495 | -178.8609 | 179.0101 | 0.079495 | -178.8609 | 179.0101
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0175e-12 | -2.6157e-11 | -3.0248e-11 | -4.0174e-12 | 2.6157e-11 | 3.0248e-11 | -5.0928e-12 | 1.5784e-09 | -1.5664e-09 | 5.0928e-12 | -1.5784e-09 | 1.5664e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 0.50293 | 0.49833 | 1.0011 | 0.50293 | 0.49833 | 0.079495 | -178.8609 | 179.0101 | 0.079495 | -178.8609 | 179.0101
Line9_3_11 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032686 | 0.0027661 | 0.00055181 | 0.0032686 | 0.0027661 | -0.00053274 | -0.001627 | 0.0013513 | 0.00053285 | 0.0016309 | -0.0013486 | -0.00014506 | 0.00018048 | -0.00029254 | 0.00014517 | -0.00017647 | 0.00029541 | 164.8314 | 7.1609 | -168.4923 | -15.1686 | -172.8391 | 11.5077 | 1.0006 | 0.50084 | 0.49985 | 1.0008 | 0.50187 | 0.49909 | 0.062639 | -179.1687 | 179.2924 | 0.071081 | -179.0148 | 179.1519

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0024038 | 0.014198 | 0.012011 | 0.0024038 | 0.014198 | 0.012011 | 0.00055514 | 0.0032789 | 0.0027739 | 0.00055514 | 0.0032789 | 0.0027739 | -0.00053524 | -0.0016287 | 0.0013584 | 0.00053535 | 0.0016326 | -0.0013556 | -0.00014805 | 0.0001814 | -0.00028824 | 0.00014816 | -0.00017736 | 0.00029113 | 164.5927 | 7.0317 | -168.5871 | -15.4073 | -172.9683 | 11.4129 | 1.0003 | 0.49981 | 0.5006 | 1.0006 | 0.50084 | 0.49984 | 0.054192 | -179.3232 | 179.4326 | 0.062631 | -179.1685 | 179.2922
Line10_11_12 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032686 | 0.0027661 | 0.00055181 | 0.0032686 | 0.0027661 | -0.00053285 | -0.0016309 | 0.0013486 | 0.00053296 | 0.0016347 | -0.0013458 | -0.00014517 | 0.00017647 | -0.00029541 | 0.00014528 | -0.00017246 | 0.00029828 | 164.8314 | 7.1608 | -168.4924 | -15.1686 | -172.8392 | 11.5076 | 1.0008 | 0.50187 | 0.49909 | 1.0011 | 0.50291 | 0.49835 | 0.071081 | -179.0148 | 179.1519 | 0.079519 | -178.8615 | 179.0109
Line11_12_13 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032686 | 0.0027661 | 0.00055181 | 0.0032686 | 0.0027661 | -0.00053296 | -0.0016347 | 0.0013458 | 0.00053307 | 0.0016386 | -0.001343 | -0.00014528 | 0.00017246 | -0.00029828 | 0.0001454 | -0.00016845 | 0.00030114 | 164.8314 | 7.1608 | -168.4924 | -15.1686 | -172.8392 | 11.5076 | 1.0011 | 0.50291 | 0.49835 | 1.0013 | 0.50396 | 0.4976 | 0.079519 | -178.8615 | 179.0109 | 0.087954 | -178.7089 | 178.8694
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4699e-11 | -8.5526e-11 | -1.0614e-10 | -1.4699e-11 | 8.5526e-11 | 1.0614e-10 | -1.6909e-11 | 4.7372e-09 | -4.6853e-09 | 1.6909e-11 | -4.7372e-09 | 4.6853e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0013 | 0.50396 | 0.4976 | 1.0013 | 0.50396 | 0.4976 | 0.087954 | -178.7089 | 178.8694 | 0.087954 | -178.7089 | 178.8694
Line13_13_14 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032685 | 0.0027661 | 0.00055181 | 0.0032685 | 0.0027661 | -0.00053307 | -0.0016386 | 0.001343 | 0.00053318 | 0.0016424 | -0.0013403 | -0.0001454 | 0.00016845 | -0.00030114 | 0.00014551 | -0.00016444 | 0.00030401 | 164.8314 | 7.1605 | -168.4927 | -15.1686 | -172.8395 | 11.5073 | 1.0013 | 0.50396 | 0.4976 | 1.0016 | 0.505 | 0.49686 | 0.087954 | -178.7089 | 178.8694 | 0.096383 | -178.5569 | 178.7276
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7992e-12 | -5.7018e-11 | -7.0758e-11 | -9.7991e-12 | 5.7018e-11 | 7.0759e-11 | -1.1272e-11 | 3.1581e-09 | -3.1236e-09 | 1.1272e-11 | -3.1581e-09 | 3.1236e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0013 | 0.50396 | 0.4976 | 1.0013 | 0.50396 | 0.4976 | 0.087954 | -178.7089 | 178.8694 | 0.087954 | -178.7089 | 178.8694
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8997e-12 | -2.8509e-11 | -3.5379e-11 | -4.8996e-12 | 2.8509e-11 | 3.5379e-11 | -5.6363e-12 | 1.5791e-09 | -1.5618e-09 | 5.6363e-12 | -1.5791e-09 | 1.5618e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0013 | 0.50396 | 0.4976 | 1.0013 | 0.50396 | 0.4976 | 0.087954 | -178.7089 | 178.8694 | 0.087954 | -178.7089 | 178.8694
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2011e-12 | -2.1427e-11 | -1.9841e-11 | -2.2011e-12 | 2.1427e-11 | 1.9841e-11 | -4.0101e-12 | 1.5769e-09 | -1.5758e-09 | 4.0101e-12 | -1.5769e-09 | 1.5758e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0006 | 0.50085 | 0.49984 | 1.0006 | 0.50085 | 0.49984 | 0.062622 | -179.1682 | 179.2919 | 0.062622 | -179.1682 | 179.2919
Line17_5_19 | 0.0024111 | 0.01422 | 0.012028 | 0.0024111 | 0.01422 | 0.012028 | 0.00055682 | 0.0032841 | 0.0027778 | 0.00055682 | 0.0032841 | 0.0027778 | -0.00053665 | -0.0016354 | 0.0013577 | 0.00053676 | 0.0016393 | -0.001355 | -0.00014973 | 0.00017578 | -0.0002904 | 0.00014985 | -0.00017174 | 0.0002933 | 164.4729 | 6.9667 | -168.635 | -15.5271 | -173.0333 | 11.365 | 1.0006 | 0.50085 | 0.49984 | 1.0008 | 0.50189 | 0.49908 | 0.062626 | -179.1684 | 179.2921 | 0.071056 | -179.0141 | 179.1511
Line1_1_3 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032686 | 0.0027661 | 0.00055181 | 0.0032686 | 0.0027661 | -0.00053263 | -0.0016232 | 0.0013541 | 0.00053274 | 0.001627 | -0.0013513 | -0.00014494 | 0.00018448 | -0.00028967 | 0.00014506 | -0.00018048 | 0.00029254 | 164.8314 | 7.1609 | -168.4923 | -15.1686 | -172.8391 | 11.5077 | 1.0003 | 0.49981 | 0.5006 | 1.0006 | 0.50084 | 0.49985 | 0.054192 | -179.3232 | 179.4326 | 0.062639 | -179.1687 | 179.2924
Line2_1_4 | 0.0024184 | 0.014243 | 0.012045 | 0.0024184 | 0.014243 | 0.012045 | 0.0005585 | 0.0032893 | 0.0027817 | 0.0005585 | 0.0032893 | 0.0027817 | -0.00053784 | -0.0016343 | 0.0013627 | 0.00053796 | 0.0016382 | -0.0013599 | -0.0001512 | 0.00017826 | -0.00028678 | 0.00015131 | -0.0001742 | 0.00028969 | 164.3526 | 6.9017 | -168.6826 | -15.6474 | -173.0983 | 11.3174 | 1.0003 | 0.49981 | 0.5006 | 1.0006 | 0.50085 | 0.49984 | 0.054192 | -179.3232 | 179.4326 | 0.062622 | -179.1682 | 179.2919
Line3_1_5 | 0.0024111 | 0.01422 | 0.012028 | 0.0024111 | 0.01422 | 0.012028 | 0.00055682 | 0.0032841 | 0.0027778 | 0.00055682 | 0.0032841 | 0.0027778 | -0.00053654 | -0.0016315 | 0.0013605 | 0.00053665 | 0.0016354 | -0.0013577 | -0.00014962 | 0.00017983 | -0.00028751 | 0.00014973 | -0.00017579 | 0.0002904 | 164.4729 | 6.9667 | -168.635 | -15.5271 | -173.0333 | 11.365 | 1.0003 | 0.49981 | 0.5006 | 1.0006 | 0.50085 | 0.49984 | 0.054192 | -179.3232 | 179.4326 | 0.062626 | -179.1684 | 179.2921
Line4_2_6 | 0.0024038 | 0.014198 | 0.012011 | 0.0024038 | 0.014198 | 0.012011 | 0.00055514 | 0.0032789 | 0.0027739 | 0.00055514 | 0.0032789 | 0.0027739 | -0.00053535 | -0.0016326 | 0.0013556 | 0.00053546 | 0.0016365 | -0.0013528 | -0.00014816 | 0.00017736 | -0.00029112 | 0.00014828 | -0.00017333 | 0.00029401 | 164.5927 | 7.0317 | -168.5872 | -15.4073 | -172.9683 | 11.4128 | 1.0006 | 0.50084 | 0.49984 | 1.0008 | 0.50189 | 0.49909 | 0.062631 | -179.1685 | 179.2922 | 0.071065 | -179.0144 | 179.1514
Line5_6_7 | 0.0024038 | 0.014198 | 0.012011 | 0.0024038 | 0.014198 | 0.012011 | 0.00055514 | 0.0032789 | 0.0027739 | 0.00055514 | 0.0032789 | 0.0027739 | -0.00053546 | -0.0016365 | 0.0013528 | 0.00053557 | 0.0016403 | -0.0013501 | -0.00014828 | 0.00017333 | -0.00029401 | 0.00014839 | -0.0001693 | 0.00029689 | 164.5927 | 7.0316 | -168.5873 | -15.4073 | -172.9684 | 11.4127 | 1.0008 | 0.50189 | 0.49909 | 1.0011 | 0.50293 | 0.49833 | 0.071065 | -179.0144 | 179.1514 | 0.079495 | -178.8609 | 179.0101
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2052e-11 | -7.847e-11 | -9.0744e-11 | -1.2052e-11 | 7.847e-11 | 9.0744e-11 | -1.5278e-11 | 4.7351e-09 | -4.6992e-09 | 1.5279e-11 | -4.7351e-09 | 4.6992e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 0.50293 | 0.49833 | 1.0011 | 0.50293 | 0.49833 | 0.079495 | -178.8609 | 179.0101 | 0.079495 | -178.8609 | 179.0101
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0174e-12 | -2.6156e-11 | -3.0248e-11 | -4.0174e-12 | 2.6156e-11 | 3.0248e-11 | -5.0928e-12 | 1.5784e-09 | -1.5664e-09 | 5.0929e-12 | -1.5784e-09 | 1.5664e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 0.50293 | 0.49833 | 1.0011 | 0.50293 | 0.49833 | 0.079495 | -178.8609 | 179.0101 | 0.079495 | -178.8609 | 179.0101
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0175e-12 | -2.6157e-11 | -3.0248e-11 | -4.0174e-12 | 2.6157e-11 | 3.0248e-11 | -5.0928e-12 | 1.5784e-09 | -1.5664e-09 | 5.0928e-12 | -1.5784e-09 | 1.5664e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0011 | 0.50293 | 0.49833 | 1.0011 | 0.50293 | 0.49833 | 0.079495 | -178.8609 | 179.0101 | 0.079495 | -178.8609 | 179.0101
Line9_3_11 | 0.0023894 | 0.014153 | 0.011977 | 0.0023894 | 0.014153 | 0.011977 | 0.00055181 | 0.0032686 | 0.0027661 | 0.00055181 | 0.0032686 | 0.0027661 | -0.00053274 | -0.001627 | 0.0013513 | 0.00053285 | 0.0016309 | -0.0013486 | -0.00014506 | 0.00018048 | -0.00029254 | 0.00014517 | -0.00017647 | 0.00029541 | 164.8314 | 7.1609 | -168.4923 | -15.1686 | -172.8391 | 11.5077 | 1.0006 | 0.50084 | 0.49985 | 1.0008 | 0.50187 | 0.49909 | 0.062639 | -179.1687 | 179.2924 | 0.071081 | -179.0148 | 179.1519

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 8.2701e-05 | 0.00048846 | 0.00041323 | 8.2701e-05 | 0.00048846 | 0.00041323 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | -1.7628e-05 | -0.00010859 | -3.1222e-05 | 1.7628e-05 | 0.00010859 | 3.1225e-05 | 7.3493e-06 | -2.5745e-05 | -8.7213e-05 | -7.3492e-06 | 2.575e-05 | 8.7216e-05 | -157.3664 | 45.0727 | -130.5462 | 22.6336 | -134.9273 | 49.4538 | 0.99999 | 0.98931 | 0.97067 | 0.99999 | 0.98936 | 0.97072 | 0.0018924 | -121.5895 | 119.7566 | 0.0024227 | -121.5876 | 119.7554
Line10_11_12 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.00010831 | -3.1284e-05 | 1.7492e-05 | 0.00010832 | 3.1288e-05 | 7.3779e-06 | -2.543e-05 | -8.6923e-05 | -7.3777e-06 | 2.5434e-05 | 8.6926e-05 | -157.1277 | 45.2017 | -130.4515 | 22.8723 | -134.7983 | 49.5485 | 1 | 0.98941 | 0.97076 | 1 | 0.98945 | 0.97081 | 0.0029484 | -121.5858 | 119.7542 | 0.0034764 | -121.584 | 119.753
Line11_12_13 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.00010832 | -3.1288e-05 | 1.7492e-05 | 0.00010832 | 3.1291e-05 | 7.3777e-06 | -2.5435e-05 | -8.6926e-05 | -7.3776e-06 | 2.5439e-05 | 8.693e-05 | -157.1277 | 45.2017 | -130.4515 | 22.8723 | -134.7983 | 49.5485 | 1 | 0.98945 | 0.97081 | 1 | 0.9895 | 0.97085 | 0.0034764 | -121.584 | 119.753 | 0.0040044 | -121.5821 | 119.7518
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8623e-14 | -1.1009e-10 | -3.1116e-10 | -3.8621e-14 | 1.1009e-10 | 3.1116e-10 | -7.6879e-13 | 3.0052e-10 | 4.6261e-11 | 7.6879e-13 | -3.0052e-10 | -4.6261e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9895 | 0.97085 | 1 | 0.9895 | 0.97085 | 0.0040044 | -121.5821 | 119.7518 | 0.0040044 | -121.5821 | 119.7518
Line13_13_14 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.00010832 | -3.129e-05 | 1.7492e-05 | 0.00010833 | 3.1294e-05 | 7.3776e-06 | -2.544e-05 | -8.693e-05 | -7.3775e-06 | 2.5444e-05 | 8.6933e-05 | -157.1277 | 45.2015 | -130.4518 | 22.8723 | -134.7985 | 49.5482 | 1 | 0.9895 | 0.97085 | 1 | 0.98955 | 0.9709 | 0.0040044 | -121.5821 | 119.7518 | 0.0045324 | -121.5803 | 119.7506
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5746e-14 | -7.3396e-11 | -2.0744e-10 | -2.5749e-14 | 7.3396e-11 | 2.0744e-10 | -5.1253e-13 | 2.0035e-10 | 3.084e-11 | 5.1253e-13 | -2.0035e-10 | -3.084e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9895 | 0.97085 | 1 | 0.9895 | 0.97085 | 0.0040044 | -121.5821 | 119.7518 | 0.0040044 | -121.5821 | 119.7518
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2868e-14 | -3.6698e-11 | -1.0372e-10 | -1.2868e-14 | 3.6698e-11 | 1.0372e-10 | -2.5626e-13 | 1.0017e-10 | 1.542e-11 | 2.5626e-13 | -1.0017e-10 | -1.542e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9895 | 0.97085 | 1 | 0.9895 | 0.97085 | 0.0040044 | -121.5821 | 119.7518 | 0.0040044 | -121.5821 | 119.7518
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5525e-14 | -3.7215e-11 | -1.0419e-10 | 2.5524e-14 | 3.7215e-11 | 1.0419e-10 | -1.552e-13 | 1.0051e-10 | 1.5197e-11 | 1.5519e-13 | -1.0051e-10 | -1.5197e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99999 | 0.98936 | 0.97072 | 0.99999 | 0.98936 | 0.97072 | 0.002425 | -121.5876 | 119.7554 | 0.002425 | -121.5876 | 119.7554
Line17_5_19 | 8.295e-05 | 0.00048923 | 0.00041381 | 8.295e-05 | 0.00048923 | 0.00041381 | 1.9157e-05 | 0.00011298 | 9.5566e-05 | 1.9157e-05 | 0.00011298 | 9.5566e-05 | -1.7697e-05 | -0.00010874 | -3.1196e-05 | 1.7697e-05 | 0.00010874 | 3.1199e-05 | 7.3343e-06 | -2.5914e-05 | -8.7365e-05 | -7.3342e-06 | 2.5919e-05 | 8.7369e-05 | -157.4862 | 45.0076 | -130.5941 | 22.5138 | -134.9924 | 49.4059 | 0.99999 | 0.98936 | 0.97072 | 1 | 0.98941 | 0.97076 | 0.0024239 | -121.5876 | 119.7554 | 0.0029554 | -121.5858 | 119.7542
Line1_1_3 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.0001083 | -3.1278e-05 | 1.7492e-05 | 0.00010831 | 3.1281e-05 | 7.3781e-06 | -2.542e-05 | -8.6916e-05 | -7.378e-06 | 2.5425e-05 | 8.6919e-05 | -157.1277 | 45.2018 | -130.4513 | 22.8723 | -134.7982 | 49.5487 | 0.99999 | 0.98931 | 0.97067 | 0.99999 | 0.98936 | 0.97072 | 0.0018924 | -121.5895 | 119.7566 | 0.0024204 | -121.5876 | 119.7554
Line2_1_4 | 8.3201e-05 | 0.00049001 | 0.0004144 | 8.3201e-05 | 0.00049001 | 0.0004144 | 1.9214e-05 | 0.00011316 | 9.5701e-05 | 1.9214e-05 | 0.00011316 | 9.5701e-05 | -1.7765e-05 | -0.00010887 | -3.1164e-05 | 1.7766e-05 | 0.00010888 | 3.1168e-05 | 7.3194e-06 | -2.6074e-05 | -8.7511e-05 | -7.3192e-06 | 2.6079e-05 | 8.7515e-05 | -157.6065 | 44.9426 | -130.6417 | 22.3935 | -135.0574 | 49.3583 | 0.99999 | 0.98931 | 0.97067 | 0.99999 | 0.98936 | 0.97072 | 0.0018924 | -121.5895 | 119.7566 | 0.002425 | -121.5876 | 119.7554
Line3_1_5 | 8.295e-05 | 0.00048923 | 0.00041381 | 8.295e-05 | 0.00048923 | 0.00041381 | 1.9157e-05 | 0.00011298 | 9.5566e-05 | 1.9157e-05 | 0.00011298 | 9.5566e-05 | -1.7697e-05 | -0.00010873 | -3.1193e-05 | 1.7697e-05 | 0.00010874 | 3.1196e-05 | 7.3345e-06 | -2.5909e-05 | -8.7362e-05 | -7.3343e-06 | 2.5914e-05 | 8.7365e-05 | -157.4862 | 45.0076 | -130.594 | 22.5138 | -134.9924 | 49.406 | 0.99999 | 0.98931 | 0.97067 | 0.99999 | 0.98936 | 0.97072 | 0.0018924 | -121.5895 | 119.7566 | 0.0024239 | -121.5876 | 119.7554
Line4_2_6 | 8.2701e-05 | 0.00048846 | 0.00041323 | 8.2701e-05 | 0.00048846 | 0.00041323 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | -1.7628e-05 | -0.00010859 | -3.1225e-05 | 1.7628e-05 | 0.0001086 | 3.1228e-05 | 7.3492e-06 | -2.575e-05 | -8.7216e-05 | -7.349e-06 | 2.5755e-05 | 8.722e-05 | -157.3664 | 45.0726 | -130.5463 | 22.6336 | -134.9274 | 49.4537 | 0.99999 | 0.98936 | 0.97072 | 1 | 0.98941 | 0.97076 | 0.0024227 | -121.5876 | 119.7554 | 0.0029531 | -121.5858 | 119.7542
Line5_6_7 | 8.2701e-05 | 0.00048846 | 0.00041323 | 8.2701e-05 | 0.00048846 | 0.00041323 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | -1.7628e-05 | -0.0001086 | -3.1228e-05 | 1.7628e-05 | 0.0001086 | 3.1232e-05 | 7.349e-06 | -2.5755e-05 | -8.722e-05 | -7.3489e-06 | 2.576e-05 | 8.7223e-05 | -157.3664 | 45.0725 | -130.5464 | 22.6336 | -134.9275 | 49.4536 | 1 | 0.98941 | 0.97076 | 1 | 0.98946 | 0.97081 | 0.0029531 | -121.5858 | 119.7542 | 0.0034834 | -121.584 | 119.753
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7609e-15 | -1.1061e-10 | -3.1163e-10 | -1.7592e-15 | 1.1061e-10 | 3.1163e-10 | -6.6876e-13 | 3.0085e-10 | 4.6041e-11 | 6.6875e-13 | -3.0085e-10 | -4.6041e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.98946 | 0.97081 | 1 | 0.98946 | 0.97081 | 0.0034834 | -121.584 | 119.753 | 0.0034834 | -121.584 | 119.753
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8717e-16 | -3.6869e-11 | -1.0388e-10 | -5.9064e-16 | 3.6869e-11 | 1.0388e-10 | -2.2292e-13 | 1.0028e-10 | 1.5347e-11 | 2.2292e-13 | -1.0028e-10 | -1.5347e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.98946 | 0.97081 | 1 | 0.98946 | 0.97081 | 0.0034834 | -121.584 | 119.753 | 0.0034834 | -121.584 | 119.753
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8254e-16 | -3.6869e-11 | -1.0388e-10 | -5.837e-16 | 3.6869e-11 | 1.0388e-10 | -2.2292e-13 | 1.0028e-10 | 1.5347e-11 | 2.2291e-13 | -1.0028e-10 | -1.5347e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.98946 | 0.97081 | 1 | 0.98946 | 0.97081 | 0.0034834 | -121.584 | 119.753 | 0.0034834 | -121.584 | 119.753
Line9_3_11 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.00010831 | -3.1281e-05 | 1.7492e-05 | 0.00010831 | 3.1284e-05 | 7.378e-06 | -2.5425e-05 | -8.6919e-05 | -7.3779e-06 | 2.543e-05 | 8.6923e-05 | -157.1277 | 45.2018 | -130.4514 | 22.8723 | -134.7982 | 49.5486 | 0.99999 | 0.98936 | 0.97072 | 1 | 0.98941 | 0.97076 | 0.0024204 | -121.5876 | 119.7554 | 0.0029484 | -121.5858 | 119.7542

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 8.2701e-05 | 0.00048846 | 0.00041323 | 8.2701e-05 | 0.00048846 | 0.00041323 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | -1.7628e-05 | -0.00010859 | -3.1222e-05 | 1.7628e-05 | 0.00010859 | 3.1225e-05 | 7.3493e-06 | -2.5745e-05 | -8.7213e-05 | -7.3492e-06 | 2.575e-05 | 8.7216e-05 | -157.3664 | 45.0727 | -130.5462 | 22.6336 | -134.9273 | 49.4538 | 0.99999 | 0.98931 | 0.97067 | 0.99999 | 0.98936 | 0.97072 | 0.0018924 | -121.5895 | 119.7566 | 0.0024227 | -121.5876 | 119.7554
Line10_11_12 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.00010831 | -3.1284e-05 | 1.7492e-05 | 0.00010832 | 3.1288e-05 | 7.3779e-06 | -2.543e-05 | -8.6923e-05 | -7.3777e-06 | 2.5434e-05 | 8.6926e-05 | -157.1277 | 45.2017 | -130.4515 | 22.8723 | -134.7983 | 49.5485 | 1 | 0.98941 | 0.97076 | 1 | 0.98945 | 0.97081 | 0.0029484 | -121.5858 | 119.7542 | 0.0034764 | -121.584 | 119.753
Line11_12_13 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.00010832 | -3.1288e-05 | 1.7492e-05 | 0.00010832 | 3.1291e-05 | 7.3777e-06 | -2.5435e-05 | -8.6926e-05 | -7.3776e-06 | 2.5439e-05 | 8.693e-05 | -157.1277 | 45.2017 | -130.4515 | 22.8723 | -134.7983 | 49.5485 | 1 | 0.98945 | 0.97081 | 1 | 0.9895 | 0.97085 | 0.0034764 | -121.584 | 119.753 | 0.0040044 | -121.5821 | 119.7518
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8623e-14 | -1.1009e-10 | -3.1116e-10 | -3.8621e-14 | 1.1009e-10 | 3.1116e-10 | -7.6879e-13 | 3.0052e-10 | 4.6261e-11 | 7.6879e-13 | -3.0052e-10 | -4.6261e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9895 | 0.97085 | 1 | 0.9895 | 0.97085 | 0.0040044 | -121.5821 | 119.7518 | 0.0040044 | -121.5821 | 119.7518
Line13_13_14 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.00010832 | -3.129e-05 | 1.7492e-05 | 0.00010833 | 3.1294e-05 | 7.3776e-06 | -2.544e-05 | -8.693e-05 | -7.3775e-06 | 2.5444e-05 | 8.6933e-05 | -157.1277 | 45.2015 | -130.4518 | 22.8723 | -134.7985 | 49.5482 | 1 | 0.9895 | 0.97085 | 1 | 0.98955 | 0.9709 | 0.0040044 | -121.5821 | 119.7518 | 0.0045324 | -121.5803 | 119.7506
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5746e-14 | -7.3396e-11 | -2.0744e-10 | -2.5749e-14 | 7.3396e-11 | 2.0744e-10 | -5.1253e-13 | 2.0035e-10 | 3.084e-11 | 5.1253e-13 | -2.0035e-10 | -3.084e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9895 | 0.97085 | 1 | 0.9895 | 0.97085 | 0.0040044 | -121.5821 | 119.7518 | 0.0040044 | -121.5821 | 119.7518
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2868e-14 | -3.6698e-11 | -1.0372e-10 | -1.2868e-14 | 3.6698e-11 | 1.0372e-10 | -2.5626e-13 | 1.0017e-10 | 1.542e-11 | 2.5626e-13 | -1.0017e-10 | -1.542e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.9895 | 0.97085 | 1 | 0.9895 | 0.97085 | 0.0040044 | -121.5821 | 119.7518 | 0.0040044 | -121.5821 | 119.7518
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5525e-14 | -3.7215e-11 | -1.0419e-10 | 2.5524e-14 | 3.7215e-11 | 1.0419e-10 | -1.552e-13 | 1.0051e-10 | 1.5197e-11 | 1.5519e-13 | -1.0051e-10 | -1.5197e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99999 | 0.98936 | 0.97072 | 0.99999 | 0.98936 | 0.97072 | 0.002425 | -121.5876 | 119.7554 | 0.002425 | -121.5876 | 119.7554
Line17_5_19 | 8.295e-05 | 0.00048923 | 0.00041381 | 8.295e-05 | 0.00048923 | 0.00041381 | 1.9157e-05 | 0.00011298 | 9.5566e-05 | 1.9157e-05 | 0.00011298 | 9.5566e-05 | -1.7697e-05 | -0.00010874 | -3.1196e-05 | 1.7697e-05 | 0.00010874 | 3.1199e-05 | 7.3343e-06 | -2.5914e-05 | -8.7365e-05 | -7.3342e-06 | 2.5919e-05 | 8.7369e-05 | -157.4862 | 45.0076 | -130.5941 | 22.5138 | -134.9924 | 49.4059 | 0.99999 | 0.98936 | 0.97072 | 1 | 0.98941 | 0.97076 | 0.0024239 | -121.5876 | 119.7554 | 0.0029554 | -121.5858 | 119.7542
Line1_1_3 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.0001083 | -3.1278e-05 | 1.7492e-05 | 0.00010831 | 3.1281e-05 | 7.3781e-06 | -2.542e-05 | -8.6916e-05 | -7.378e-06 | 2.5425e-05 | 8.6919e-05 | -157.1277 | 45.2018 | -130.4513 | 22.8723 | -134.7982 | 49.5487 | 0.99999 | 0.98931 | 0.97067 | 0.99999 | 0.98936 | 0.97072 | 0.0018924 | -121.5895 | 119.7566 | 0.0024204 | -121.5876 | 119.7554
Line2_1_4 | 8.3201e-05 | 0.00049001 | 0.0004144 | 8.3201e-05 | 0.00049001 | 0.0004144 | 1.9214e-05 | 0.00011316 | 9.5701e-05 | 1.9214e-05 | 0.00011316 | 9.5701e-05 | -1.7765e-05 | -0.00010887 | -3.1164e-05 | 1.7766e-05 | 0.00010888 | 3.1168e-05 | 7.3194e-06 | -2.6074e-05 | -8.7511e-05 | -7.3192e-06 | 2.6079e-05 | 8.7515e-05 | -157.6065 | 44.9426 | -130.6417 | 22.3935 | -135.0574 | 49.3583 | 0.99999 | 0.98931 | 0.97067 | 0.99999 | 0.98936 | 0.97072 | 0.0018924 | -121.5895 | 119.7566 | 0.002425 | -121.5876 | 119.7554
Line3_1_5 | 8.295e-05 | 0.00048923 | 0.00041381 | 8.295e-05 | 0.00048923 | 0.00041381 | 1.9157e-05 | 0.00011298 | 9.5566e-05 | 1.9157e-05 | 0.00011298 | 9.5566e-05 | -1.7697e-05 | -0.00010873 | -3.1193e-05 | 1.7697e-05 | 0.00010874 | 3.1196e-05 | 7.3345e-06 | -2.5909e-05 | -8.7362e-05 | -7.3343e-06 | 2.5914e-05 | 8.7365e-05 | -157.4862 | 45.0076 | -130.594 | 22.5138 | -134.9924 | 49.406 | 0.99999 | 0.98931 | 0.97067 | 0.99999 | 0.98936 | 0.97072 | 0.0018924 | -121.5895 | 119.7566 | 0.0024239 | -121.5876 | 119.7554
Line4_2_6 | 8.2701e-05 | 0.00048846 | 0.00041323 | 8.2701e-05 | 0.00048846 | 0.00041323 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | -1.7628e-05 | -0.00010859 | -3.1225e-05 | 1.7628e-05 | 0.0001086 | 3.1228e-05 | 7.3492e-06 | -2.575e-05 | -8.7216e-05 | -7.349e-06 | 2.5755e-05 | 8.722e-05 | -157.3664 | 45.0726 | -130.5463 | 22.6336 | -134.9274 | 49.4537 | 0.99999 | 0.98936 | 0.97072 | 1 | 0.98941 | 0.97076 | 0.0024227 | -121.5876 | 119.7554 | 0.0029531 | -121.5858 | 119.7542
Line5_6_7 | 8.2701e-05 | 0.00048846 | 0.00041323 | 8.2701e-05 | 0.00048846 | 0.00041323 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | 1.9099e-05 | 0.00011281 | 9.5432e-05 | -1.7628e-05 | -0.0001086 | -3.1228e-05 | 1.7628e-05 | 0.0001086 | 3.1232e-05 | 7.349e-06 | -2.5755e-05 | -8.722e-05 | -7.3489e-06 | 2.576e-05 | 8.7223e-05 | -157.3664 | 45.0725 | -130.5464 | 22.6336 | -134.9275 | 49.4536 | 1 | 0.98941 | 0.97076 | 1 | 0.98946 | 0.97081 | 0.0029531 | -121.5858 | 119.7542 | 0.0034834 | -121.584 | 119.753
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7609e-15 | -1.1061e-10 | -3.1163e-10 | -1.7592e-15 | 1.1061e-10 | 3.1163e-10 | -6.6876e-13 | 3.0085e-10 | 4.6041e-11 | 6.6875e-13 | -3.0085e-10 | -4.6041e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.98946 | 0.97081 | 1 | 0.98946 | 0.97081 | 0.0034834 | -121.584 | 119.753 | 0.0034834 | -121.584 | 119.753
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8717e-16 | -3.6869e-11 | -1.0388e-10 | -5.9064e-16 | 3.6869e-11 | 1.0388e-10 | -2.2292e-13 | 1.0028e-10 | 1.5347e-11 | 2.2292e-13 | -1.0028e-10 | -1.5347e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.98946 | 0.97081 | 1 | 0.98946 | 0.97081 | 0.0034834 | -121.584 | 119.753 | 0.0034834 | -121.584 | 119.753
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8254e-16 | -3.6869e-11 | -1.0388e-10 | -5.837e-16 | 3.6869e-11 | 1.0388e-10 | -2.2292e-13 | 1.0028e-10 | 1.5347e-11 | 2.2291e-13 | -1.0028e-10 | -1.5347e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.98946 | 0.97081 | 1 | 0.98946 | 0.97081 | 0.0034834 | -121.584 | 119.753 | 0.0034834 | -121.584 | 119.753
Line9_3_11 | 8.2204e-05 | 0.00048692 | 0.00041207 | 8.2204e-05 | 0.00048692 | 0.00041207 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | 1.8984e-05 | 0.00011245 | 9.5163e-05 | -1.7492e-05 | -0.00010831 | -3.1281e-05 | 1.7492e-05 | 0.00010831 | 3.1284e-05 | 7.378e-06 | -2.5425e-05 | -8.6919e-05 | -7.3779e-06 | 2.543e-05 | 8.6923e-05 | -157.1277 | 45.2018 | -130.4514 | 22.8723 | -134.7982 | 49.5486 | 0.99999 | 0.98936 | 0.97072 | 1 | 0.98941 | 0.97076 | 0.0024204 | -121.5876 | 119.7554 | 0.0029484 | -121.5858 | 119.7542

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.46944 | 0.23688 | 0.28112 | 0.46944 | 0.23688 | 0.28112 | 0.10841 | 0.054705 | 0.064923 | 0.10841 | 0.054705 | 0.064923 | -0.0082188 | 0.035421 | -0.058012 | 0.010423 | -0.03486 | 0.058802 | -0.060016 | -0.044421 | -0.033605 | 0.064423 | 0.045544 | 0.035186 | 99.2276 | -53.3733 | -103.5876 | -80.7724 | 126.6267 | 76.4124 |  | 0.55876 | 1.0386 | 1.0326 | 0.60197 | 1.0484 | 1.0555 | 1.4298 | -104.8047 | 106.4952 | 0.037854 | -105.942 | 107.3075
Line10_11_12 | 0.42076 | 0.21554 | 0.24614 | 0.42076 | 0.21554 | 0.24614 | 0.097171 | 0.049777 | 0.056844 | 0.097171 | 0.049777 | 0.056844 | -0.011922 | 0.031467 | -0.052637 | 0.013693 | -0.031003 | 0.053243 | -0.060726 | -0.042145 | -0.030727 | 0.064267 | 0.043074 | 0.031939 | 100.31 | -53.609 | -102.3328 | -79.69 | 126.391 | 77.6672 |  | 0.63687 | 1.0566 | 1.0722 | 0.67622 | 1.0662 | 1.0923 | -0.79755 | -106.8625 | 107.9419 | -1.7176 | -107.8646 | 108.6258
Line11_12_13 | 0.42076 | 0.21554 | 0.24614 | 0.42076 | 0.21554 | 0.24614 | 0.097171 | 0.049777 | 0.056844 | 0.097171 | 0.049777 | 0.056844 | -0.013693 | 0.031003 | -0.053243 | 0.015463 | -0.030538 | 0.053849 | -0.064267 | -0.043074 | -0.031939 | 0.067808 | 0.044004 | 0.033151 | 100.31 | -53.609 | -102.3328 | -79.69 | 126.391 | 77.6672 |  | 0.67622 | 1.0662 | 1.0923 | 0.71573 | 1.076 | 1.1124 | -1.7176 | -107.8646 | 108.6258 | -2.5363 | -108.8486 | 109.2849
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0169e-09 | -3.7794e-11 | 3.8679e-10 | 3.0169e-09 | 3.7794e-11 | -3.8679e-10 | 3.8324e-10 | -2.5181e-09 | 2.5026e-09 | -3.8324e-10 | 2.5181e-09 | -2.5026e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71573 | 1.076 | 1.1124 | 0.71573 | 1.076 | 1.1124 | -2.5363 | -108.8486 | 109.2849 | -2.5363 | -108.8486 | 109.2849
Line13_13_14 | 0.42076 | 0.21554 | 0.24614 | 0.42076 | 0.21554 | 0.24614 | 0.097171 | 0.049777 | 0.056844 | 0.097171 | 0.049777 | 0.056844 | -0.015463 | 0.030538 | -0.053849 | 0.017234 | -0.030074 | 0.054455 | -0.067808 | -0.044004 | -0.033151 | 0.071349 | 0.044933 | 0.034363 | 100.31 | -53.609 | -102.3328 | -79.69 | 126.391 | 77.6672 |  | 0.71573 | 1.076 | 1.1124 | 0.75537 | 1.0862 | 1.1328 | -2.5363 | -108.8486 | 109.2849 | -3.2691 | -109.8145 | 109.9204
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0112e-09 | -2.5196e-11 | 2.5786e-10 | 2.0112e-09 | 2.5196e-11 | -2.5786e-10 | 2.5549e-10 | -1.6787e-09 | 1.6684e-09 | -2.5549e-10 | 1.6787e-09 | -1.6684e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71573 | 1.076 | 1.1124 | 0.71573 | 1.076 | 1.1124 | -2.5363 | -108.8486 | 109.2849 | -2.5363 | -108.8486 | 109.2849
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0056e-09 | -1.2598e-11 | 1.2893e-10 | 1.0056e-09 | 1.2598e-11 | -1.2893e-10 | 1.2775e-10 | -8.3937e-10 | 8.3421e-10 | -1.2775e-10 | 8.3937e-10 | -8.3421e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71573 | 1.076 | 1.1124 | 0.71573 | 1.076 | 1.1124 | -2.5363 | -108.8486 | 109.2849 | -2.5363 | -108.8486 | 109.2849
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0971e-09 | -6.8913e-11 | -5.365e-11 | 1.0971e-09 | 6.8913e-11 | 5.3651e-11 | 1.0029e-11 | -1.0198e-09 | 9.3274e-10 | -1.0029e-11 | 1.0198e-09 | -9.3274e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.60723 | 1.0497 | 1.0597 | 0.60723 | 1.0497 | 1.0597 | -0.23461 | -106.0623 | 107.3947 | -0.23461 | -106.0623 | 107.3947
Line17_5_19 | 0.49807 | 0.24929 | 0.30231 | 0.49807 | 0.24929 | 0.30231 | 0.11503 | 0.057571 | 0.069816 | 0.11503 | 0.057571 | 0.069816 | -0.010503 | 0.036505 | -0.062816 | 0.012984 | -0.035883 | 0.06373 | -0.06873 | -0.048112 | -0.038785 | 0.073692 | 0.049355 | 0.040613 | 98.6 | -53.1887 | -104.343 | -81.4 | 126.8113 | 75.657 |  | 0.60446 | 1.049 | 1.0574 | 0.65053 | 1.0599 | 1.0824 | -0.088338 | -105.9992 | 107.3496 | -1.3923 | -107.1695 | 108.1648
Line1_1_3 | 0.42076 | 0.21554 | 0.24614 | 0.42076 | 0.21554 | 0.24614 | 0.097171 | 0.049777 | 0.056844 | 0.097171 | 0.049777 | 0.056844 | -0.0083815 | 0.032396 | -0.051425 | 0.010152 | -0.031932 | 0.052031 | -0.053644 | -0.040287 | -0.028304 | 0.057185 | 0.041216 | 0.029516 | 100.31 | -53.609 | -102.3328 | -79.69 | 126.391 | 77.6672 |  | 0.55876 | 1.0386 | 1.0326 | 0.5977 | 1.0474 | 1.0524 | 1.4298 | -104.8047 | 106.4952 | 0.24338 | -105.8425 | 107.2321
Line2_1_4 | 0.53027 | 0.26316 | 0.32666 | 0.53027 | 0.26316 | 0.32666 | 0.12246 | 0.060775 | 0.075438 | 0.12246 | 0.060775 | 0.075438 | -0.0077141 | 0.03898 | -0.066278 | 0.010526 | -0.038287 | 0.067345 | -0.06799 | -0.049645 | -0.040936 | 0.073613 | 0.05103 | 0.04307 | 97.9029 | -52.9424 | -105.2059 | -82.0971 | 127.0576 | 74.7941 |  | 0.55876 | 1.0386 | 1.0326 | 0.60723 | 1.0497 | 1.0597 | 1.4298 | -104.8047 | 106.4952 | -0.23461 | -106.0623 | 107.3947
Line3_1_5 | 0.49807 | 0.24929 | 0.30231 | 0.49807 | 0.24929 | 0.30231 | 0.11503 | 0.057571 | 0.069816 | 0.11503 | 0.057571 | 0.069816 | -0.0080222 | 0.037126 | -0.061902 | 0.010503 | -0.036505 | 0.062816 | -0.063769 | -0.046869 | -0.036957 | 0.06873 | 0.048112 | 0.038785 | 98.6 | -53.1887 | -104.343 | -81.4 | 126.8113 | 75.657 |  | 0.55876 | 1.0386 | 1.0326 | 0.60446 | 1.049 | 1.0574 | 1.4298 | -104.8047 | 106.4952 | -0.088338 | -105.9992 | 107.3496
Line4_2_6 | 0.46944 | 0.23688 | 0.28112 | 0.46944 | 0.23688 | 0.28112 | 0.10841 | 0.054705 | 0.064923 | 0.10841 | 0.054705 | 0.064923 | -0.010423 | 0.03486 | -0.058802 | 0.012626 | -0.034299 | 0.059593 | -0.064423 | -0.045544 | -0.035186 | 0.068831 | 0.046666 | 0.036766 | 99.2276 | -53.3733 | -103.5876 | -80.7724 | 126.6267 | 76.4124 |  | 0.60197 | 1.0484 | 1.0555 | 0.64549 | 1.0587 | 1.0785 | 0.037854 | -105.942 | 107.3075 | -1.1671 | -107.0577 | 108.0854
Line5_6_7 | 0.46944 | 0.23688 | 0.28112 | 0.46944 | 0.23688 | 0.28112 | 0.10841 | 0.054705 | 0.064923 | 0.10841 | 0.054705 | 0.064923 | -0.012626 | 0.034299 | -0.059593 | 0.01483 | -0.033738 | 0.060383 | -0.068831 | -0.046666 | -0.036766 | 0.073238 | 0.047788 | 0.038347 | 99.2276 | -53.3733 | -103.5876 | -80.7724 | 126.6267 | 76.4124 |  | 0.64549 | 1.0587 | 1.0785 | 0.68927 | 1.0693 | 1.1018 | -1.1671 | -107.0577 | 108.0854 | -2.2194 | -108.1516 | 108.8305
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1079e-09 | -8.5135e-11 | 2.7401e-10 | 3.1079e-09 | 8.5134e-11 | -2.7401e-10 | 3.2297e-10 | -2.6566e-09 | 2.5825e-09 | -3.2297e-10 | 2.6566e-09 | -2.5825e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68927 | 1.0693 | 1.1018 | 0.68927 | 1.0693 | 1.1018 | -2.2194 | -108.1516 | 108.8305 | -2.2194 | -108.1516 | 108.8305
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.036e-09 | -2.8378e-11 | 9.1337e-11 | 1.036e-09 | 2.8378e-11 | -9.1337e-11 | 1.0766e-10 | -8.8555e-10 | 8.6082e-10 | -1.0766e-10 | 8.8555e-10 | -8.6082e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68927 | 1.0693 | 1.1018 | 0.68927 | 1.0693 | 1.1018 | -2.2194 | -108.1516 | 108.8305 | -2.2194 | -108.1516 | 108.8305
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.036e-09 | -2.8378e-11 | 9.1337e-11 | 1.036e-09 | 2.8378e-11 | -9.1336e-11 | 1.0766e-10 | -8.8555e-10 | 8.6082e-10 | -1.0766e-10 | 8.8555e-10 | -8.6082e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68927 | 1.0693 | 1.1018 | 0.68927 | 1.0693 | 1.1018 | -2.2194 | -108.1516 | 108.8305 | -2.2194 | -108.1516 | 108.8305
Line9_3_11 | 0.42076 | 0.21554 | 0.24614 | 0.42076 | 0.21554 | 0.24614 | 0.097171 | 0.049777 | 0.056844 | 0.097171 | 0.049777 | 0.056844 | -0.010152 | 0.031932 | -0.052031 | 0.011922 | -0.031467 | 0.052637 | -0.057185 | -0.041216 | -0.029516 | 0.060726 | 0.042145 | 0.030727 | 100.31 | -53.609 | -102.3328 | -79.69 | 126.391 | 77.6672 |  | 0.5977 | 1.0474 | 1.0524 | 0.63687 | 1.0566 | 1.0722 | 0.24338 | -105.8425 | 107.2321 | -0.79755 | -106.8625 | 107.9419

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.45618 | 0.23193 | 0.27438 | 0.45618 | 0.23193 | 0.27438 | 0.10535 | 0.053563 | 0.063366 | 0.10535 | 0.053563 | 0.063366 | -0.0079322 | 0.034257 | -0.056274 | 0.010013 | -0.033719 | 0.057026 | -0.058674 | -0.043998 | -0.033723 | 0.062836 | 0.045074 | 0.035228 | 99.1105 | -52.7567 | -104.3785 | -80.8895 | 127.2433 | 75.6215 |  | 0.56201 | 1.041 | 1.0353 | 0.60398 | 1.0509 | 1.0578 | 1.4113 | -104.8525 | 106.5541 | 0.056324 | -105.9574 | 107.3273
Line10_11_12 | 0.41049 | 0.2117 | 0.24135 | 0.41049 | 0.2117 | 0.24135 | 0.094798 | 0.048889 | 0.055737 | 0.094798 | 0.048889 | 0.055737 | -0.011462 | 0.030545 | -0.05127 | 0.013147 | -0.030097 | 0.051852 | -0.059399 | -0.041815 | -0.030958 | 0.062769 | 0.042711 | 0.032123 | 100.1477 | -53.0058 | -103.1878 | -79.8523 | 126.9942 | 76.8122 |  | 0.63815 | 1.0592 | 1.0745 | 0.67651 | 1.0688 | 1.0944 | -0.77434 | -106.8581 | 107.9367 | -1.682 | -107.8347 | 108.5907
Line11_12_13 | 0.41049 | 0.2117 | 0.24135 | 0.41049 | 0.2117 | 0.24135 | 0.094798 | 0.048889 | 0.055737 | 0.094798 | 0.048889 | 0.055737 | -0.013147 | 0.030097 | -0.051852 | 0.014832 | -0.029649 | 0.052435 | -0.062769 | -0.042711 | -0.032123 | 0.066139 | 0.043608 | 0.033288 | 100.1477 | -53.0058 | -103.1878 | -79.8523 | 126.9942 | 76.8122 |  | 0.67651 | 1.0688 | 1.0944 | 0.71502 | 1.0786 | 1.1143 | -1.682 | -107.8347 | 108.5907 | -2.4921 | -108.7938 | 109.2213
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0198e-09 | -4.956e-12 | 4.1332e-10 | 3.0198e-09 | 4.9557e-12 | -4.1332e-10 | 3.762e-10 | -2.5364e-09 | 2.5216e-09 | -3.762e-10 | 2.5364e-09 | -2.5216e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71502 | 1.0786 | 1.1143 | 0.71502 | 1.0786 | 1.1143 | -2.4921 | -108.7938 | 109.2213 | -2.4921 | -108.7938 | 109.2213
Line13_13_14 | 0.41049 | 0.2117 | 0.24135 | 0.41049 | 0.2117 | 0.24135 | 0.094798 | 0.048889 | 0.055737 | 0.094798 | 0.048889 | 0.055737 | -0.014832 | 0.029649 | -0.052435 | 0.016517 | -0.029201 | 0.053017 | -0.066139 | -0.043608 | -0.033288 | 0.069509 | 0.044504 | 0.034453 | 100.1477 | -53.0058 | -103.1878 | -79.8523 | 126.9942 | 76.8122 |  | 0.71502 | 1.0786 | 1.1143 | 0.75365 | 1.0888 | 1.1344 | -2.4921 | -108.7938 | 109.2213 | -3.2193 | -109.7352 | 109.8297
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.0132e-09 | -3.3038e-12 | 2.7554e-10 | 2.0132e-09 | 3.3039e-12 | -2.7554e-10 | 2.508e-10 | -1.6909e-09 | 1.681e-09 | -2.508e-10 | 1.6909e-09 | -1.681e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71502 | 1.0786 | 1.1143 | 0.71502 | 1.0786 | 1.1143 | -2.4921 | -108.7938 | 109.2213 | -2.4921 | -108.7938 | 109.2213
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0066e-09 | -1.6522e-12 | 1.3777e-10 | 1.0066e-09 | 1.652e-12 | -1.3777e-10 | 1.254e-10 | -8.4546e-10 | 8.4052e-10 | -1.254e-10 | 8.4546e-10 | -8.4052e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.71502 | 1.0786 | 1.1143 | 0.71502 | 1.0786 | 1.1143 | -2.4921 | -108.7938 | 109.2213 | -2.4921 | -108.7938 | 109.2213
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0964e-09 | -5.974e-11 | -4.5842e-11 | 1.0964e-09 | 5.974e-11 | 4.5842e-11 | 8.4202e-12 | -1.0217e-09 | 9.3371e-10 | -8.4202e-12 | 1.0217e-09 | -9.3371e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.60887 | 1.0522 | 1.0618 | 0.60887 | 1.0522 | 1.0618 | -0.19645 | -106.0695 | 107.4066 | -0.19645 | -106.0695 | 107.4066
Line17_5_19 | 0.4829 | 0.24365 | 0.29425 | 0.4829 | 0.24365 | 0.29425 | 0.11152 | 0.056268 | 0.067953 | 0.11152 | 0.056268 | 0.067953 | -0.01008 | 0.035242 | -0.060759 | 0.012412 | -0.034648 | 0.061625 | -0.066859 | -0.047525 | -0.038644 | 0.071523 | 0.048712 | 0.040375 | 98.5127 | -52.569 | -105.0911 | -81.4873 | 127.431 | 74.9089 |  | 0.6063 | 1.0515 | 1.0597 | 0.65093 | 1.0624 | 1.0842 | -0.061134 | -106.0107 | 107.3657 | -1.3324 | -107.1457 | 108.1407
Line1_1_3 | 0.41049 | 0.2117 | 0.24135 | 0.41049 | 0.2117 | 0.24135 | 0.094798 | 0.048889 | 0.055737 | 0.094798 | 0.048889 | 0.055737 | -0.0080922 | 0.031442 | -0.050105 | 0.0097772 | -0.030993 | 0.050687 | -0.052659 | -0.040022 | -0.028628 | 0.056029 | 0.040919 | 0.029793 | 100.1477 | -53.0058 | -103.1878 | -79.8523 | 126.9942 | 76.8122 |  | 0.56201 | 1.041 | 1.0353 | 0.59997 | 1.05 | 1.0549 | 1.4113 | -104.8525 | 106.5541 | 0.24916 | -105.864 | 107.2583
Line2_1_4 | 0.5128 | 0.2567 | 0.31695 | 0.5128 | 0.2567 | 0.31695 | 0.11843 | 0.059281 | 0.073196 | 0.11843 | 0.059281 | 0.073196 | -0.0074656 | 0.037545 | -0.063946 | 0.010095 | -0.036886 | 0.06495 | -0.066136 | -0.04898 | -0.040668 | 0.071396 | 0.050298 | 0.042677 | 97.8517 | -52.3241 | -105.9013 | -82.1483 | 127.6759 | 74.0987 |  | 0.56201 | 1.041 | 1.0353 | 0.60887 | 1.0522 | 1.0618 | 1.4113 | -104.8525 | 106.5541 | -0.19645 | -106.0695 | 107.4066
Line3_1_5 | 0.4829 | 0.24365 | 0.29425 | 0.4829 | 0.24365 | 0.29425 | 0.11152 | 0.056268 | 0.067953 | 0.11152 | 0.056268 | 0.067953 | -0.0077483 | 0.035835 | -0.059894 | 0.01008 | -0.035242 | 0.060759 | -0.062195 | -0.046338 | -0.036912 | 0.066859 | 0.047525 | 0.038644 | 98.5127 | -52.569 | -105.0911 | -81.4873 | 127.431 | 74.9089 |  | 0.56201 | 1.041 | 1.0353 | 0.6063 | 1.0515 | 1.0597 | 1.4113 | -104.8525 | 106.5541 | -0.061134 | -106.0107 | 107.3657
Line4_2_6 | 0.45618 | 0.23193 | 0.27438 | 0.45618 | 0.23193 | 0.27438 | 0.10535 | 0.053563 | 0.063366 | 0.10535 | 0.053563 | 0.063366 | -0.010013 | 0.033719 | -0.057026 | 0.012094 | -0.033181 | 0.057779 | -0.062836 | -0.045074 | -0.035228 | 0.066998 | 0.04615 | 0.036734 | 99.1105 | -52.7567 | -104.3785 | -80.8895 | 127.2433 | 75.6215 |  | 0.60398 | 1.0509 | 1.0578 | 0.64624 | 1.0612 | 1.0805 | 0.056324 | -105.9574 | 107.3273 | -1.1221 | -107.0413 | 108.0682
Line5_6_7 | 0.45618 | 0.23193 | 0.27438 | 0.45618 | 0.23193 | 0.27438 | 0.10535 | 0.053563 | 0.063366 | 0.10535 | 0.053563 | 0.063366 | -0.012094 | 0.033181 | -0.057779 | 0.014175 | -0.032643 | 0.058532 | -0.066998 | -0.04615 | -0.036734 | 0.07116 | 0.047225 | 0.03824 | 99.1105 | -52.7567 | -104.3785 | -80.8895 | 127.2433 | 75.6215 |  | 0.64624 | 1.0612 | 1.0805 | 0.68873 | 1.0718 | 1.1034 | -1.1221 | -107.0413 | 108.0682 | -2.1554 | -108.1041 | 108.7785
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1099e-09 | -5.3882e-11 | 2.9627e-10 | 3.1099e-09 | 5.3882e-11 | -2.9627e-10 | 3.1343e-10 | -2.6733e-09 | 2.5981e-09 | -3.1343e-10 | 2.6733e-09 | -2.5981e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68873 | 1.0718 | 1.1034 | 0.68873 | 1.0718 | 1.1034 | -2.1554 | -108.1041 | 108.7785 | -2.1554 | -108.1041 | 108.7785
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0366e-09 | -1.7961e-11 | 9.8758e-11 | 1.0366e-09 | 1.7961e-11 | -9.8758e-11 | 1.0448e-10 | -8.9111e-10 | 8.6604e-10 | -1.0448e-10 | 8.9111e-10 | -8.6604e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68873 | 1.0718 | 1.1034 | 0.68873 | 1.0718 | 1.1034 | -2.1554 | -108.1041 | 108.7785 | -2.1554 | -108.1041 | 108.7785
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0366e-09 | -1.7961e-11 | 9.8758e-11 | 1.0366e-09 | 1.7961e-11 | -9.8758e-11 | 1.0448e-10 | -8.9111e-10 | 8.6604e-10 | -1.0448e-10 | 8.9111e-10 | -8.6604e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68873 | 1.0718 | 1.1034 | 0.68873 | 1.0718 | 1.1034 | -2.1554 | -108.1041 | 108.7785 | -2.1554 | -108.1041 | 108.7785
Line9_3_11 | 0.41049 | 0.2117 | 0.24135 | 0.41049 | 0.2117 | 0.24135 | 0.094798 | 0.048889 | 0.055737 | 0.094798 | 0.048889 | 0.055737 | -0.0097772 | 0.030993 | -0.050687 | 0.011462 | -0.030545 | 0.05127 | -0.056029 | -0.040919 | -0.029793 | 0.059399 | 0.041815 | 0.030958 | 100.1477 | -53.0058 | -103.1878 | -79.8523 | 126.9942 | 76.8122 |  | 0.59997 | 1.05 | 1.0549 | 0.63815 | 1.0592 | 1.0745 | 0.24916 | -105.864 | 107.2583 | -0.77434 | -106.8581 | 107.9367

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11644 | 0.11463 | 0.11188 | 0.11644 | 0.11463 | 0.11188 | 0.02689 | 0.026473 | 0.025837 | 0.02689 | 0.026473 | 0.025837 | -0.004125 | -0.0027819 | -0.0038375 | 0.0042606 | 0.0029133 | 0.0039626 | -0.030355 | -0.030106 | -0.029386 | 0.030626 | 0.030369 | 0.029636 | 97.5002 | -24.5895 | -142.7356 | -82.4998 | 155.4105 | 37.2644 |  | 1.1392 | 1.1421 | 1.147 | 1.1499 | 1.1524 | 1.1573 | -0.23843 | -119.8688 | 119.8243 | -0.41971 | -120.0691 | 119.6486
Line10_11_12 | 0.10374 | 0.10226 | 0.099631 | 0.10374 | 0.10226 | 0.099631 | 0.023957 | 0.023617 | 0.023009 | 0.023957 | 0.023617 | 0.023009 | -0.0038183 | -0.0025877 | -0.0034999 | 0.0039259 | 0.0026923 | 0.0035992 | -0.027484 | -0.027285 | -0.026581 | 0.027699 | 0.027494 | 0.02678 | 97.3478 | -24.8095 | -142.9895 | -82.6522 | 155.1905 | 37.0105 |  | 1.1583 | 1.1605 | 1.1652 | 1.1678 | 1.1698 | 1.1744 | -0.56161 | -120.2272 | 119.5095 | -0.71925 | -120.4022 | 119.3558
Line11_12_13 | 0.10374 | 0.10226 | 0.099631 | 0.10374 | 0.10226 | 0.099631 | 0.023957 | 0.023617 | 0.023009 | 0.023957 | 0.023617 | 0.023009 | -0.0039259 | -0.0026923 | -0.0035992 | 0.0040335 | 0.0027968 | 0.0036985 | -0.027699 | -0.027494 | -0.02678 | 0.027914 | 0.027703 | 0.026978 | 97.3478 | -24.8095 | -142.9895 | -82.6522 | 155.1905 | 37.0105 |  | 1.1678 | 1.1698 | 1.1744 | 1.1773 | 1.179 | 1.1835 | -0.71925 | -120.4022 | 119.3558 | -0.87433 | -120.5744 | 119.2045
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0028e-09 | 1.0253e-09 | 1.0883e-09 | -1.0028e-09 | -1.0253e-09 | -1.0883e-09 | 2.1738e-10 | 1.4302e-10 | 1.9883e-10 | -2.1738e-10 | -1.4302e-10 | -1.9883e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1773 | 1.179 | 1.1835 | 1.1773 | 1.179 | 1.1835 | -0.87433 | -120.5744 | 119.2045 | -0.87433 | -120.5744 | 119.2045
Line13_13_14 | 0.10374 | 0.10226 | 0.099631 | 0.10374 | 0.10226 | 0.099631 | 0.023957 | 0.023617 | 0.023009 | 0.023957 | 0.023617 | 0.023009 | -0.0040335 | -0.0027968 | -0.0036985 | 0.0041411 | 0.0029014 | 0.0037977 | -0.027914 | -0.027703 | -0.026978 | 0.02813 | 0.027912 | 0.027177 | 97.3478 | -24.8095 | -142.9895 | -82.6522 | 155.1905 | 37.0105 |  | 1.1773 | 1.179 | 1.1835 | 1.1868 | 1.1883 | 1.1926 | -0.87433 | -120.5744 | 119.2045 | -1.0269 | -120.744 | 119.0554
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6851e-10 | 6.8355e-10 | 7.2554e-10 | -6.6851e-10 | -6.8355e-10 | -7.2554e-10 | 1.4492e-10 | 9.5348e-11 | 1.3255e-10 | -1.4492e-10 | -9.5348e-11 | -1.3255e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1773 | 1.179 | 1.1835 | 1.1773 | 1.179 | 1.1835 | -0.87433 | -120.5744 | 119.2045 | -0.87433 | -120.5744 | 119.2045
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3426e-10 | 3.4177e-10 | 3.6277e-10 | -3.3426e-10 | -3.4177e-10 | -3.6277e-10 | 7.2459e-11 | 4.7674e-11 | 6.6275e-11 | -7.2459e-11 | -4.7674e-11 | -6.6275e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1773 | 1.179 | 1.1835 | 1.1773 | 1.179 | 1.1835 | -0.87433 | -120.5744 | 119.2045 | -0.87433 | -120.5744 | 119.2045
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1721e-10 | 2.2788e-10 | 2.4957e-10 | -2.1721e-10 | -2.2788e-10 | -2.4957e-10 | 3.5872e-11 | 7.5894e-12 | 3.0384e-11 | -3.5872e-11 | -7.5895e-12 | -3.0384e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1514 | 1.1539 | 1.1587 | 1.1514 | 1.1539 | 1.1587 | -0.44257 | -120.0934 | 119.6275 | -0.44257 | -120.0934 | 119.6275
Line17_5_19 | 0.12402 | 0.122 | 0.1192 | 0.12402 | 0.122 | 0.1192 | 0.02864 | 0.028176 | 0.027527 | 0.02864 | 0.028176 | 0.027527 | -0.0045992 | -0.0031845 | -0.0043125 | 0.004753 | 0.0033333 | 0.0044546 | -0.032632 | -0.032333 | -0.031582 | 0.032939 | 0.03263 | 0.031866 | 97.5921 | -24.4557 | -142.5856 | -82.4079 | 155.5443 | 37.4144 |  | 1.1506 | 1.1531 | 1.1579 | 1.162 | 1.1641 | 1.1689 | -0.43048 | -120.0806 | 119.6386 | -0.61876 | -120.2884 | 119.4564
Line1_1_3 | 0.10374 | 0.10226 | 0.099631 | 0.10374 | 0.10226 | 0.099631 | 0.023957 | 0.023617 | 0.023009 | 0.023957 | 0.023617 | 0.023009 | -0.0036031 | -0.0023785 | -0.0033014 | 0.0037107 | 0.0024831 | 0.0034007 | -0.027053 | -0.026867 | -0.026184 | 0.027269 | 0.027076 | 0.026383 | 97.3478 | -24.8095 | -142.9895 | -82.6522 | 155.1905 | 37.0105 |  | 1.1392 | 1.1421 | 1.147 | 1.1487 | 1.1513 | 1.1561 | -0.23843 | -119.8688 | 119.8243 | -0.40136 | -120.0495 | 119.6657
Line2_1_4 | 0.13264 | 0.13038 | 0.12753 | 0.13264 | 0.13038 | 0.12753 | 0.030631 | 0.030111 | 0.029452 | 0.030631 | 0.030111 | 0.029452 | -0.004818 | -0.0033363 | -0.004561 | 0.004994 | 0.0035062 | 0.0047237 | -0.034562 | -0.034226 | -0.033473 | 0.034914 | 0.034566 | 0.033798 | 97.6976 | -24.3014 | -142.4163 | -82.3024 | 155.6986 | 37.5837 |  | 1.1392 | 1.1421 | 1.147 | 1.1514 | 1.1539 | 1.1587 | -0.23843 | -119.8688 | 119.8243 | -0.44257 | -120.0934 | 119.6275
Line3_1_5 | 0.12402 | 0.122 | 0.1192 | 0.12402 | 0.122 | 0.1192 | 0.02864 | 0.028176 | 0.027527 | 0.02864 | 0.028176 | 0.027527 | -0.0044454 | -0.0030356 | -0.0041705 | 0.0045992 | 0.0031845 | 0.0043125 | -0.032324 | -0.032035 | -0.031298 | 0.032632 | 0.032333 | 0.031582 | 97.5921 | -24.4557 | -142.5856 | -82.4079 | 155.5443 | 37.4144 |  | 1.1392 | 1.1421 | 1.147 | 1.1506 | 1.1531 | 1.1579 | -0.23843 | -119.8688 | 119.8243 | -0.43048 | -120.0806 | 119.6386
Line4_2_6 | 0.11644 | 0.11463 | 0.11188 | 0.11644 | 0.11463 | 0.11188 | 0.02689 | 0.026473 | 0.025837 | 0.02689 | 0.026473 | 0.025837 | -0.0042606 | -0.0029133 | -0.0039626 | 0.0043962 | 0.0030447 | 0.0040878 | -0.030626 | -0.030369 | -0.029636 | 0.030898 | 0.030631 | 0.029887 | 97.5002 | -24.5895 | -142.7356 | -82.4998 | 155.4105 | 37.2644 |  | 1.1499 | 1.1524 | 1.1573 | 1.1606 | 1.1628 | 1.1675 | -0.41971 | -120.0691 | 119.6486 | -0.59764 | -120.2659 | 119.476
Line5_6_7 | 0.11644 | 0.11463 | 0.11188 | 0.11644 | 0.11463 | 0.11188 | 0.02689 | 0.026473 | 0.025837 | 0.02689 | 0.026473 | 0.025837 | -0.0043962 | -0.0030447 | -0.0040878 | 0.0045318 | 0.0031761 | 0.004213 | -0.030898 | -0.030631 | -0.029887 | 0.031169 | 0.030894 | 0.030137 | 97.5002 | -24.5895 | -142.7356 | -82.4998 | 155.4105 | 37.2644 |  | 1.1606 | 1.1628 | 1.1675 | 1.1713 | 1.1732 | 1.1778 | -0.59764 | -120.2659 | 119.476 | -0.77233 | -120.4592 | 119.3064
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1997e-10 | 9.4449e-10 | 1.0086e-09 | -9.1997e-10 | -9.4449e-10 | -1.0086e-09 | 1.9104e-10 | 1.1376e-10 | 1.7252e-10 | -1.9104e-10 | -1.1376e-10 | -1.7252e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1713 | 1.1732 | 1.1778 | 1.1713 | 1.1732 | 1.1778 | -0.77233 | -120.4592 | 119.3064 | -0.77233 | -120.4592 | 119.3064
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0666e-10 | 3.1483e-10 | 3.3621e-10 | -3.0666e-10 | -3.1483e-10 | -3.3621e-10 | 6.368e-11 | 3.792e-11 | 5.7507e-11 | -6.368e-11 | -3.792e-11 | -5.7507e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1713 | 1.1732 | 1.1778 | 1.1713 | 1.1732 | 1.1778 | -0.77233 | -120.4592 | 119.3064 | -0.77233 | -120.4592 | 119.3064
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0666e-10 | 3.1483e-10 | 3.3621e-10 | -3.0666e-10 | -3.1483e-10 | -3.3621e-10 | 6.368e-11 | 3.792e-11 | 5.7507e-11 | -6.368e-11 | -3.792e-11 | -5.7507e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1713 | 1.1732 | 1.1778 | 1.1713 | 1.1732 | 1.1778 | -0.77233 | -120.4592 | 119.3064 | -0.77233 | -120.4592 | 119.3064
Line9_3_11 | 0.10374 | 0.10226 | 0.099631 | 0.10374 | 0.10226 | 0.099631 | 0.023957 | 0.023617 | 0.023009 | 0.023957 | 0.023617 | 0.023009 | -0.0037107 | -0.0024831 | -0.0034007 | 0.0038183 | 0.0025877 | 0.0034999 | -0.027269 | -0.027076 | -0.026383 | 0.027484 | 0.027285 | 0.026581 | 97.3478 | -24.8095 | -142.9895 | -82.6522 | 155.1905 | 37.0105 |  | 1.1487 | 1.1513 | 1.1561 | 1.1583 | 1.1605 | 1.1652 | -0.40136 | -120.0495 | 119.6657 | -0.56161 | -120.2272 | 119.5095

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11706 | 0.11532 | 0.11268 | 0.11706 | 0.11532 | 0.11268 | 0.027035 | 0.026633 | 0.026023 | 0.027035 | 0.026633 | 0.026023 | -0.0041104 | -0.0028106 | -0.0038358 | 0.0042474 | 0.0029436 | 0.0039628 | -0.030591 | -0.030352 | -0.029667 | 0.030865 | 0.030618 | 0.029921 | 97.4171 | -24.5767 | -142.8056 | -82.5829 | 155.4233 | 37.1944 |  | 1.1417 | 1.1445 | 1.1495 | 1.1525 | 1.155 | 1.1598 | -0.23562 | -119.8672 | 119.8271 | -0.41827 | -120.0681 | 119.6499
Line10_11_12 | 0.10473 | 0.1033 | 0.10077 | 0.10473 | 0.1033 | 0.10077 | 0.024186 | 0.023855 | 0.023271 | 0.024186 | 0.023855 | 0.023271 | -0.0038233 | -0.0026281 | -0.0035187 | 0.0039329 | 0.0027348 | 0.0036202 | -0.027816 | -0.027623 | -0.02695 | 0.028035 | 0.027836 | 0.027153 | 97.2637 | -24.7933 | -143.0531 | -82.7363 | 155.2067 | 36.9469 |  | 1.1609 | 1.1632 | 1.1679 | 1.1705 | 1.1725 | 1.1771 | -0.56257 | -120.2281 | 119.5084 | -0.72202 | -120.4043 | 119.3528
Line11_12_13 | 0.10473 | 0.1033 | 0.10077 | 0.10473 | 0.1033 | 0.10077 | 0.024186 | 0.023855 | 0.023271 | 0.024186 | 0.023855 | 0.023271 | -0.0039329 | -0.0027348 | -0.0036202 | 0.0040426 | 0.0028415 | 0.0037217 | -0.028035 | -0.027836 | -0.027153 | 0.028254 | 0.02805 | 0.027357 | 97.2637 | -24.7933 | -143.0531 | -82.7363 | 155.2067 | 36.9469 |  | 1.1705 | 1.1725 | 1.1771 | 1.1801 | 1.1819 | 1.1864 | -0.72202 | -120.4043 | 119.3528 | -0.87888 | -120.5777 | 119.1996
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0419e-09 | 1.0649e-09 | 1.1285e-09 | -1.0419e-09 | -1.0649e-09 | -1.1285e-09 | 2.1903e-10 | 1.4419e-10 | 2.0052e-10 | -2.1903e-10 | -1.4419e-10 | -2.0052e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1801 | 1.1819 | 1.1864 | 1.1801 | 1.1819 | 1.1864 | -0.87888 | -120.5777 | 119.1996 | -0.87888 | -120.5777 | 119.1996
Line13_13_14 | 0.10473 | 0.1033 | 0.10077 | 0.10473 | 0.1033 | 0.10077 | 0.024186 | 0.023855 | 0.023271 | 0.024186 | 0.023855 | 0.023271 | -0.0040426 | -0.0028415 | -0.0037217 | 0.0041523 | 0.0029482 | 0.0038233 | -0.028254 | -0.02805 | -0.027357 | 0.028474 | 0.028263 | 0.02756 | 97.2637 | -24.7933 | -143.0531 | -82.7363 | 155.2067 | 36.9469 |  | 1.1801 | 1.1819 | 1.1864 | 1.1898 | 1.1912 | 1.1956 | -0.87888 | -120.5777 | 119.1996 | -1.0332 | -120.7484 | 119.0488
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9461e-10 | 7.0994e-10 | 7.5234e-10 | -6.9461e-10 | -7.0994e-10 | -7.5234e-10 | 1.4602e-10 | 9.6126e-11 | 1.3368e-10 | -1.4602e-10 | -9.6126e-11 | -1.3368e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1801 | 1.1819 | 1.1864 | 1.1801 | 1.1819 | 1.1864 | -0.87888 | -120.5777 | 119.1996 | -0.87888 | -120.5777 | 119.1996
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.473e-10 | 3.5497e-10 | 3.7617e-10 | -3.473e-10 | -3.5497e-10 | -3.7617e-10 | 7.301e-11 | 4.8063e-11 | 6.6841e-11 | -7.3011e-11 | -4.8063e-11 | -6.6841e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1801 | 1.1819 | 1.1864 | 1.1801 | 1.1819 | 1.1864 | -0.87888 | -120.5777 | 119.1996 | -0.87888 | -120.5777 | 119.1996
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2816e-10 | 2.3892e-10 | 2.6071e-10 | -2.2816e-10 | -2.3892e-10 | -2.6071e-10 | 3.5761e-11 | 7.4446e-12 | 3.0286e-11 | -3.5761e-11 | -7.4446e-12 | -3.0286e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1539 | 1.1563 | 1.1612 | 1.1539 | 1.1563 | 1.1612 | -0.44026 | -120.0915 | 119.6295 | -0.44026 | -120.0915 | 119.6295
Line17_5_19 | 0.12438 | 0.12244 | 0.11976 | 0.12438 | 0.12244 | 0.11976 | 0.028724 | 0.028277 | 0.027657 | 0.028724 | 0.028277 | 0.027657 | -0.0045739 | -0.0032076 | -0.0043001 | 0.0047286 | 0.0033575 | 0.0044435 | -0.032805 | -0.03252 | -0.031805 | 0.033114 | 0.03282 | 0.032092 | 97.5089 | -24.446 | -142.6601 | -82.4911 | 155.554 | 37.3399 |  | 1.1531 | 1.1556 | 1.1605 | 1.1645 | 1.1667 | 1.1714 | -0.42866 | -120.0792 | 119.6402 | -0.61791 | -120.2872 | 119.4568
Line1_1_3 | 0.10473 | 0.1033 | 0.10077 | 0.10473 | 0.1033 | 0.10077 | 0.024186 | 0.023855 | 0.023271 | 0.024186 | 0.023855 | 0.023271 | -0.0036039 | -0.0024147 | -0.0033156 | 0.0037136 | 0.0025214 | 0.0034171 | -0.027377 | -0.027196 | -0.026544 | 0.027596 | 0.02741 | 0.026747 | 97.2637 | -24.7933 | -143.0531 | -82.7363 | 155.2067 | 36.9469 |  | 1.1417 | 1.1445 | 1.1495 | 1.1513 | 1.1539 | 1.1587 | -0.23562 | -119.8672 | 119.8271 | -0.40046 | -120.0491 | 119.6665
Line2_1_4 | 0.13265 | 0.1305 | 0.12777 | 0.13265 | 0.1305 | 0.12777 | 0.030635 | 0.030137 | 0.029508 | 0.030635 | 0.030137 | 0.029508 | -0.0047767 | -0.0033485 | -0.0045307 | 0.0049526 | 0.0035188 | 0.004694 | -0.034649 | -0.03433 | -0.033615 | 0.035 | 0.034671 | 0.033941 | 97.6137 | -24.2962 | -142.4966 | -82.3863 | 155.7038 | 37.5034 |  | 1.1417 | 1.1445 | 1.1495 | 1.1539 | 1.1563 | 1.1612 | -0.23562 | -119.8672 | 119.8271 | -0.44026 | -120.0915 | 119.6295
Line3_1_5 | 0.12438 | 0.12244 | 0.11976 | 0.12438 | 0.12244 | 0.11976 | 0.028724 | 0.028277 | 0.027657 | 0.028724 | 0.028277 | 0.027657 | -0.0044192 | -0.0030577 | -0.0041567 | 0.0045739 | 0.0032076 | 0.0043001 | -0.032495 | -0.03222 | -0.031519 | 0.032805 | 0.03252 | 0.031805 | 97.5089 | -24.446 | -142.6601 | -82.4911 | 155.554 | 37.3399 |  | 1.1417 | 1.1445 | 1.1495 | 1.1531 | 1.1556 | 1.1605 | -0.23562 | -119.8672 | 119.8271 | -0.42866 | -120.0792 | 119.6402
Line4_2_6 | 0.11706 | 0.11532 | 0.11268 | 0.11706 | 0.11532 | 0.11268 | 0.027035 | 0.026633 | 0.026023 | 0.027035 | 0.026633 | 0.026023 | -0.0042474 | -0.0029436 | -0.0039628 | 0.0043844 | 0.0030766 | 0.0040898 | -0.030865 | -0.030618 | -0.029921 | 0.031139 | 0.030884 | 0.030175 | 97.4171 | -24.5767 | -142.8056 | -82.5829 | 155.4233 | 37.1944 |  | 1.1525 | 1.155 | 1.1598 | 1.1632 | 1.1654 | 1.1701 | -0.41827 | -120.0681 | 119.6499 | -0.59754 | -120.2655 | 119.4758
Line5_6_7 | 0.11706 | 0.11532 | 0.11268 | 0.11706 | 0.11532 | 0.11268 | 0.027035 | 0.026633 | 0.026023 | 0.027035 | 0.026633 | 0.026023 | -0.0043844 | -0.0030766 | -0.0040898 | 0.0045215 | 0.0032096 | 0.0042168 | -0.031139 | -0.030884 | -0.030175 | 0.031413 | 0.03115 | 0.030429 | 97.4171 | -24.5767 | -142.8056 | -82.5829 | 155.4233 | 37.1944 |  | 1.1632 | 1.1654 | 1.1701 | 1.1739 | 1.1758 | 1.1805 | -0.59754 | -120.2655 | 119.4758 | -0.77354 | -120.4594 | 119.3047
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5614e-10 | 9.8112e-10 | 1.0458e-09 | -9.5614e-10 | -9.8112e-10 | -1.0458e-09 | 1.9177e-10 | 1.1408e-10 | 1.7333e-10 | -1.9177e-10 | -1.1408e-10 | -1.7333e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1739 | 1.1758 | 1.1805 | 1.1739 | 1.1758 | 1.1805 | -0.77354 | -120.4594 | 119.3047 | -0.77354 | -120.4594 | 119.3047
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1871e-10 | 3.2704e-10 | 3.4859e-10 | -3.1871e-10 | -3.2704e-10 | -3.4859e-10 | 6.3923e-11 | 3.8027e-11 | 5.7778e-11 | -6.3923e-11 | -3.8027e-11 | -5.7778e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1739 | 1.1758 | 1.1805 | 1.1739 | 1.1758 | 1.1805 | -0.77354 | -120.4594 | 119.3047 | -0.77354 | -120.4594 | 119.3047
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1871e-10 | 3.2704e-10 | 3.4859e-10 | -3.1871e-10 | -3.2704e-10 | -3.4859e-10 | 6.3923e-11 | 3.8027e-11 | 5.7778e-11 | -6.3923e-11 | -3.8027e-11 | -5.7778e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1739 | 1.1758 | 1.1805 | 1.1739 | 1.1758 | 1.1805 | -0.77354 | -120.4594 | 119.3047 | -0.77354 | -120.4594 | 119.3047
Line9_3_11 | 0.10473 | 0.1033 | 0.10077 | 0.10473 | 0.1033 | 0.10077 | 0.024186 | 0.023855 | 0.023271 | 0.024186 | 0.023855 | 0.023271 | -0.0037136 | -0.0025214 | -0.0034171 | 0.0038233 | 0.0026281 | 0.0035187 | -0.027596 | -0.02741 | -0.026747 | 0.027816 | 0.027623 | 0.02695 | 97.2637 | -24.7933 | -143.0531 | -82.7363 | 155.2067 | 36.9469 |  | 1.1513 | 1.1539 | 1.1587 | 1.1609 | 1.1632 | 1.1679 | -0.40046 | -120.0491 | 119.6665 | -0.56257 | -120.2281 | 119.5084

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.010081 | 0.0038204 | 0.0063301 | 0.010081 | 0.0038204 | 0.0063301 | 0.0023281 | 0.00088229 | 0.0014619 | 0.0023281 | 0.00088229 | 0.0014619 | -0.00012272 | 0.00068319 | -0.0012798 | 0.00012467 | -0.00068291 | 0.0012806 | -0.00077607 | -0.00037361 | -0.00016229 | 0.0007781 | 0.0003739 | 0.00016309 | 99.0391 | -72.3141 | -86.167 | -80.9609 | 107.6859 | 93.833 |  | 0.33749 | 0.88256 | 0.88246 | 0.33848 | 0.88244 | 0.88305 | 0.053388 | -100.9866 | 101.0602 | -0.06366 | -101.0154 | 101.0912
Line10_11_12 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00012777 | 0.00068066 | -0.0012773 | 0.00012971 | -0.00068038 | 0.0012781 | -0.00077755 | -0.00037375 | -0.00015994 | 0.00077957 | 0.00037404 | 0.00016073 | 99.1528 | -72.2726 | -86.0149 | -80.8472 | 107.7274 | 93.9851 |  | 0.33948 | 0.88232 | 0.88364 | 0.34047 | 0.8822 | 0.88422 | -0.17866 | -101.044 | 101.1221 | -0.29367 | -101.0727 | 101.153
Line11_12_13 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00012971 | 0.00068038 | -0.0012781 | 0.00013165 | -0.0006801 | 0.0012789 | -0.00077957 | -0.00037404 | -0.00016073 | 0.00078159 | 0.00037433 | 0.00016153 | 99.1527 | -72.2727 | -86.015 | -80.8473 | 107.7273 | 93.985 |  | 0.34047 | 0.8822 | 0.88422 | 0.34147 | 0.88208 | 0.88481 | -0.29367 | -101.0727 | 101.153 | -0.40801 | -101.1014 | 101.1839
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4734e-09 | -6.2107e-10 | -6.0096e-10 | 2.4734e-09 | 6.2107e-10 | 6.0096e-10 | 2.6747e-11 | -3.1427e-09 | 3.1392e-09 | -2.6747e-11 | 3.1427e-09 | -3.1392e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34147 | 0.88208 | 0.88481 | 0.34147 | 0.88208 | 0.88481 | -0.40801 | -101.1014 | 101.1839 | -0.40801 | -101.1014 | 101.1839
Line13_13_14 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00013164 | 0.0006801 | -0.0012789 | 0.00013358 | -0.00067983 | 0.0012796 | -0.00078159 | -0.00037433 | -0.00016153 | 0.00078361 | 0.00037462 | 0.00016233 | 99.1525 | -72.273 | -86.0152 | -80.8475 | 107.727 | 93.9848 |  | 0.34147 | 0.88208 | 0.88481 | 0.34246 | 0.88197 | 0.8854 | -0.40801 | -101.1014 | 101.1839 | -0.52168 | -101.1301 | 101.2147
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.649e-09 | -4.1405e-10 | -4.0064e-10 | 1.649e-09 | 4.1405e-10 | 4.0064e-10 | 1.7832e-11 | -2.0951e-09 | 2.0928e-09 | -1.7832e-11 | 2.0952e-09 | -2.0928e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34147 | 0.88208 | 0.88481 | 0.34147 | 0.88208 | 0.88481 | -0.40801 | -101.1014 | 101.1839 | -0.40801 | -101.1014 | 101.1839
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2448e-10 | -2.0702e-10 | -2.0032e-10 | 8.2448e-10 | 2.0702e-10 | 2.0032e-10 | 8.9158e-12 | -1.0476e-09 | 1.0464e-09 | -8.9158e-12 | 1.0476e-09 | -1.0464e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34147 | 0.88208 | 0.88481 | 0.34147 | 0.88208 | 0.88481 | -0.40801 | -101.1014 | 101.1839 | -0.40801 | -101.1014 | 101.1839
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2101e-10 | -2.0438e-10 | -2.0392e-10 | 8.2101e-10 | 2.0438e-10 | 2.0392e-10 | 1.3939e-12 | -1.0526e-09 | 1.0493e-09 | -1.3938e-12 | 1.0526e-09 | -1.0493e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.33848 | 0.88244 | 0.88305 | 0.33848 | 0.88244 | 0.88305 | -0.064347 | -101.0154 | 101.0912 | -0.064347 | -101.0154 | 101.0912
Line17_5_19 | 0.010096 | 0.0038252 | 0.006341 | 0.010096 | 0.0038252 | 0.006341 | 0.0023316 | 0.0008834 | 0.0014644 | 0.0023316 | 0.0008834 | 0.0014644 | -0.00012408 | 0.0006839 | -0.0012826 | 0.00012604 | -0.00068362 | 0.0012833 | -0.00077939 | -0.00037412 | -0.00016509 | 0.00078143 | 0.00037441 | 0.0001659 | 98.9817 | -72.3352 | -86.2436 | -81.0183 | 107.6648 | 93.7564 |  | 0.33848 | 0.88244 | 0.88305 | 0.33948 | 0.88232 | 0.88365 | -0.064003 | -101.0154 | 101.0912 | -0.18071 | -101.0442 | 101.1221
Line1_1_3 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00012389 | 0.00068122 | -0.0012758 | 0.00012583 | -0.00068094 | 0.0012766 | -0.00077351 | -0.00037317 | -0.00015834 | 0.00077553 | 0.00037347 | 0.00015914 | 99.1529 | -72.2725 | -86.0148 | -80.8471 | 107.7275 | 93.9852 |  | 0.33749 | 0.88256 | 0.88246 | 0.33848 | 0.88244 | 0.88305 | 0.053388 | -100.9866 | 101.0602 | -0.062978 | -101.0153 | 101.0911
Line2_1_4 | 0.010111 | 0.00383 | 0.006352 | 0.010111 | 0.00383 | 0.006352 | 0.0023351 | 0.00088451 | 0.0014669 | 0.0023351 | 0.00088451 | 0.0014669 | -0.00012153 | 0.00068518 | -0.0012838 | 0.00012349 | -0.0006849 | 0.0012846 | -0.00077864 | -0.00037405 | -0.00016629 | 0.00078068 | 0.00037434 | 0.00016709 | 98.9245 | -72.3558 | -86.3202 | -81.0755 | 107.6442 | 93.6798 |  | 0.33749 | 0.88256 | 0.88246 | 0.33848 | 0.88244 | 0.88305 | 0.053388 | -100.9866 | 101.0602 | -0.064347 | -101.0154 | 101.0912
Line3_1_5 | 0.010096 | 0.0038252 | 0.006341 | 0.010096 | 0.0038252 | 0.006341 | 0.0023316 | 0.0008834 | 0.0014644 | 0.0023316 | 0.0008834 | 0.0014644 | -0.00012212 | 0.00068418 | -0.0012818 | 0.00012408 | -0.0006839 | 0.0012826 | -0.00077735 | -0.00037383 | -0.00016429 | 0.00077939 | 0.00037412 | 0.00016509 | 98.9818 | -72.3351 | -86.2436 | -81.0182 | 107.6649 | 93.7564 |  | 0.33749 | 0.88256 | 0.88246 | 0.33848 | 0.88244 | 0.88305 | 0.053388 | -100.9866 | 101.0602 | -0.064003 | -101.0154 | 101.0912
Line4_2_6 | 0.010081 | 0.0038204 | 0.0063301 | 0.010081 | 0.0038204 | 0.0063301 | 0.0023281 | 0.00088229 | 0.0014619 | 0.0023281 | 0.00088229 | 0.0014619 | -0.00012467 | 0.00068291 | -0.0012806 | 0.00012662 | -0.00068263 | 0.0012813 | -0.0007781 | -0.0003739 | -0.00016309 | 0.00078013 | 0.00037419 | 0.0001639 | 99.039 | -72.3141 | -86.167 | -80.961 | 107.6859 | 93.833 |  | 0.33848 | 0.88244 | 0.88305 | 0.33948 | 0.88232 | 0.88364 | -0.06366 | -101.0154 | 101.0912 | -0.18002 | -101.0441 | 101.1221
Line5_6_7 | 0.010081 | 0.0038204 | 0.0063301 | 0.010081 | 0.0038204 | 0.0063301 | 0.0023281 | 0.00088229 | 0.0014619 | 0.0023281 | 0.00088229 | 0.0014619 | -0.00012662 | 0.00068263 | -0.0012813 | 0.00012857 | -0.00068235 | 0.0012821 | -0.00078013 | -0.00037419 | -0.0001639 | 0.00078216 | 0.00037449 | 0.0001647 | 99.039 | -72.3142 | -86.1671 | -80.961 | 107.6858 | 93.8329 |  | 0.33948 | 0.88232 | 0.88364 | 0.34048 | 0.8822 | 0.88423 | -0.18002 | -101.0441 | 101.1221 | -0.2957 | -101.0729 | 101.153
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.47e-09 | -6.1846e-10 | -6.0451e-10 | 2.47e-09 | 6.1846e-10 | 6.0451e-10 | 1.9329e-11 | -3.1477e-09 | 3.1421e-09 | -1.9329e-11 | 3.1477e-09 | -3.1421e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34048 | 0.8822 | 0.88423 | 0.34048 | 0.8822 | 0.88423 | -0.2957 | -101.0729 | 101.153 | -0.2957 | -101.0729 | 101.153
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2334e-10 | -2.0615e-10 | -2.015e-10 | 8.2334e-10 | 2.0615e-10 | 2.015e-10 | 6.443e-12 | -1.0492e-09 | 1.0474e-09 | -6.443e-12 | 1.0492e-09 | -1.0474e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34048 | 0.8822 | 0.88423 | 0.34048 | 0.8822 | 0.88423 | -0.2957 | -101.0729 | 101.153 | -0.2957 | -101.0729 | 101.153
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2334e-10 | -2.0615e-10 | -2.015e-10 | 8.2334e-10 | 2.0615e-10 | 2.015e-10 | 6.443e-12 | -1.0492e-09 | 1.0474e-09 | -6.4429e-12 | 1.0492e-09 | -1.0474e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34048 | 0.8822 | 0.88423 | 0.34048 | 0.8822 | 0.88423 | -0.2957 | -101.0729 | 101.153 | -0.2957 | -101.0729 | 101.153
Line9_3_11 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00012583 | 0.00068094 | -0.0012766 | 0.00012777 | -0.00068066 | 0.0012773 | -0.00077553 | -0.00037346 | -0.00015914 | 0.00077755 | 0.00037375 | 0.00015994 | 99.1529 | -72.2726 | -86.0149 | -80.8471 | 107.7274 | 93.9851 |  | 0.33848 | 0.88244 | 0.88305 | 0.33948 | 0.88232 | 0.88364 | -0.062978 | -101.0153 | 101.0911 | -0.17866 | -101.044 | 101.1221

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.010081 | 0.0038204 | 0.0063301 | 0.010081 | 0.0038204 | 0.0063301 | 0.0023281 | 0.00088229 | 0.0014619 | 0.0023281 | 0.00088229 | 0.0014619 | -0.00012272 | 0.00068319 | -0.0012798 | 0.00012467 | -0.00068291 | 0.0012806 | -0.00077607 | -0.00037361 | -0.00016229 | 0.0007781 | 0.0003739 | 0.00016309 | 99.0391 | -72.3141 | -86.167 | -80.9609 | 107.6859 | 93.833 |  | 0.33749 | 0.88256 | 0.88246 | 0.33848 | 0.88244 | 0.88305 | 0.053388 | -100.9866 | 101.0602 | -0.06366 | -101.0154 | 101.0912
Line10_11_12 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00012777 | 0.00068066 | -0.0012773 | 0.00012971 | -0.00068038 | 0.0012781 | -0.00077755 | -0.00037375 | -0.00015994 | 0.00077957 | 0.00037404 | 0.00016073 | 99.1528 | -72.2726 | -86.0149 | -80.8472 | 107.7274 | 93.9851 |  | 0.33948 | 0.88232 | 0.88364 | 0.34047 | 0.8822 | 0.88422 | -0.17866 | -101.044 | 101.1221 | -0.29367 | -101.0727 | 101.153
Line11_12_13 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00012971 | 0.00068038 | -0.0012781 | 0.00013165 | -0.0006801 | 0.0012789 | -0.00077957 | -0.00037404 | -0.00016073 | 0.00078159 | 0.00037433 | 0.00016153 | 99.1527 | -72.2727 | -86.015 | -80.8473 | 107.7273 | 93.985 |  | 0.34047 | 0.8822 | 0.88422 | 0.34147 | 0.88208 | 0.88481 | -0.29367 | -101.0727 | 101.153 | -0.40801 | -101.1014 | 101.1839
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4734e-09 | -6.2107e-10 | -6.0096e-10 | 2.4734e-09 | 6.2107e-10 | 6.0096e-10 | 2.6747e-11 | -3.1427e-09 | 3.1392e-09 | -2.6747e-11 | 3.1427e-09 | -3.1392e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34147 | 0.88208 | 0.88481 | 0.34147 | 0.88208 | 0.88481 | -0.40801 | -101.1014 | 101.1839 | -0.40801 | -101.1014 | 101.1839
Line13_13_14 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00013164 | 0.0006801 | -0.0012789 | 0.00013358 | -0.00067983 | 0.0012796 | -0.00078159 | -0.00037433 | -0.00016153 | 0.00078361 | 0.00037462 | 0.00016233 | 99.1525 | -72.273 | -86.0152 | -80.8475 | 107.727 | 93.9848 |  | 0.34147 | 0.88208 | 0.88481 | 0.34246 | 0.88197 | 0.8854 | -0.40801 | -101.1014 | 101.1839 | -0.52168 | -101.1301 | 101.2147
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.649e-09 | -4.1405e-10 | -4.0064e-10 | 1.649e-09 | 4.1405e-10 | 4.0064e-10 | 1.7832e-11 | -2.0951e-09 | 2.0928e-09 | -1.7832e-11 | 2.0952e-09 | -2.0928e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34147 | 0.88208 | 0.88481 | 0.34147 | 0.88208 | 0.88481 | -0.40801 | -101.1014 | 101.1839 | -0.40801 | -101.1014 | 101.1839
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2448e-10 | -2.0702e-10 | -2.0032e-10 | 8.2448e-10 | 2.0702e-10 | 2.0032e-10 | 8.9158e-12 | -1.0476e-09 | 1.0464e-09 | -8.9158e-12 | 1.0476e-09 | -1.0464e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34147 | 0.88208 | 0.88481 | 0.34147 | 0.88208 | 0.88481 | -0.40801 | -101.1014 | 101.1839 | -0.40801 | -101.1014 | 101.1839
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2101e-10 | -2.0438e-10 | -2.0392e-10 | 8.2101e-10 | 2.0438e-10 | 2.0392e-10 | 1.3939e-12 | -1.0526e-09 | 1.0493e-09 | -1.3938e-12 | 1.0526e-09 | -1.0493e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.33848 | 0.88244 | 0.88305 | 0.33848 | 0.88244 | 0.88305 | -0.064347 | -101.0154 | 101.0912 | -0.064347 | -101.0154 | 101.0912
Line17_5_19 | 0.010096 | 0.0038252 | 0.006341 | 0.010096 | 0.0038252 | 0.006341 | 0.0023316 | 0.0008834 | 0.0014644 | 0.0023316 | 0.0008834 | 0.0014644 | -0.00012408 | 0.0006839 | -0.0012826 | 0.00012604 | -0.00068362 | 0.0012833 | -0.00077939 | -0.00037412 | -0.00016509 | 0.00078143 | 0.00037441 | 0.0001659 | 98.9817 | -72.3352 | -86.2436 | -81.0183 | 107.6648 | 93.7564 |  | 0.33848 | 0.88244 | 0.88305 | 0.33948 | 0.88232 | 0.88365 | -0.064003 | -101.0154 | 101.0912 | -0.18071 | -101.0442 | 101.1221
Line1_1_3 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00012389 | 0.00068122 | -0.0012758 | 0.00012583 | -0.00068094 | 0.0012766 | -0.00077351 | -0.00037317 | -0.00015834 | 0.00077553 | 0.00037347 | 0.00015914 | 99.1529 | -72.2725 | -86.0148 | -80.8471 | 107.7275 | 93.9852 |  | 0.33749 | 0.88256 | 0.88246 | 0.33848 | 0.88244 | 0.88305 | 0.053388 | -100.9866 | 101.0602 | -0.062978 | -101.0153 | 101.0911
Line2_1_4 | 0.010111 | 0.00383 | 0.006352 | 0.010111 | 0.00383 | 0.006352 | 0.0023351 | 0.00088451 | 0.0014669 | 0.0023351 | 0.00088451 | 0.0014669 | -0.00012153 | 0.00068518 | -0.0012838 | 0.00012349 | -0.0006849 | 0.0012846 | -0.00077864 | -0.00037405 | -0.00016629 | 0.00078068 | 0.00037434 | 0.00016709 | 98.9245 | -72.3558 | -86.3202 | -81.0755 | 107.6442 | 93.6798 |  | 0.33749 | 0.88256 | 0.88246 | 0.33848 | 0.88244 | 0.88305 | 0.053388 | -100.9866 | 101.0602 | -0.064347 | -101.0154 | 101.0912
Line3_1_5 | 0.010096 | 0.0038252 | 0.006341 | 0.010096 | 0.0038252 | 0.006341 | 0.0023316 | 0.0008834 | 0.0014644 | 0.0023316 | 0.0008834 | 0.0014644 | -0.00012212 | 0.00068418 | -0.0012818 | 0.00012408 | -0.0006839 | 0.0012826 | -0.00077735 | -0.00037383 | -0.00016429 | 0.00077939 | 0.00037412 | 0.00016509 | 98.9818 | -72.3351 | -86.2436 | -81.0182 | 107.6649 | 93.7564 |  | 0.33749 | 0.88256 | 0.88246 | 0.33848 | 0.88244 | 0.88305 | 0.053388 | -100.9866 | 101.0602 | -0.064003 | -101.0154 | 101.0912
Line4_2_6 | 0.010081 | 0.0038204 | 0.0063301 | 0.010081 | 0.0038204 | 0.0063301 | 0.0023281 | 0.00088229 | 0.0014619 | 0.0023281 | 0.00088229 | 0.0014619 | -0.00012467 | 0.00068291 | -0.0012806 | 0.00012662 | -0.00068263 | 0.0012813 | -0.0007781 | -0.0003739 | -0.00016309 | 0.00078013 | 0.00037419 | 0.0001639 | 99.039 | -72.3141 | -86.167 | -80.961 | 107.6859 | 93.833 |  | 0.33848 | 0.88244 | 0.88305 | 0.33948 | 0.88232 | 0.88364 | -0.06366 | -101.0154 | 101.0912 | -0.18002 | -101.0441 | 101.1221
Line5_6_7 | 0.010081 | 0.0038204 | 0.0063301 | 0.010081 | 0.0038204 | 0.0063301 | 0.0023281 | 0.00088229 | 0.0014619 | 0.0023281 | 0.00088229 | 0.0014619 | -0.00012662 | 0.00068263 | -0.0012813 | 0.00012857 | -0.00068235 | 0.0012821 | -0.00078013 | -0.00037419 | -0.0001639 | 0.00078216 | 0.00037449 | 0.0001647 | 99.039 | -72.3142 | -86.1671 | -80.961 | 107.6858 | 93.8329 |  | 0.33948 | 0.88232 | 0.88364 | 0.34048 | 0.8822 | 0.88423 | -0.18002 | -101.0441 | 101.1221 | -0.2957 | -101.0729 | 101.153
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.47e-09 | -6.1846e-10 | -6.0451e-10 | 2.47e-09 | 6.1846e-10 | 6.0451e-10 | 1.9329e-11 | -3.1477e-09 | 3.1421e-09 | -1.9329e-11 | 3.1477e-09 | -3.1421e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34048 | 0.8822 | 0.88423 | 0.34048 | 0.8822 | 0.88423 | -0.2957 | -101.0729 | 101.153 | -0.2957 | -101.0729 | 101.153
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2334e-10 | -2.0615e-10 | -2.015e-10 | 8.2334e-10 | 2.0615e-10 | 2.015e-10 | 6.443e-12 | -1.0492e-09 | 1.0474e-09 | -6.443e-12 | 1.0492e-09 | -1.0474e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34048 | 0.8822 | 0.88423 | 0.34048 | 0.8822 | 0.88423 | -0.2957 | -101.0729 | 101.153 | -0.2957 | -101.0729 | 101.153
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.2334e-10 | -2.0615e-10 | -2.015e-10 | 8.2334e-10 | 2.0615e-10 | 2.015e-10 | 6.443e-12 | -1.0492e-09 | 1.0474e-09 | -6.4429e-12 | 1.0492e-09 | -1.0474e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.34048 | 0.8822 | 0.88423 | 0.34048 | 0.8822 | 0.88423 | -0.2957 | -101.0729 | 101.153 | -0.2957 | -101.0729 | 101.153
Line9_3_11 | 0.010051 | 0.0038109 | 0.0063082 | 0.010051 | 0.0038109 | 0.0063082 | 0.0023212 | 0.00088009 | 0.0014568 | 0.0023212 | 0.00088009 | 0.0014568 | -0.00012583 | 0.00068094 | -0.0012766 | 0.00012777 | -0.00068066 | 0.0012773 | -0.00077553 | -0.00037346 | -0.00015914 | 0.00077755 | 0.00037375 | 0.00015994 | 99.1529 | -72.2726 | -86.0149 | -80.8471 | 107.7274 | 93.9851 |  | 0.33848 | 0.88244 | 0.88305 | 0.33948 | 0.88232 | 0.88364 | -0.062978 | -101.0153 | 101.0911 | -0.17866 | -101.044 | 101.1221

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00017578 | 6.6615e-05 | 0.00011037 | 0.00017578 | 6.6615e-05 | 0.00011037 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | -2.9949e-05 | 1.0084e-06 | -2.4877e-05 | 2.9949e-05 | -1.0083e-06 | 2.4877e-05 | -2.6859e-05 | -1.5268e-05 | 5.6593e-06 | 2.686e-05 | 1.5268e-05 | -5.6591e-06 | 137.696 | -33.6571 | -47.51 | -42.304 | 146.3429 | 132.49 |  | 0.991 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41695 | -119.8784 | 119.6737 | -0.41686 | -119.8787 | 119.6743
Line10_11_12 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9914e-05 | 9.9471e-07 | -2.4776e-05 | 2.9914e-05 | -9.9463e-07 | 2.4777e-05 | -2.6721e-05 | -1.5231e-05 | 5.7051e-06 | 2.6722e-05 | 1.5231e-05 | -5.7048e-06 | 137.8098 | -33.6157 | -47.358 | -42.1902 | 146.3843 | 132.642 |  | 0.99104 | 0.99463 | 1.0009 | 0.99106 | 0.99463 | 1.0009 | -0.41677 | -119.879 | 119.675 | -0.41667 | -119.8794 | 119.6756
Line11_12_13 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9914e-05 | 9.9465e-07 | -2.4777e-05 | 2.9915e-05 | -9.9456e-07 | 2.4777e-05 | -2.6722e-05 | -1.5231e-05 | 5.7048e-06 | 2.6722e-05 | 1.5231e-05 | -5.7046e-06 | 137.8097 | -33.6158 | -47.358 | -42.1903 | 146.3842 | 132.642 |  | 0.99106 | 0.99463 | 1.0009 | 0.99109 | 0.99464 | 1.0009 | -0.41667 | -119.8794 | 119.6756 | -0.41658 | -119.8797 | 119.6763
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.6893e-11 | -5.8648e-11 | 1.0217e-11 | 9.6893e-11 | 5.8648e-11 | -1.0217e-11 | 7.9264e-11 | -2.2967e-11 | 6.2209e-11 | -7.9264e-11 | 2.2967e-11 | -6.2209e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99109 | 0.99464 | 1.0009 | 0.99109 | 0.99464 | 1.0009 | -0.41658 | -119.8797 | 119.6763 | -0.41658 | -119.8797 | 119.6763
Line13_13_14 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9915e-05 | 9.9464e-07 | -2.4777e-05 | 2.9915e-05 | -9.9456e-07 | 2.4777e-05 | -2.6722e-05 | -1.5231e-05 | 5.7045e-06 | 2.6723e-05 | 1.5231e-05 | -5.7042e-06 | 137.8095 | -33.6161 | -47.3582 | -42.1905 | 146.3839 | 132.6418 |  | 0.99109 | 0.99464 | 1.0009 | 0.99111 | 0.99464 | 1.0009 | -0.41658 | -119.8797 | 119.6763 | -0.41649 | -119.8801 | 119.6769
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.4595e-11 | -3.9099e-11 | 6.8115e-12 | 6.4595e-11 | 3.9099e-11 | -6.8115e-12 | 5.2843e-11 | -1.5312e-11 | 4.1473e-11 | -5.2843e-11 | 1.5312e-11 | -4.1473e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99109 | 0.99464 | 1.0009 | 0.99109 | 0.99464 | 1.0009 | -0.41658 | -119.8797 | 119.6763 | -0.41658 | -119.8797 | 119.6763
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2298e-11 | -1.9549e-11 | 3.4058e-12 | 3.2298e-11 | 1.9549e-11 | -3.4058e-12 | 2.6421e-11 | -7.6558e-12 | 2.0736e-11 | -2.6421e-11 | 7.6558e-12 | -2.0736e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99109 | 0.99464 | 1.0009 | 0.99109 | 0.99464 | 1.0009 | -0.41658 | -119.8797 | 119.6763 | -0.41658 | -119.8797 | 119.6763
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2524e-11 | -1.9608e-11 | 3.3322e-12 | 3.2524e-11 | 1.9608e-11 | -3.3322e-12 | 2.6438e-11 | -7.7203e-12 | 2.0861e-11 | -2.6438e-11 | 7.7203e-12 | -2.0861e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99102 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41686 | -119.8787 | 119.6743 | -0.41686 | -119.8787 | 119.6743
Line17_5_19 | 0.00017604 | 6.6698e-05 | 0.00011057 | 0.00017604 | 6.6698e-05 | 0.00011057 | 4.0655e-05 | 1.5403e-05 | 2.5534e-05 | 4.0655e-05 | 1.5403e-05 | 2.5534e-05 | -2.9967e-05 | 1.0152e-06 | -2.4928e-05 | 2.9968e-05 | -1.0151e-06 | 2.4928e-05 | -2.693e-05 | -1.5287e-05 | 5.6355e-06 | 2.6931e-05 | 1.5287e-05 | -5.6353e-06 | 137.6386 | -33.6782 | -47.5867 | -42.3614 | 146.3218 | 132.4133 |  | 0.99102 | 0.99462 | 1.0009 | 0.99104 | 0.99463 | 1.0009 | -0.41686 | -119.8787 | 119.6743 | -0.41677 | -119.879 | 119.675
Line1_1_3 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9913e-05 | 9.9484e-07 | -2.4776e-05 | 2.9913e-05 | -9.9476e-07 | 2.4776e-05 | -2.672e-05 | -1.5231e-05 | 5.7056e-06 | 2.672e-05 | 1.5231e-05 | -5.7053e-06 | 137.8099 | -33.6155 | -47.3579 | -42.1901 | 146.3845 | 132.6421 |  | 0.991 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41695 | -119.8784 | 119.6737 | -0.41686 | -119.8787 | 119.6743
Line2_1_4 | 0.0001763 | 6.6782e-05 | 0.00011076 | 0.0001763 | 6.6782e-05 | 0.00011076 | 4.0716e-05 | 1.5423e-05 | 2.5578e-05 | 4.0716e-05 | 1.5423e-05 | 2.5578e-05 | -2.9985e-05 | 1.0221e-06 | -2.4978e-05 | 2.9985e-05 | -1.022e-06 | 2.4978e-05 | -2.7e-05 | -1.5306e-05 | 5.6122e-06 | 2.7e-05 | 1.5306e-05 | -5.6119e-06 | 137.5814 | -33.6989 | -47.6632 | -42.4186 | 146.3011 | 132.3368 |  | 0.991 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41695 | -119.8784 | 119.6737 | -0.41686 | -119.8787 | 119.6743
Line3_1_5 | 0.00017604 | 6.6698e-05 | 0.00011057 | 0.00017604 | 6.6698e-05 | 0.00011057 | 4.0655e-05 | 1.5403e-05 | 2.5534e-05 | 4.0655e-05 | 1.5403e-05 | 2.5534e-05 | -2.9967e-05 | 1.0153e-06 | -2.4927e-05 | 2.9967e-05 | -1.0152e-06 | 2.4928e-05 | -2.6929e-05 | -1.5287e-05 | 5.6358e-06 | 2.693e-05 | 1.5287e-05 | -5.6356e-06 | 137.6387 | -33.6781 | -47.5866 | -42.3613 | 146.3219 | 132.4134 |  | 0.991 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41695 | -119.8784 | 119.6737 | -0.41686 | -119.8787 | 119.6743
Line4_2_6 | 0.00017578 | 6.6615e-05 | 0.00011037 | 0.00017578 | 6.6615e-05 | 0.00011037 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | -2.9949e-05 | 1.0083e-06 | -2.4877e-05 | 2.995e-05 | -1.0083e-06 | 2.4877e-05 | -2.686e-05 | -1.5268e-05 | 5.659e-06 | 2.686e-05 | 1.5268e-05 | -5.6588e-06 | 137.696 | -33.6572 | -47.5101 | -42.304 | 146.3428 | 132.4899 |  | 0.99102 | 0.99462 | 1.0009 | 0.99104 | 0.99463 | 1.0009 | -0.41686 | -119.8787 | 119.6743 | -0.41677 | -119.879 | 119.675
Line5_6_7 | 0.00017578 | 6.6615e-05 | 0.00011037 | 0.00017578 | 6.6615e-05 | 0.00011037 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | -2.995e-05 | 1.0083e-06 | -2.4877e-05 | 2.995e-05 | -1.0082e-06 | 2.4877e-05 | -2.686e-05 | -1.5268e-05 | 5.6588e-06 | 2.6861e-05 | 1.5268e-05 | -5.6585e-06 | 137.6959 | -33.6573 | -47.5101 | -42.3041 | 146.3427 | 132.4899 |  | 0.99104 | 0.99463 | 1.0009 | 0.99107 | 0.99463 | 1.0009 | -0.41677 | -119.879 | 119.675 | -0.41668 | -119.8794 | 119.6756
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.7117e-11 | -5.8707e-11 | 1.0145e-11 | 9.7117e-11 | 5.8707e-11 | -1.0145e-11 | 7.9281e-11 | -2.3031e-11 | 6.2333e-11 | -7.9281e-11 | 2.3031e-11 | -6.2333e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99107 | 0.99463 | 1.0009 | 0.99107 | 0.99463 | 1.0009 | -0.41668 | -119.8794 | 119.6756 | -0.41668 | -119.8794 | 119.6756
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2372e-11 | -1.9569e-11 | 3.3817e-12 | 3.2372e-11 | 1.9569e-11 | -3.3817e-12 | 2.6427e-11 | -7.6771e-12 | 2.0778e-11 | -2.6427e-11 | 7.6771e-12 | -2.0778e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99107 | 0.99463 | 1.0009 | 0.99107 | 0.99463 | 1.0009 | -0.41668 | -119.8794 | 119.6756 | -0.41668 | -119.8794 | 119.6756
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2372e-11 | -1.9569e-11 | 3.3817e-12 | 3.2372e-11 | 1.9569e-11 | -3.3817e-12 | 2.6427e-11 | -7.6771e-12 | 2.0778e-11 | -2.6427e-11 | 7.6771e-12 | -2.0778e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99107 | 0.99463 | 1.0009 | 0.99107 | 0.99463 | 1.0009 | -0.41668 | -119.8794 | 119.6756 | -0.41668 | -119.8794 | 119.6756
Line9_3_11 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9913e-05 | 9.9478e-07 | -2.4776e-05 | 2.9914e-05 | -9.9469e-07 | 2.4776e-05 | -2.672e-05 | -1.5231e-05 | 5.7053e-06 | 2.6721e-05 | 1.5231e-05 | -5.7051e-06 | 137.8098 | -33.6156 | -47.3579 | -42.1902 | 146.3844 | 132.6421 |  | 0.99102 | 0.99462 | 1.0009 | 0.99104 | 0.99463 | 1.0009 | -0.41686 | -119.8787 | 119.6743 | -0.41677 | -119.879 | 119.675

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00017578 | 6.6615e-05 | 0.00011037 | 0.00017578 | 6.6615e-05 | 0.00011037 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | -2.9949e-05 | 1.0084e-06 | -2.4877e-05 | 2.9949e-05 | -1.0083e-06 | 2.4877e-05 | -2.6859e-05 | -1.5268e-05 | 5.6593e-06 | 2.686e-05 | 1.5268e-05 | -5.6591e-06 | 137.696 | -33.6571 | -47.51 | -42.304 | 146.3429 | 132.49 |  | 0.991 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41695 | -119.8784 | 119.6737 | -0.41686 | -119.8787 | 119.6743
Line10_11_12 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9914e-05 | 9.9471e-07 | -2.4776e-05 | 2.9914e-05 | -9.9463e-07 | 2.4777e-05 | -2.6721e-05 | -1.5231e-05 | 5.7051e-06 | 2.6722e-05 | 1.5231e-05 | -5.7048e-06 | 137.8098 | -33.6157 | -47.358 | -42.1902 | 146.3843 | 132.642 |  | 0.99104 | 0.99463 | 1.0009 | 0.99106 | 0.99463 | 1.0009 | -0.41677 | -119.879 | 119.675 | -0.41667 | -119.8794 | 119.6756
Line11_12_13 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9914e-05 | 9.9465e-07 | -2.4777e-05 | 2.9915e-05 | -9.9456e-07 | 2.4777e-05 | -2.6722e-05 | -1.5231e-05 | 5.7048e-06 | 2.6722e-05 | 1.5231e-05 | -5.7046e-06 | 137.8097 | -33.6158 | -47.358 | -42.1903 | 146.3842 | 132.642 |  | 0.99106 | 0.99463 | 1.0009 | 0.99109 | 0.99464 | 1.0009 | -0.41667 | -119.8794 | 119.6756 | -0.41658 | -119.8797 | 119.6763
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.6893e-11 | -5.8648e-11 | 1.0217e-11 | 9.6893e-11 | 5.8648e-11 | -1.0217e-11 | 7.9264e-11 | -2.2967e-11 | 6.2209e-11 | -7.9264e-11 | 2.2967e-11 | -6.2209e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99109 | 0.99464 | 1.0009 | 0.99109 | 0.99464 | 1.0009 | -0.41658 | -119.8797 | 119.6763 | -0.41658 | -119.8797 | 119.6763
Line13_13_14 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9915e-05 | 9.9464e-07 | -2.4777e-05 | 2.9915e-05 | -9.9456e-07 | 2.4777e-05 | -2.6722e-05 | -1.5231e-05 | 5.7045e-06 | 2.6723e-05 | 1.5231e-05 | -5.7042e-06 | 137.8095 | -33.6161 | -47.3582 | -42.1905 | 146.3839 | 132.6418 |  | 0.99109 | 0.99464 | 1.0009 | 0.99111 | 0.99464 | 1.0009 | -0.41658 | -119.8797 | 119.6763 | -0.41649 | -119.8801 | 119.6769
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.4595e-11 | -3.9099e-11 | 6.8115e-12 | 6.4595e-11 | 3.9099e-11 | -6.8115e-12 | 5.2843e-11 | -1.5312e-11 | 4.1473e-11 | -5.2843e-11 | 1.5312e-11 | -4.1473e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99109 | 0.99464 | 1.0009 | 0.99109 | 0.99464 | 1.0009 | -0.41658 | -119.8797 | 119.6763 | -0.41658 | -119.8797 | 119.6763
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2298e-11 | -1.9549e-11 | 3.4058e-12 | 3.2298e-11 | 1.9549e-11 | -3.4058e-12 | 2.6421e-11 | -7.6558e-12 | 2.0736e-11 | -2.6421e-11 | 7.6558e-12 | -2.0736e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99109 | 0.99464 | 1.0009 | 0.99109 | 0.99464 | 1.0009 | -0.41658 | -119.8797 | 119.6763 | -0.41658 | -119.8797 | 119.6763
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2524e-11 | -1.9608e-11 | 3.3322e-12 | 3.2524e-11 | 1.9608e-11 | -3.3322e-12 | 2.6438e-11 | -7.7203e-12 | 2.0861e-11 | -2.6438e-11 | 7.7203e-12 | -2.0861e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99102 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41686 | -119.8787 | 119.6743 | -0.41686 | -119.8787 | 119.6743
Line17_5_19 | 0.00017604 | 6.6698e-05 | 0.00011057 | 0.00017604 | 6.6698e-05 | 0.00011057 | 4.0655e-05 | 1.5403e-05 | 2.5534e-05 | 4.0655e-05 | 1.5403e-05 | 2.5534e-05 | -2.9967e-05 | 1.0152e-06 | -2.4928e-05 | 2.9968e-05 | -1.0151e-06 | 2.4928e-05 | -2.693e-05 | -1.5287e-05 | 5.6355e-06 | 2.6931e-05 | 1.5287e-05 | -5.6353e-06 | 137.6386 | -33.6782 | -47.5867 | -42.3614 | 146.3218 | 132.4133 |  | 0.99102 | 0.99462 | 1.0009 | 0.99104 | 0.99463 | 1.0009 | -0.41686 | -119.8787 | 119.6743 | -0.41677 | -119.879 | 119.675
Line1_1_3 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9913e-05 | 9.9484e-07 | -2.4776e-05 | 2.9913e-05 | -9.9476e-07 | 2.4776e-05 | -2.672e-05 | -1.5231e-05 | 5.7056e-06 | 2.672e-05 | 1.5231e-05 | -5.7053e-06 | 137.8099 | -33.6155 | -47.3579 | -42.1901 | 146.3845 | 132.6421 |  | 0.991 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41695 | -119.8784 | 119.6737 | -0.41686 | -119.8787 | 119.6743
Line2_1_4 | 0.0001763 | 6.6782e-05 | 0.00011076 | 0.0001763 | 6.6782e-05 | 0.00011076 | 4.0716e-05 | 1.5423e-05 | 2.5578e-05 | 4.0716e-05 | 1.5423e-05 | 2.5578e-05 | -2.9985e-05 | 1.0221e-06 | -2.4978e-05 | 2.9985e-05 | -1.022e-06 | 2.4978e-05 | -2.7e-05 | -1.5306e-05 | 5.6122e-06 | 2.7e-05 | 1.5306e-05 | -5.6119e-06 | 137.5814 | -33.6989 | -47.6632 | -42.4186 | 146.3011 | 132.3368 |  | 0.991 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41695 | -119.8784 | 119.6737 | -0.41686 | -119.8787 | 119.6743
Line3_1_5 | 0.00017604 | 6.6698e-05 | 0.00011057 | 0.00017604 | 6.6698e-05 | 0.00011057 | 4.0655e-05 | 1.5403e-05 | 2.5534e-05 | 4.0655e-05 | 1.5403e-05 | 2.5534e-05 | -2.9967e-05 | 1.0153e-06 | -2.4927e-05 | 2.9967e-05 | -1.0152e-06 | 2.4928e-05 | -2.6929e-05 | -1.5287e-05 | 5.6358e-06 | 2.693e-05 | 1.5287e-05 | -5.6356e-06 | 137.6387 | -33.6781 | -47.5866 | -42.3613 | 146.3219 | 132.4134 |  | 0.991 | 0.99462 | 1.0009 | 0.99102 | 0.99462 | 1.0009 | -0.41695 | -119.8784 | 119.6737 | -0.41686 | -119.8787 | 119.6743
Line4_2_6 | 0.00017578 | 6.6615e-05 | 0.00011037 | 0.00017578 | 6.6615e-05 | 0.00011037 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | -2.9949e-05 | 1.0083e-06 | -2.4877e-05 | 2.995e-05 | -1.0083e-06 | 2.4877e-05 | -2.686e-05 | -1.5268e-05 | 5.659e-06 | 2.686e-05 | 1.5268e-05 | -5.6588e-06 | 137.696 | -33.6572 | -47.5101 | -42.304 | 146.3428 | 132.4899 |  | 0.99102 | 0.99462 | 1.0009 | 0.99104 | 0.99463 | 1.0009 | -0.41686 | -119.8787 | 119.6743 | -0.41677 | -119.879 | 119.675
Line5_6_7 | 0.00017578 | 6.6615e-05 | 0.00011037 | 0.00017578 | 6.6615e-05 | 0.00011037 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | 4.0594e-05 | 1.5384e-05 | 2.549e-05 | -2.995e-05 | 1.0083e-06 | -2.4877e-05 | 2.995e-05 | -1.0082e-06 | 2.4877e-05 | -2.686e-05 | -1.5268e-05 | 5.6588e-06 | 2.6861e-05 | 1.5268e-05 | -5.6585e-06 | 137.6959 | -33.6573 | -47.5101 | -42.3041 | 146.3427 | 132.4899 |  | 0.99104 | 0.99463 | 1.0009 | 0.99107 | 0.99463 | 1.0009 | -0.41677 | -119.879 | 119.675 | -0.41668 | -119.8794 | 119.6756
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.7117e-11 | -5.8707e-11 | 1.0145e-11 | 9.7117e-11 | 5.8707e-11 | -1.0145e-11 | 7.9281e-11 | -2.3031e-11 | 6.2333e-11 | -7.9281e-11 | 2.3031e-11 | -6.2333e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99107 | 0.99463 | 1.0009 | 0.99107 | 0.99463 | 1.0009 | -0.41668 | -119.8794 | 119.6756 | -0.41668 | -119.8794 | 119.6756
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2372e-11 | -1.9569e-11 | 3.3817e-12 | 3.2372e-11 | 1.9569e-11 | -3.3817e-12 | 2.6427e-11 | -7.6771e-12 | 2.0778e-11 | -2.6427e-11 | 7.6771e-12 | -2.0778e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99107 | 0.99463 | 1.0009 | 0.99107 | 0.99463 | 1.0009 | -0.41668 | -119.8794 | 119.6756 | -0.41668 | -119.8794 | 119.6756
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2372e-11 | -1.9569e-11 | 3.3817e-12 | 3.2372e-11 | 1.9569e-11 | -3.3817e-12 | 2.6427e-11 | -7.6771e-12 | 2.0778e-11 | -2.6427e-11 | 7.6771e-12 | -2.0778e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99107 | 0.99463 | 1.0009 | 0.99107 | 0.99463 | 1.0009 | -0.41668 | -119.8794 | 119.6756 | -0.41668 | -119.8794 | 119.6756
Line9_3_11 | 0.00017525 | 6.6449e-05 | 0.00010999 | 0.00017525 | 6.6449e-05 | 0.00010999 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | 4.0473e-05 | 1.5346e-05 | 2.5402e-05 | -2.9913e-05 | 9.9478e-07 | -2.4776e-05 | 2.9914e-05 | -9.9469e-07 | 2.4776e-05 | -2.672e-05 | -1.5231e-05 | 5.7053e-06 | 2.6721e-05 | 1.5231e-05 | -5.7051e-06 | 137.8098 | -33.6156 | -47.3579 | -42.1902 | 146.3844 | 132.6421 |  | 0.99102 | 0.99462 | 1.0009 | 0.99104 | 0.99463 | 1.0009 | -0.41686 | -119.8787 | 119.6743 | -0.41677 | -119.879 | 119.675

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.31517 | 0.60778 | 0.56992 | 0.31517 | 0.60778 | 0.56992 | 0.072786 | 0.14036 | 0.13162 | 0.072786 | 0.14036 | 0.13162 | -0.017496 | -0.054508 | 0.040387 | 0.01849 | 0.058201 | -0.037139 | -0.060148 | -0.038277 | -0.052467 | 0.062134 | 0.045665 | 0.058963 | 108.2366 | -3.8294 | -152.9982 | -71.7634 | 176.1706 | 27.0018 |  | 0.86061 | 0.47452 | 0.50306 | 0.89065 | 0.52705 | 0.52945 | 2.0173 | -148.7519 | 154.5896 | 1.6647 | -145.7119 | 149.2074
Line10_11_12 | 0.27719 | 0.54036 | 0.5123 | 0.27719 | 0.54036 | 0.5123 | 0.064013 | 0.12479 | 0.11831 | 0.064013 | 0.12479 | 0.11831 | -0.016816 | -0.054973 | 0.030474 | 0.017584 | 0.057893 | -0.02785 | -0.056003 | -0.044732 | -0.058101 | 0.057539 | 0.050572 | 0.06335 | 108.1191 | -2.681 | -152.2964 | -71.8809 | 177.319 | 27.7036 |  | 0.91344 | 0.56794 | 0.55455 | 0.9399 | 0.616 | 0.58492 | 1.4058 | -143.5455 | 145.3809 | 1.1259 | -141.5425 | 141.4348
Line11_12_13 | 0.27719 | 0.54036 | 0.5123 | 0.27719 | 0.54036 | 0.5123 | 0.064013 | 0.12479 | 0.11831 | 0.064013 | 0.12479 | 0.11831 | -0.017584 | -0.057893 | 0.02785 | 0.018352 | 0.060813 | -0.025225 | -0.057539 | -0.050572 | -0.06335 | 0.059076 | 0.056412 | 0.068599 | 108.1191 | -2.681 | -152.2964 | -71.8809 | 177.319 | 27.7036 |  | 0.9399 | 0.616 | 0.58492 | 0.96637 | 0.6647 | 0.61779 | 1.1259 | -141.5425 | 141.4348 | 0.86131 | -139.8312 | 137.8933
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4191e-09 | -2.7058e-09 | -2.9154e-09 | 1.4191e-09 | 2.7058e-09 | 2.9154e-09 | -1.7577e-10 | 2.7286e-09 | -2.2967e-09 | 1.7577e-10 | -2.7286e-09 | 2.2967e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96637 | 0.6647 | 0.61779 | 0.96637 | 0.6647 | 0.61779 | 0.86131 | -139.8312 | 137.8933 | 0.86131 | -139.8312 | 137.8933
Line13_13_14 | 0.27719 | 0.54036 | 0.5123 | 0.27719 | 0.54036 | 0.5123 | 0.064013 | 0.12479 | 0.11831 | 0.064013 | 0.12479 | 0.11831 | -0.018352 | -0.060813 | 0.025225 | 0.019121 | 0.063733 | -0.022601 | -0.059076 | -0.056412 | -0.068599 | 0.060612 | 0.062252 | 0.073848 | 108.1191 | -2.681 | -152.2964 | -71.8809 | 177.319 | 27.7036 |  | 0.96637 | 0.6647 | 0.61779 | 0.99287 | 0.71392 | 0.65277 | 0.86131 | -139.8312 | 137.8933 | 0.61083 | -138.3547 | 134.7202
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4609e-10 | -1.8039e-09 | -1.9436e-09 | 9.4609e-10 | 1.8039e-09 | 1.9436e-09 | -1.1718e-10 | 1.819e-09 | -1.5311e-09 | 1.1718e-10 | -1.819e-09 | 1.5311e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96637 | 0.6647 | 0.61779 | 0.96637 | 0.6647 | 0.61779 | 0.86131 | -139.8312 | 137.8933 | 0.86131 | -139.8312 | 137.8933
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7305e-10 | -9.0193e-10 | -9.7179e-10 | 4.7305e-10 | 9.0193e-10 | 9.7179e-10 | -5.8591e-11 | 9.0952e-10 | -7.6557e-10 | 5.8591e-11 | -9.0952e-10 | 7.6557e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96637 | 0.6647 | 0.61779 | 0.96637 | 0.6647 | 0.61779 | 0.86131 | -139.8312 | 137.8933 | 0.86131 | -139.8312 | 137.8933
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.7025e-10 | -8.9811e-10 | -8.4757e-10 | 6.7025e-10 | 8.9811e-10 | 8.4757e-10 | -1.0157e-10 | 9.2933e-10 | -1.025e-09 | 1.0157e-10 | -9.2933e-10 | 1.025e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89542 | 0.53527 | 0.53232 | 0.89542 | 0.53527 | 0.53232 | 1.6116 | -145.4969 | 148.5151 | 1.6116 | -145.4969 | 148.5151
Line17_5_19 | 0.33836 | 0.64794 | 0.60382 | 0.33836 | 0.64794 | 0.60382 | 0.078141 | 0.14964 | 0.13945 | 0.078141 | 0.14964 | 0.13945 | -0.019958 | -0.061819 | 0.039531 | 0.021103 | 0.066018 | -0.035885 | -0.066854 | -0.049889 | -0.06258 | 0.069144 | 0.058285 | 0.069872 | 108.2624 | -4.5092 | -153.3987 | -71.7376 | 175.4908 | 26.6013 |  | 0.89286 | 0.53088 | 0.53081 | 0.92515 | 0.58853 | 0.56328 | 1.6407 | -145.6053 | 148.8817 | 1.2903 | -143.0686 | 143.7858
Line1_1_3 | 0.27719 | 0.54036 | 0.5123 | 0.27719 | 0.54036 | 0.5123 | 0.064013 | 0.12479 | 0.11831 | 0.064013 | 0.12479 | 0.11831 | -0.015279 | -0.049134 | 0.035723 | 0.016047 | 0.052054 | -0.033099 | -0.052929 | -0.033053 | -0.047603 | 0.054466 | 0.038892 | 0.052852 | 108.1191 | -2.681 | -152.2964 | -71.8809 | 177.319 | 27.7036 |  | 0.86061 | 0.47452 | 0.50306 | 0.88701 | 0.5207 | 0.5271 | 2.0173 | -148.7519 | 154.5896 | 1.7025 | -145.9153 | 149.7606
Line2_1_4 | 0.3652 | 0.69353 | 0.64197 | 0.3652 | 0.69353 | 0.64197 | 0.08434 | 0.16016 | 0.14826 | 0.08434 | 0.16016 | 0.14826 | -0.020293 | -0.061075 | 0.046355 | 0.021627 | 0.065884 | -0.042234 | -0.069689 | -0.045234 | -0.058427 | 0.072357 | 0.054853 | 0.06667 | 108.2525 | -5.2765 | -153.8383 | -71.7475 | 174.7235 | 26.1617 |  | 0.86061 | 0.47452 | 0.50306 | 0.89542 | 0.53527 | 0.53232 | 2.0173 | -148.7519 | 154.5896 | 1.6116 | -145.4969 | 148.5151
Line3_1_5 | 0.33836 | 0.64794 | 0.60382 | 0.33836 | 0.64794 | 0.60382 | 0.078141 | 0.14964 | 0.13945 | 0.078141 | 0.14964 | 0.13945 | -0.018813 | -0.057621 | 0.043177 | 0.019958 | 0.061819 | -0.039531 | -0.064564 | -0.041492 | -0.055288 | 0.066854 | 0.049889 | 0.06258 | 108.2624 | -4.5092 | -153.3987 | -71.7376 | 175.4908 | 26.6013 |  | 0.86061 | 0.47452 | 0.50306 | 0.89286 | 0.53088 | 0.53081 | 2.0173 | -148.7519 | 154.5896 | 1.6407 | -145.6053 | 148.8817
Line4_2_6 | 0.31517 | 0.60778 | 0.56992 | 0.31517 | 0.60778 | 0.56992 | 0.072786 | 0.14036 | 0.13162 | 0.072786 | 0.14036 | 0.13162 | -0.01849 | -0.058201 | 0.037139 | 0.019483 | 0.061895 | -0.033891 | -0.062134 | -0.045665 | -0.058963 | 0.064121 | 0.053052 | 0.065459 | 108.2366 | -3.8294 | -152.9982 | -71.7634 | 176.1706 | 27.0018 |  | 0.89065 | 0.52705 | 0.52945 | 0.92071 | 0.58079 | 0.56005 | 1.6647 | -145.7119 | 149.2074 | 1.3352 | -143.2285 | 144.3743
Line5_6_7 | 0.31517 | 0.60778 | 0.56992 | 0.31517 | 0.60778 | 0.56992 | 0.072786 | 0.14036 | 0.13162 | 0.072786 | 0.14036 | 0.13162 | -0.019483 | -0.061895 | 0.033891 | 0.020476 | 0.065589 | -0.030643 | -0.064121 | -0.053052 | -0.065459 | 0.066108 | 0.06044 | 0.071955 | 108.2366 | -3.8294 | -152.9982 | -71.7634 | 176.1706 | 27.0018 |  | 0.92071 | 0.58079 | 0.56005 | 0.95081 | 0.63544 | 0.59421 | 1.3352 | -143.2285 | 144.3743 | 1.0265 | -141.169 | 140.0691
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5585e-09 | -2.7284e-09 | -2.8694e-09 | 1.5585e-09 | 2.7284e-09 | 2.8694e-09 | -2.0611e-10 | 2.7766e-09 | -2.4673e-09 | 2.0611e-10 | -2.7766e-09 | 2.4673e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95081 | 0.63544 | 0.59421 | 0.95081 | 0.63544 | 0.59421 | 1.0265 | -141.169 | 140.0691 | 1.0265 | -141.169 | 140.0691
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.195e-10 | -9.0945e-10 | -9.5647e-10 | 5.195e-10 | 9.0945e-10 | 9.5647e-10 | -6.8702e-11 | 9.2553e-10 | -8.2242e-10 | 6.8702e-11 | -9.2553e-10 | 8.2242e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95081 | 0.63544 | 0.59421 | 0.95081 | 0.63544 | 0.59421 | 1.0265 | -141.169 | 140.0691 | 1.0265 | -141.169 | 140.0691
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.195e-10 | -9.0945e-10 | -9.5647e-10 | 5.195e-10 | 9.0945e-10 | 9.5647e-10 | -6.8702e-11 | 9.2553e-10 | -8.2242e-10 | 6.8702e-11 | -9.2553e-10 | 8.2242e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95081 | 0.63544 | 0.59421 | 0.95081 | 0.63544 | 0.59421 | 1.0265 | -141.169 | 140.0691 | 1.0265 | -141.169 | 140.0691
Line9_3_11 | 0.27719 | 0.54036 | 0.5123 | 0.27719 | 0.54036 | 0.5123 | 0.064013 | 0.12479 | 0.11831 | 0.064013 | 0.12479 | 0.11831 | -0.016047 | -0.052054 | 0.033099 | 0.016816 | 0.054973 | -0.030474 | -0.054466 | -0.038892 | -0.052852 | 0.056003 | 0.044732 | 0.058101 | 108.1191 | -2.681 | -152.2964 | -71.8809 | 177.319 | 27.7036 |  | 0.88701 | 0.5207 | 0.5271 | 0.91344 | 0.56794 | 0.55455 | 1.7025 | -145.9153 | 149.7606 | 1.4058 | -143.5455 | 145.3809

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.30819 | 0.58904 | 0.55259 | 0.30819 | 0.58904 | 0.55259 | 0.071173 | 0.13603 | 0.12761 | 0.071173 | 0.13603 | 0.12761 | -0.01693 | -0.052841 | 0.039118 | 0.01788 | 0.056311 | -0.036064 | -0.059088 | -0.037799 | -0.051325 | 0.060988 | 0.044738 | 0.057432 | 108.0107 | -4.0887 | -152.9746 | -71.9893 | 175.9113 | 27.0254 |  | 0.86361 | 0.47759 | 0.50568 | 0.89296 | 0.52869 | 0.53141 | 2.0223 | -148.5115 | 154.3386 | 1.6708 | -145.6221 | 149.152
Line10_11_12 | 0.27229 | 0.52589 | 0.49862 | 0.27229 | 0.52589 | 0.49862 | 0.062884 | 0.12145 | 0.11515 | 0.062884 | 0.12145 | 0.11515 | -0.016339 | -0.05335 | 0.02978 | 0.01708 | 0.056115 | -0.027293 | -0.055201 | -0.043891 | -0.056668 | 0.056684 | 0.049422 | 0.061641 | 107.8983 | -2.9821 | -152.303 | -72.1017 | 177.0179 | 27.697 |  | 0.91548 | 0.56884 | 0.55593 | 0.94145 | 0.6157 | 0.58542 | 1.4101 | -143.5379 | 145.4195 | 1.1294 | -141.6109 | 141.58
Line11_12_13 | 0.27229 | 0.52589 | 0.49862 | 0.27229 | 0.52589 | 0.49862 | 0.062884 | 0.12145 | 0.11515 | 0.062884 | 0.12145 | 0.11515 | -0.01708 | -0.056115 | 0.027293 | 0.017822 | 0.058881 | -0.024807 | -0.056684 | -0.049422 | -0.061641 | 0.058167 | 0.054953 | 0.066613 | 107.8983 | -2.9821 | -152.303 | -72.1017 | 177.0179 | 27.697 |  | 0.94145 | 0.6157 | 0.58542 | 0.96744 | 0.66317 | 0.61729 | 1.1294 | -141.6109 | 141.58 | 0.86372 | -139.9582 | 138.1227
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4094e-09 | -2.7047e-09 | -2.9072e-09 | 1.4094e-09 | 2.7047e-09 | 2.9072e-09 | -1.7646e-10 | 2.739e-09 | -2.3233e-09 | 1.7646e-10 | -2.739e-09 | 2.3233e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96744 | 0.66317 | 0.61729 | 0.96744 | 0.66317 | 0.61729 | 0.86372 | -139.9582 | 138.1227 | 0.86372 | -139.9582 | 138.1227
Line13_13_14 | 0.27229 | 0.52589 | 0.49862 | 0.27229 | 0.52589 | 0.49862 | 0.062884 | 0.12145 | 0.11515 | 0.062884 | 0.12145 | 0.11515 | -0.017822 | -0.058881 | 0.024807 | 0.018563 | 0.061646 | -0.022321 | -0.058167 | -0.054953 | -0.066613 | 0.05965 | 0.060484 | 0.071586 | 107.8983 | -2.9821 | -152.303 | -72.1017 | 177.0179 | 27.697 |  | 0.96744 | 0.66317 | 0.61729 | 0.99345 | 0.71111 | 0.65118 | 0.86372 | -139.9582 | 138.1227 | 0.61195 | -138.5273 | 135.0149
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.3959e-10 | -1.8031e-09 | -1.9381e-09 | 9.3959e-10 | 1.8031e-09 | 1.9381e-09 | -1.1764e-10 | 1.826e-09 | -1.5489e-09 | 1.1764e-10 | -1.826e-09 | 1.5489e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96744 | 0.66317 | 0.61729 | 0.96744 | 0.66317 | 0.61729 | 0.86372 | -139.9582 | 138.1227 | 0.86372 | -139.9582 | 138.1227
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.6979e-10 | -9.0156e-10 | -9.6905e-10 | 4.6979e-10 | 9.0156e-10 | 9.6905e-10 | -5.8819e-11 | 9.13e-10 | -7.7444e-10 | 5.8819e-11 | -9.13e-10 | 7.7444e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96744 | 0.66317 | 0.61729 | 0.96744 | 0.66317 | 0.61729 | 0.86372 | -139.9582 | 138.1227 | 0.86372 | -139.9582 | 138.1227
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6516e-10 | -8.9895e-10 | -8.4697e-10 | 6.6516e-10 | 8.9895e-10 | 8.4697e-10 | -1.0234e-10 | 9.2876e-10 | -1.0283e-09 | 1.0234e-10 | -9.2876e-10 | 1.0283e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89742 | 0.53632 | 0.5341 | 0.89742 | 0.53632 | 0.5341 | 1.6202 | -145.4266 | 148.5122 | 1.6202 | -145.4266 | 148.5122
Line17_5_19 | 0.32993 | 0.62642 | 0.58415 | 0.32993 | 0.62642 | 0.58415 | 0.076195 | 0.14466 | 0.1349 | 0.076195 | 0.14466 | 0.1349 | -0.019242 | -0.059658 | 0.0383 | 0.020331 | 0.063582 | -0.034887 | -0.065426 | -0.048681 | -0.060805 | 0.067604 | 0.056529 | 0.067629 | 108.0365 | -4.7395 | -153.3556 | -71.9635 | 175.2605 | 26.6444 |  | 0.89503 | 0.53226 | 0.53269 | 0.92649 | 0.5881 | 0.56409 | 1.6478 | -145.525 | 148.8503 | 1.2987 | -143.1001 | 143.9317
Line1_1_3 | 0.27229 | 0.52589 | 0.49862 | 0.27229 | 0.52589 | 0.49862 | 0.062884 | 0.12145 | 0.11515 | 0.062884 | 0.12145 | 0.11515 | -0.014856 | -0.047819 | 0.034752 | 0.015597 | 0.050584 | -0.032266 | -0.052236 | -0.032829 | -0.046723 | 0.053718 | 0.03836 | 0.051696 | 107.8983 | -2.9821 | -152.303 | -72.1017 | 177.0179 | 27.697 |  | 0.86361 | 0.47759 | 0.50568 | 0.88953 | 0.52273 | 0.5292 | 2.0223 | -148.5115 | 154.3386 | 1.7073 | -145.8077 | 149.6675
Line2_1_4 | 0.35496 | 0.66863 | 0.6195 | 0.35496 | 0.66863 | 0.6195 | 0.081974 | 0.15441 | 0.14307 | 0.081974 | 0.15441 | 0.14307 | -0.019522 | -0.058928 | 0.044651 | 0.020782 | 0.063399 | -0.040813 | -0.068048 | -0.04434 | -0.056924 | 0.070568 | 0.053281 | 0.064599 | 108.0297 | -5.4706 | -153.7722 | -71.9703 | 174.5294 | 26.2278 |  | 0.86361 | 0.47759 | 0.50568 | 0.89742 | 0.53632 | 0.5341 | 2.0223 | -148.5115 | 154.3386 | 1.6202 | -145.4266 | 148.5122
Line3_1_5 | 0.32993 | 0.62642 | 0.58415 | 0.32993 | 0.62642 | 0.58415 | 0.076195 | 0.14466 | 0.1349 | 0.076195 | 0.14466 | 0.1349 | -0.018153 | -0.055734 | 0.041712 | 0.019242 | 0.059658 | -0.0383 | -0.063249 | -0.040833 | -0.05398 | 0.065426 | 0.048681 | 0.060805 | 108.0365 | -4.7395 | -153.3556 | -71.9635 | 175.2605 | 26.6444 |  | 0.86361 | 0.47759 | 0.50568 | 0.89503 | 0.53226 | 0.53269 | 2.0223 | -148.5115 | 154.3386 | 1.6478 | -145.525 | 148.8503
Line4_2_6 | 0.30819 | 0.58904 | 0.55259 | 0.30819 | 0.58904 | 0.55259 | 0.071173 | 0.13603 | 0.12761 | 0.071173 | 0.13603 | 0.12761 | -0.01788 | -0.056311 | 0.036064 | 0.01883 | 0.05978 | -0.033011 | -0.060988 | -0.044738 | -0.057432 | 0.062887 | 0.051677 | 0.063539 | 108.0107 | -4.0887 | -152.9746 | -71.9893 | 175.9113 | 27.0254 |  | 0.89296 | 0.52869 | 0.53141 | 0.92234 | 0.58089 | 0.56108 | 1.6708 | -145.6221 | 149.152 | 1.3418 | -143.2468 | 144.4788
Line5_6_7 | 0.30819 | 0.58904 | 0.55259 | 0.30819 | 0.58904 | 0.55259 | 0.071173 | 0.13603 | 0.12761 | 0.071173 | 0.13603 | 0.12761 | -0.01883 | -0.05978 | 0.033011 | 0.01978 | 0.06325 | -0.029957 | -0.062887 | -0.051677 | -0.063539 | 0.064787 | 0.058617 | 0.069646 | 108.0107 | -4.0887 | -152.9746 | -71.9893 | 175.9113 | 27.0254 |  | 0.92234 | 0.58089 | 0.56108 | 0.95175 | 0.63393 | 0.5941 | 1.3418 | -143.2468 | 144.4788 | 1.033 | -141.266 | 140.2995
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5502e-09 | -2.7277e-09 | -2.8596e-09 | 1.5502e-09 | 2.7277e-09 | 2.8596e-09 | -2.0762e-10 | 2.7821e-09 | -2.4939e-09 | 2.0762e-10 | -2.7821e-09 | 2.4939e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95175 | 0.63393 | 0.5941 | 0.95175 | 0.63393 | 0.5941 | 1.033 | -141.266 | 140.2995 | 1.033 | -141.266 | 140.2995
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1673e-10 | -9.0923e-10 | -9.5321e-10 | 5.1673e-10 | 9.0923e-10 | 9.5321e-10 | -6.9207e-11 | 9.2736e-10 | -8.3131e-10 | 6.9207e-11 | -9.2736e-10 | 8.3131e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95175 | 0.63393 | 0.5941 | 0.95175 | 0.63393 | 0.5941 | 1.033 | -141.266 | 140.2995 | 1.033 | -141.266 | 140.2995
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.1673e-10 | -9.0923e-10 | -9.5321e-10 | 5.1673e-10 | 9.0923e-10 | 9.5321e-10 | -6.9207e-11 | 9.2736e-10 | -8.3131e-10 | 6.9207e-11 | -9.2736e-10 | 8.3131e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95175 | 0.63393 | 0.5941 | 0.95175 | 0.63393 | 0.5941 | 1.033 | -141.266 | 140.2995 | 1.033 | -141.266 | 140.2995
Line9_3_11 | 0.27229 | 0.52589 | 0.49862 | 0.27229 | 0.52589 | 0.49862 | 0.062884 | 0.12145 | 0.11515 | 0.062884 | 0.12145 | 0.11515 | -0.015597 | -0.050584 | 0.032266 | 0.016339 | 0.05335 | -0.02978 | -0.053718 | -0.03836 | -0.051696 | 0.055201 | 0.043891 | 0.056668 | 107.8983 | -2.9821 | -152.303 | -72.1017 | 177.0179 | 27.697 |  | 0.88953 | 0.52273 | 0.5292 | 0.91548 | 0.56884 | 0.55593 | 1.7073 | -145.8077 | 149.6675 | 1.4101 | -143.5379 | 145.4195

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1141 | 0.11602 | 0.11866 | 0.1141 | 0.11602 | 0.11866 | 0.026351 | 0.026795 | 0.027404 | 0.026351 | 0.026795 | 0.027404 | -0.003712 | -0.0050536 | -0.0039977 | 0.0038422 | 0.0051882 | 0.0041385 | -0.029881 | -0.030122 | -0.030842 | 0.030142 | 0.030391 | 0.031124 | 96.9986 | -20.9287 | -142.7598 | -83.0014 | 159.0713 | 37.2402 |  | 1.1427 | 1.1399 | 1.1349 | 1.1531 | 1.1506 | 1.1458 | -0.082712 | -120.4527 | 119.8549 | -0.26581 | -120.6166 | 119.6662
Line10_11_12 | 0.10168 | 0.10326 | 0.10578 | 0.10168 | 0.10326 | 0.10578 | 0.023482 | 0.023847 | 0.02443 | 0.023482 | 0.023847 | 0.02443 | -0.0033992 | -0.0046286 | -0.003716 | 0.0035026 | 0.0047352 | 0.0038279 | -0.027056 | -0.027248 | -0.027952 | 0.027263 | 0.027461 | 0.028176 | 96.7502 | -21.1045 | -142.909 | -83.2498 | 158.8955 | 37.091 |  | 1.1612 | 1.159 | 1.1542 | 1.1705 | 1.1686 | 1.1639 | -0.41073 | -120.7452 | 119.5183 | -0.57083 | -120.888 | 119.3543
Line11_12_13 | 0.10168 | 0.10326 | 0.10578 | 0.10168 | 0.10326 | 0.10578 | 0.023482 | 0.023847 | 0.02443 | 0.023482 | 0.023847 | 0.02443 | -0.0035026 | -0.0047352 | -0.0038279 | 0.003606 | 0.0048418 | 0.0039398 | -0.027263 | -0.027461 | -0.028176 | 0.027469 | 0.027674 | 0.0284 | 96.7502 | -21.1045 | -142.909 | -83.2498 | 158.8955 | 37.091 |  | 1.1705 | 1.1686 | 1.1639 | 1.1798 | 1.1781 | 1.1736 | -0.57083 | -120.888 | 119.3543 | -0.72842 | -121.0283 | 119.1929
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0372e-09 | 1.015e-09 | 9.5207e-10 | -1.0372e-09 | -1.015e-09 | -9.5207e-10 | 1.8149e-10 | 2.5584e-10 | 2.0004e-10 | -1.8149e-10 | -2.5584e-10 | -2.0004e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1798 | 1.1781 | 1.1736 | 1.1798 | 1.1781 | 1.1736 | -0.72842 | -121.0283 | 119.1929 | -0.72842 | -121.0283 | 119.1929
Line13_13_14 | 0.10168 | 0.10326 | 0.10578 | 0.10168 | 0.10326 | 0.10578 | 0.023482 | 0.023847 | 0.02443 | 0.023482 | 0.023847 | 0.02443 | -0.003606 | -0.0048418 | -0.0039398 | 0.0037094 | 0.0049485 | 0.0040517 | -0.027469 | -0.027674 | -0.0284 | 0.027676 | 0.027888 | 0.028623 | 96.7502 | -21.1045 | -142.909 | -83.2498 | 158.8955 | 37.091 |  | 1.1798 | 1.1781 | 1.1736 | 1.1891 | 1.1877 | 1.1833 | -0.72842 | -121.0283 | 119.1929 | -0.88353 | -121.1665 | 119.0342
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9143e-10 | 6.7667e-10 | 6.3471e-10 | -6.9143e-10 | -6.7667e-10 | -6.3471e-10 | 1.2099e-10 | 1.7056e-10 | 1.3336e-10 | -1.2099e-10 | -1.7056e-10 | -1.3336e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1798 | 1.1781 | 1.1736 | 1.1798 | 1.1781 | 1.1736 | -0.72842 | -121.0283 | 119.1929 | -0.72842 | -121.0283 | 119.1929
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4572e-10 | 3.3833e-10 | 3.1736e-10 | -3.4572e-10 | -3.3833e-10 | -3.1736e-10 | 6.0496e-11 | 8.5281e-11 | 6.668e-11 | -6.0496e-11 | -8.5281e-11 | -6.668e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1798 | 1.1781 | 1.1736 | 1.1798 | 1.1781 | 1.1736 | -0.72842 | -121.0283 | 119.1929 | -0.72842 | -121.0283 | 119.1929
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3111e-10 | 2.2062e-10 | 1.9895e-10 | -2.3111e-10 | -2.2062e-10 | -1.9895e-10 | 2.3386e-11 | 5.1669e-11 | 2.8874e-11 | -2.3386e-11 | -5.1669e-11 | -2.8874e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1546 | 1.1522 | 1.1473 | 1.1546 | 1.1522 | 1.1473 | -0.28774 | -120.6371 | 119.6425 | -0.28774 | -120.6371 | 119.6425
Line17_5_19 | 0.12152 | 0.12365 | 0.12634 | 0.12152 | 0.12365 | 0.12634 | 0.028064 | 0.028557 | 0.029177 | 0.028064 | 0.028557 | 0.029177 | -0.0041834 | -0.0055969 | -0.0044684 | 0.0043311 | 0.0057498 | 0.004628 | -0.032109 | -0.032399 | -0.03315 | 0.032404 | 0.032705 | 0.03347 | 97.147 | -20.8251 | -142.6684 | -82.853 | 159.1749 | 37.3316 |  | 1.1538 | 1.1513 | 1.1465 | 1.1649 | 1.1628 | 1.158 | -0.27617 | -120.6262 | 119.655 | -0.46594 | -120.7964 | 119.4591
Line1_1_3 | 0.10168 | 0.10326 | 0.10578 | 0.10168 | 0.10326 | 0.10578 | 0.023482 | 0.023847 | 0.02443 | 0.023482 | 0.023847 | 0.02443 | -0.0031924 | -0.0044153 | -0.0034922 | 0.0032958 | 0.004522 | 0.0036041 | -0.026642 | -0.026821 | -0.027504 | 0.026849 | 0.027035 | 0.027728 | 96.7502 | -21.1045 | -142.909 | -83.2498 | 158.8955 | 37.091 |  | 1.1427 | 1.1399 | 1.1349 | 1.152 | 1.1494 | 1.1446 | -0.082712 | -120.4527 | 119.8549 | -0.24804 | -120.6002 | 119.6852
Line2_1_4 | 0.12997 | 0.13235 | 0.13507 | 0.12997 | 0.13235 | 0.13507 | 0.030014 | 0.030564 | 0.031193 | 0.030014 | 0.030564 | 0.031193 | -0.0044163 | -0.0058967 | -0.0046714 | 0.0045852 | 0.0060719 | 0.0048539 | -0.034011 | -0.034337 | -0.035091 | 0.034349 | 0.034687 | 0.035456 | 97.3157 | -20.7083 | -142.5623 | -82.6843 | 159.2917 | 37.4377 |  | 1.1427 | 1.1399 | 1.1349 | 1.1546 | 1.1522 | 1.1473 | -0.082712 | -120.4527 | 119.8549 | -0.28774 | -120.6371 | 119.6425
Line3_1_5 | 0.12152 | 0.12365 | 0.12634 | 0.12152 | 0.12365 | 0.12634 | 0.028064 | 0.028557 | 0.029177 | 0.028064 | 0.028557 | 0.029177 | -0.0040357 | -0.005444 | -0.0043088 | 0.0041834 | 0.0055969 | 0.0044684 | -0.031813 | -0.032093 | -0.032831 | 0.032109 | 0.032399 | 0.03315 | 97.147 | -20.8251 | -142.6684 | -82.853 | 159.1749 | 37.3316 |  | 1.1427 | 1.1399 | 1.1349 | 1.1538 | 1.1513 | 1.1465 | -0.082712 | -120.4527 | 119.8549 | -0.27617 | -120.6262 | 119.655
Line4_2_6 | 0.1141 | 0.11602 | 0.11866 | 0.1141 | 0.11602 | 0.11866 | 0.026351 | 0.026795 | 0.027404 | 0.026351 | 0.026795 | 0.027404 | -0.0038422 | -0.0051882 | -0.0041385 | 0.0039724 | 0.0053228 | 0.0042793 | -0.030142 | -0.030391 | -0.031124 | 0.030402 | 0.03066 | 0.031406 | 96.9986 | -20.9287 | -142.7598 | -83.0014 | 159.0713 | 37.2402 |  | 1.1531 | 1.1506 | 1.1458 | 1.1635 | 1.1614 | 1.1566 | -0.26581 | -120.6166 | 119.6662 | -0.44563 | -120.7775 | 119.481
Line5_6_7 | 0.1141 | 0.11602 | 0.11866 | 0.1141 | 0.11602 | 0.11866 | 0.026351 | 0.026795 | 0.027404 | 0.026351 | 0.026795 | 0.027404 | -0.0039724 | -0.0053228 | -0.0042793 | 0.0041026 | 0.0054575 | 0.0044201 | -0.030402 | -0.03066 | -0.031406 | 0.030662 | 0.03093 | 0.031687 | 96.9986 | -20.9287 | -142.7598 | -83.0014 | 159.0713 | 37.2402 |  | 1.1635 | 1.1614 | 1.1566 | 1.174 | 1.1721 | 1.1675 | -0.44563 | -120.7775 | 119.481 | -0.62225 | -120.9354 | 119.2992
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5622e-10 | 9.3214e-10 | 8.6803e-10 | -9.5622e-10 | -9.3214e-10 | -8.6803e-10 | 1.5427e-10 | 2.3155e-10 | 1.7279e-10 | -1.5427e-10 | -2.3155e-10 | -1.7279e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.174 | 1.1721 | 1.1675 | 1.174 | 1.1721 | 1.1675 | -0.62225 | -120.9354 | 119.2992 | -0.62225 | -120.9354 | 119.2992
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1874e-10 | 3.1071e-10 | 2.8935e-10 | -3.1874e-10 | -3.1071e-10 | -2.8935e-10 | 5.1423e-11 | 7.7183e-11 | 5.7596e-11 | -5.1423e-11 | -7.7183e-11 | -5.7596e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.174 | 1.1721 | 1.1675 | 1.174 | 1.1721 | 1.1675 | -0.62225 | -120.9354 | 119.2992 | -0.62225 | -120.9354 | 119.2992
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1874e-10 | 3.1071e-10 | 2.8935e-10 | -3.1874e-10 | -3.1071e-10 | -2.8935e-10 | 5.1423e-11 | 7.7183e-11 | 5.7596e-11 | -5.1423e-11 | -7.7183e-11 | -5.7596e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.174 | 1.1721 | 1.1675 | 1.174 | 1.1721 | 1.1675 | -0.62225 | -120.9354 | 119.2992 | -0.62225 | -120.9354 | 119.2992
Line9_3_11 | 0.10168 | 0.10326 | 0.10578 | 0.10168 | 0.10326 | 0.10578 | 0.023482 | 0.023847 | 0.02443 | 0.023482 | 0.023847 | 0.02443 | -0.0032958 | -0.004522 | -0.0036041 | 0.0033992 | 0.0046286 | 0.003716 | -0.026849 | -0.027035 | -0.027728 | 0.027056 | 0.027248 | 0.027952 | 96.7502 | -21.1045 | -142.909 | -83.2498 | 158.8955 | 37.091 |  | 1.152 | 1.1494 | 1.1446 | 1.1612 | 1.159 | 1.1542 | -0.24804 | -120.6002 | 119.6852 | -0.41073 | -120.7452 | 119.5183

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11482 | 0.11667 | 0.1192 | 0.11482 | 0.11667 | 0.1192 | 0.026517 | 0.026943 | 0.027528 | 0.026517 | 0.026943 | 0.027528 | -0.0037121 | -0.0050104 | -0.0039849 | 0.003844 | 0.0051465 | 0.0041269 | -0.030138 | -0.030369 | -0.031055 | 0.030402 | 0.030641 | 0.031339 | 96.9416 | -21.0803 | -142.8305 | -83.0584 | 158.9197 | 37.1695 |  | 1.1452 | 1.1424 | 1.1374 | 1.1556 | 1.1532 | 1.1483 | -0.080193 | -120.449 | 119.8575 | -0.26458 | -120.6149 | 119.6676
Line10_11_12 | 0.10274 | 0.10427 | 0.1067 | 0.10274 | 0.10427 | 0.1067 | 0.023727 | 0.02408 | 0.024641 | 0.023727 | 0.02408 | 0.024641 | -0.0034185 | -0.0046125 | -0.0037217 | 0.0035241 | 0.0047212 | 0.0038355 | -0.027404 | -0.02759 | -0.028263 | 0.027615 | 0.027807 | 0.028491 | 96.6989 | -21.2553 | -142.9809 | -83.3011 | 158.7447 | 37.0191 |  | 1.1639 | 1.1617 | 1.1569 | 1.1733 | 1.1713 | 1.1667 | -0.41174 | -120.7463 | 119.5175 | -0.57354 | -120.8913 | 119.3518
Line11_12_13 | 0.10274 | 0.10427 | 0.1067 | 0.10274 | 0.10427 | 0.1067 | 0.023727 | 0.02408 | 0.024641 | 0.023727 | 0.02408 | 0.024641 | -0.0035241 | -0.0047212 | -0.0038355 | 0.0036296 | 0.00483 | 0.0039494 | -0.027615 | -0.027807 | -0.028491 | 0.027826 | 0.028025 | 0.028718 | 96.6989 | -21.2553 | -142.9809 | -83.3011 | 158.7447 | 37.0191 |  | 1.1733 | 1.1713 | 1.1667 | 1.1827 | 1.181 | 1.1764 | -0.57354 | -120.8913 | 119.3518 | -0.73277 | -121.034 | 119.1888
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0768e-09 | 1.0542e-09 | 9.9066e-10 | -1.0768e-09 | -1.0542e-09 | -9.9066e-10 | 1.8301e-10 | 2.5786e-10 | 2.0152e-10 | -1.8301e-10 | -2.5786e-10 | -2.0152e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1827 | 1.181 | 1.1764 | 1.1827 | 1.181 | 1.1764 | -0.73277 | -121.034 | 119.1888 | -0.73277 | -121.034 | 119.1888
Line13_13_14 | 0.10274 | 0.10427 | 0.1067 | 0.10274 | 0.10427 | 0.1067 | 0.023727 | 0.02408 | 0.024641 | 0.023727 | 0.02408 | 0.024641 | -0.0036296 | -0.00483 | -0.0039494 | 0.0037352 | 0.0049387 | 0.0040632 | -0.027826 | -0.028025 | -0.028718 | 0.028037 | 0.028242 | 0.028946 | 96.6989 | -21.2553 | -142.9809 | -83.3011 | 158.7447 | 37.0191 |  | 1.1827 | 1.181 | 1.1764 | 1.1921 | 1.1906 | 1.1862 | -0.73277 | -121.034 | 119.1888 | -0.88949 | -121.1743 | 119.0286
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1787e-10 | 7.028e-10 | 6.6044e-10 | -7.1787e-10 | -7.028e-10 | -6.6044e-10 | 1.2201e-10 | 1.719e-10 | 1.3435e-10 | -1.2201e-10 | -1.719e-10 | -1.3435e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1827 | 1.181 | 1.1764 | 1.1827 | 1.181 | 1.1764 | -0.73277 | -121.034 | 119.1888 | -0.73277 | -121.034 | 119.1888
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5893e-10 | 3.514e-10 | 3.3022e-10 | -3.5893e-10 | -3.514e-10 | -3.3022e-10 | 6.1005e-11 | 8.5952e-11 | 6.7175e-11 | -6.1005e-11 | -8.5952e-11 | -6.7175e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1827 | 1.181 | 1.1764 | 1.1827 | 1.181 | 1.1764 | -0.73277 | -121.034 | 119.1888 | -0.73277 | -121.034 | 119.1888
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4215e-10 | 2.3158e-10 | 2.0981e-10 | -2.4215e-10 | -2.3158e-10 | -2.0981e-10 | 2.3271e-11 | 5.1588e-11 | 2.8746e-11 | -2.3271e-11 | -5.1588e-11 | -2.8746e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1571 | 1.1546 | 1.1497 | 1.1571 | 1.1546 | 1.1497 | -0.28571 | -120.6347 | 119.6448 | -0.28571 | -120.6347 | 119.6448
Line17_5_19 | 0.12199 | 0.12403 | 0.1266 | 0.12199 | 0.12403 | 0.1266 | 0.028171 | 0.028643 | 0.029238 | 0.028171 | 0.028643 | 0.029238 | -0.004173 | -0.0055382 | -0.0044453 | 0.0043218 | 0.005692 | 0.0046056 | -0.032306 | -0.032583 | -0.033298 | 0.032604 | 0.03289 | 0.033618 | 97.0856 | -20.9777 | -142.7391 | -82.9144 | 159.0223 | 37.2609 |  | 1.1563 | 1.1539 | 1.149 | 1.1675 | 1.1653 | 1.1606 | -0.27459 | -120.6243 | 119.6568 | -0.46526 | -120.7961 | 119.4602
Line1_1_3 | 0.10274 | 0.10427 | 0.1067 | 0.10274 | 0.10427 | 0.1067 | 0.023727 | 0.02408 | 0.024641 | 0.023727 | 0.02408 | 0.024641 | -0.0032074 | -0.0043951 | -0.003494 | 0.003313 | 0.0045038 | 0.0036078 | -0.026982 | -0.027155 | -0.027808 | 0.027193 | 0.027372 | 0.028035 | 96.6989 | -21.2553 | -142.9809 | -83.3011 | 158.7447 | 37.0191 |  | 1.1452 | 1.1424 | 1.1374 | 1.1545 | 1.152 | 1.1471 | -0.080193 | -120.449 | 119.8575 | -0.24731 | -120.5989 | 119.686
Line2_1_4 | 0.1301 | 0.13237 | 0.13498 | 0.1301 | 0.13237 | 0.13498 | 0.030045 | 0.03057 | 0.031172 | 0.030045 | 0.03057 | 0.031172 | -0.0043889 | -0.0058158 | -0.0046331 | 0.0045582 | 0.005991 | 0.0048153 | -0.034125 | -0.034434 | -0.03515 | 0.034464 | 0.034784 | 0.035515 | 97.2485 | -20.8624 | -142.6338 | -82.7515 | 159.1376 | 37.3662 |  | 1.1452 | 1.1424 | 1.1374 | 1.1571 | 1.1546 | 1.1497 | -0.080193 | -120.449 | 119.8575 | -0.28571 | -120.6347 | 119.6448
Line3_1_5 | 0.12199 | 0.12403 | 0.1266 | 0.12199 | 0.12403 | 0.1266 | 0.028171 | 0.028643 | 0.029238 | 0.028171 | 0.028643 | 0.029238 | -0.0040242 | -0.0053844 | -0.004285 | 0.004173 | 0.0055382 | 0.0044453 | -0.032009 | -0.032275 | -0.032977 | 0.032306 | 0.032583 | 0.033298 | 97.0856 | -20.9777 | -142.7391 | -82.9144 | 159.0223 | 37.2609 |  | 1.1452 | 1.1424 | 1.1374 | 1.1563 | 1.1539 | 1.149 | -0.080193 | -120.449 | 119.8575 | -0.27459 | -120.6243 | 119.6568
Line4_2_6 | 0.11482 | 0.11667 | 0.1192 | 0.11482 | 0.11667 | 0.1192 | 0.026517 | 0.026943 | 0.027528 | 0.026517 | 0.026943 | 0.027528 | -0.003844 | -0.0051465 | -0.0041269 | 0.0039758 | 0.0052826 | 0.004269 | -0.030402 | -0.030641 | -0.031339 | 0.030665 | 0.030913 | 0.031623 | 96.9416 | -21.0803 | -142.8305 | -83.0584 | 158.9197 | 37.1695 |  | 1.1556 | 1.1532 | 1.1483 | 1.1661 | 1.164 | 1.1592 | -0.26458 | -120.6149 | 119.6676 | -0.44565 | -120.7778 | 119.4813
Line5_6_7 | 0.11482 | 0.11667 | 0.1192 | 0.11482 | 0.11667 | 0.1192 | 0.026517 | 0.026943 | 0.027528 | 0.026517 | 0.026943 | 0.027528 | -0.0039758 | -0.0052826 | -0.004269 | 0.0041076 | 0.0054187 | 0.0044111 | -0.030665 | -0.030913 | -0.031623 | 0.030929 | 0.031185 | 0.031907 | 96.9416 | -21.0803 | -142.8305 | -83.0584 | 158.9197 | 37.1695 |  | 1.1661 | 1.164 | 1.1592 | 1.1766 | 1.1748 | 1.1701 | -0.44565 | -120.7778 | 119.4813 | -0.62348 | -120.9376 | 119.2984
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9286e-10 | 9.6832e-10 | 9.0371e-10 | -9.9286e-10 | -9.6832e-10 | -9.0371e-10 | 1.5493e-10 | 2.3261e-10 | 1.7336e-10 | -1.5493e-10 | -2.3261e-10 | -1.7336e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1766 | 1.1748 | 1.1701 | 1.1766 | 1.1748 | 1.1701 | -0.62348 | -120.9376 | 119.2984 | -0.62348 | -120.9376 | 119.2984
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3095e-10 | 3.2277e-10 | 3.0124e-10 | -3.3095e-10 | -3.2277e-10 | -3.0124e-10 | 5.1642e-11 | 7.7538e-11 | 5.7788e-11 | -5.1642e-11 | -7.7538e-11 | -5.7788e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1766 | 1.1748 | 1.1701 | 1.1766 | 1.1748 | 1.1701 | -0.62348 | -120.9376 | 119.2984 | -0.62348 | -120.9376 | 119.2984
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3095e-10 | 3.2277e-10 | 3.0124e-10 | -3.3095e-10 | -3.2277e-10 | -3.0124e-10 | 5.1642e-11 | 7.7538e-11 | 5.7788e-11 | -5.1642e-11 | -7.7538e-11 | -5.7788e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1766 | 1.1748 | 1.1701 | 1.1766 | 1.1748 | 1.1701 | -0.62348 | -120.9376 | 119.2984 | -0.62348 | -120.9376 | 119.2984
Line9_3_11 | 0.10274 | 0.10427 | 0.1067 | 0.10274 | 0.10427 | 0.1067 | 0.023727 | 0.02408 | 0.024641 | 0.023727 | 0.02408 | 0.024641 | -0.003313 | -0.0045038 | -0.0036078 | 0.0034185 | 0.0046125 | 0.0037217 | -0.027193 | -0.027372 | -0.028035 | 0.027404 | 0.02759 | 0.028263 | 96.6989 | -21.2553 | -142.9809 | -83.3011 | 158.7447 | 37.0191 |  | 1.1545 | 1.152 | 1.1471 | 1.1639 | 1.1617 | 1.1569 | -0.24731 | -120.5989 | 119.686 | -0.41174 | -120.7463 | 119.5175

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00642 | 0.014672 | 0.012819 | 0.00642 | 0.014672 | 0.012819 | 0.0014826 | 0.0033883 | 0.0029603 | 0.0014826 | 0.0033883 | 0.0029603 | -0.00047902 | -0.0011311 | 0.00088871 | 0.00047981 | 0.0011352 | -0.00088556 | -0.00086868 | -2.6919e-05 | -0.00044177 | 0.0008695 | 3.1224e-05 | 0.00044506 | 118.9686 | -0.3197 | -154.4193 | -61.0314 | 179.6803 | 25.5807 |  | 0.66908 | 0.33392 | 0.33525 | 0.66983 | 0.33517 | 0.33479 | 0.094448 | -178.9564 | 179.149 | 0.077433 | -178.7442 | 178.8977
Line10_11_12 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.00048001 | -0.0011356 | 0.00087898 | 0.0004808 | 0.0011397 | -0.00087585 | -0.00086569 | -3.3005e-05 | -0.00044835 | 0.00086651 | 3.7282e-05 | 0.00045162 | 119.0685 | -0.19883 | -154.3277 | -60.9315 | 179.8012 | 25.6723 |  | 0.67056 | 0.33642 | 0.33435 | 0.67131 | 0.33767 | 0.33391 | 0.060825 | -178.5341 | 178.6471 | 0.044069 | -178.3253 | 178.3951
Line11_12_13 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.0004808 | -0.0011397 | 0.00087585 | 0.00048158 | 0.0011438 | -0.00087271 | -0.00086651 | -3.7283e-05 | -0.00045162 | 0.00086733 | 4.1559e-05 | 0.00045488 | 119.0684 | -0.19888 | -154.3278 | -60.9316 | 179.8011 | 25.6722 |  | 0.67131 | 0.33767 | 0.33391 | 0.67205 | 0.33893 | 0.33348 | 0.044069 | -178.3253 | 178.3951 | 0.02735 | -178.118 | 178.1424
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4244e-09 | -7.0554e-10 | -7.1286e-10 | 2.4244e-09 | 7.0554e-10 | 7.1286e-10 | -3.5291e-12 | 3.1658e-09 | -3.1157e-09 | 3.5291e-12 | -3.1658e-09 | 3.1157e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67205 | 0.33893 | 0.33348 | 0.67205 | 0.33893 | 0.33348 | 0.02735 | -178.118 | 178.1424 | 0.02735 | -178.118 | 178.1424
Line13_13_14 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.00048158 | -0.0011438 | 0.00087271 | 0.00048236 | 0.0011479 | -0.00086958 | -0.00086733 | -4.1564e-05 | -0.00045488 | 0.00086815 | 4.584e-05 | 0.00045814 | 119.0683 | -0.19909 | -154.328 | -60.9317 | 179.8009 | 25.672 |  | 0.67205 | 0.33893 | 0.33348 | 0.67279 | 0.34019 | 0.33305 | 0.02735 | -178.118 | 178.1424 | 0.010668 | -177.9123 | 177.8891
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6163e-09 | -4.7036e-10 | -4.7524e-10 | 1.6163e-09 | 4.7036e-10 | 4.7524e-10 | -2.3527e-12 | 2.1105e-09 | -2.0771e-09 | 2.3526e-12 | -2.1105e-09 | 2.0771e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67205 | 0.33893 | 0.33348 | 0.67205 | 0.33893 | 0.33348 | 0.02735 | -178.118 | 178.1424 | 0.02735 | -178.118 | 178.1424
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0813e-10 | -2.3518e-10 | -2.3762e-10 | 8.0813e-10 | 2.3518e-10 | 2.3762e-10 | -1.1763e-12 | 1.0553e-09 | -1.0386e-09 | 1.1763e-12 | -1.0553e-09 | 1.0386e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67205 | 0.33893 | 0.33348 | 0.67205 | 0.33893 | 0.33348 | 0.02735 | -178.118 | 178.1424 | 0.02735 | -178.118 | 178.1424
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1091e-10 | -2.2575e-10 | -2.2316e-10 | 8.1091e-10 | 2.2575e-10 | 2.2316e-10 | -3.3112e-12 | 1.0506e-09 | -1.0511e-09 | 3.3112e-12 | -1.0506e-09 | 1.0511e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.66983 | 0.33518 | 0.33479 | 0.66983 | 0.33518 | 0.33479 | 0.077246 | -178.744 | 178.8971 | 0.077246 | -178.744 | 178.8971
Line17_5_19 | 0.006434 | 0.014696 | 0.012839 | 0.006434 | 0.014696 | 0.012839 | 0.0014859 | 0.0033939 | 0.0029649 | 0.0014859 | 0.0033939 | 0.0029649 | -0.0004801 | -0.0011371 | 0.00088729 | 0.00048089 | 0.0011412 | -0.00088412 | -0.00087183 | -3.2489e-05 | -0.00044504 | 0.00087265 | 3.6809e-05 | 0.00044833 | 118.9181 | -0.3807 | -154.4656 | -61.0819 | 179.6193 | 25.5344 |  | 0.66983 | 0.33518 | 0.33479 | 0.67057 | 0.33644 | 0.33434 | 0.07734 | -178.7441 | 178.8974 | 0.06027 | -178.5334 | 178.6451
Line1_1_3 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.00047845 | -0.0011274 | 0.00088525 | 0.00047923 | 0.0011315 | -0.00088212 | -0.00086406 | -2.4449e-05 | -0.00044182 | 0.00086488 | 2.8726e-05 | 0.00044509 | 119.0686 | -0.19872 | -154.3276 | -60.9314 | 179.8013 | 25.6724 |  | 0.66908 | 0.33392 | 0.33525 | 0.66982 | 0.33517 | 0.3348 | 0.094448 | -178.9564 | 179.149 | 0.077618 | -178.7445 | 178.8984
Line2_1_4 | 0.0064481 | 0.014721 | 0.012859 | 0.0064481 | 0.014721 | 0.012859 | 0.0014891 | 0.0033996 | 0.0029696 | 0.0014891 | 0.0033996 | 0.0029696 | -0.00047958 | -0.0011348 | 0.00089219 | 0.00048038 | 0.001139 | -0.00088902 | -0.00087333 | -2.9422e-05 | -0.00044171 | 0.00087416 | 3.3756e-05 | 0.00044502 | 118.8676 | -0.44156 | -154.5116 | -61.1324 | 179.5584 | 25.4884 |  | 0.66908 | 0.33392 | 0.33525 | 0.66983 | 0.33518 | 0.33479 | 0.094448 | -178.9564 | 179.149 | 0.077246 | -178.744 | 178.8971
Line3_1_5 | 0.006434 | 0.014696 | 0.012839 | 0.006434 | 0.014696 | 0.012839 | 0.0014859 | 0.0033939 | 0.0029649 | 0.0014859 | 0.0033939 | 0.0029649 | -0.0004793 | -0.001133 | 0.00089045 | 0.0004801 | 0.0011371 | -0.00088729 | -0.000871 | -2.8169e-05 | -0.00044174 | 0.00087183 | 3.2488e-05 | 0.00044504 | 118.9181 | -0.38064 | -154.4655 | -61.0819 | 179.6194 | 25.5345 |  | 0.66908 | 0.33392 | 0.33525 | 0.66983 | 0.33518 | 0.33479 | 0.094448 | -178.9564 | 179.149 | 0.07734 | -178.7441 | 178.8974
Line4_2_6 | 0.00642 | 0.014672 | 0.012819 | 0.00642 | 0.014672 | 0.012819 | 0.0014826 | 0.0033883 | 0.0029603 | 0.0014826 | 0.0033883 | 0.0029603 | -0.00047981 | -0.0011352 | 0.00088556 | 0.0004806 | 0.0011394 | -0.0008824 | -0.0008695 | -3.1225e-05 | -0.00044506 | 0.00087032 | 3.5531e-05 | 0.00044834 | 118.9686 | -0.31976 | -154.4193 | -61.0314 | 179.6802 | 25.5807 |  | 0.66983 | 0.33517 | 0.33479 | 0.67057 | 0.33643 | 0.33434 | 0.077433 | -178.7442 | 178.8977 | 0.060456 | -178.5336 | 178.6457
Line5_6_7 | 0.00642 | 0.014672 | 0.012819 | 0.00642 | 0.014672 | 0.012819 | 0.0014826 | 0.0033883 | 0.0029603 | 0.0014826 | 0.0033883 | 0.0029603 | -0.0004806 | -0.0011394 | 0.0008824 | 0.0004814 | 0.0011435 | -0.00087925 | -0.00087032 | -3.5532e-05 | -0.00044834 | 0.00087115 | 3.9837e-05 | 0.00045163 | 118.9685 | -0.31981 | -154.4194 | -61.0315 | 179.6802 | 25.5806 |  | 0.67057 | 0.33643 | 0.33434 | 0.67131 | 0.33769 | 0.3339 | 0.060456 | -178.5336 | 178.6457 | 0.043517 | -178.3246 | 178.3931
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4272e-09 | -6.9617e-10 | -6.9855e-10 | 2.4272e-09 | 6.9617e-10 | 6.9855e-10 | -5.6087e-12 | 3.1613e-09 | -3.1281e-09 | 5.6086e-12 | -3.1613e-09 | 3.1281e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67131 | 0.33769 | 0.3339 | 0.67131 | 0.33769 | 0.3339 | 0.043517 | -178.3246 | 178.3931 | 0.043517 | -178.3246 | 178.3931
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0905e-10 | -2.3206e-10 | -2.3285e-10 | 8.0905e-10 | 2.3206e-10 | 2.3285e-10 | -1.8696e-12 | 1.0538e-09 | -1.0427e-09 | 1.8695e-12 | -1.0538e-09 | 1.0427e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67131 | 0.33769 | 0.3339 | 0.67131 | 0.33769 | 0.3339 | 0.043517 | -178.3246 | 178.3931 | 0.043517 | -178.3246 | 178.3931
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0905e-10 | -2.3206e-10 | -2.3285e-10 | 8.0905e-10 | 2.3206e-10 | 2.3285e-10 | -1.8695e-12 | 1.0538e-09 | -1.0427e-09 | 1.8694e-12 | -1.0538e-09 | 1.0427e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67131 | 0.33769 | 0.3339 | 0.67131 | 0.33769 | 0.3339 | 0.043517 | -178.3246 | 178.3931 | 0.043517 | -178.3246 | 178.3931
Line9_3_11 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.00047923 | -0.0011315 | 0.00088212 | 0.00048001 | 0.0011356 | -0.00087898 | -0.00086488 | -2.8727e-05 | -0.00044509 | 0.00086569 | 3.3004e-05 | 0.00044835 | 119.0685 | -0.19877 | -154.3277 | -60.9315 | 179.8012 | 25.6723 |  | 0.66982 | 0.33517 | 0.3348 | 0.67056 | 0.33642 | 0.33435 | 0.077618 | -178.7445 | 178.8984 | 0.060825 | -178.5341 | 178.6471

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00642 | 0.014672 | 0.012819 | 0.00642 | 0.014672 | 0.012819 | 0.0014826 | 0.0033883 | 0.0029603 | 0.0014826 | 0.0033883 | 0.0029603 | -0.00047902 | -0.0011311 | 0.00088871 | 0.00047981 | 0.0011352 | -0.00088556 | -0.00086868 | -2.6919e-05 | -0.00044177 | 0.0008695 | 3.1224e-05 | 0.00044506 | 118.9686 | -0.3197 | -154.4193 | -61.0314 | 179.6803 | 25.5807 |  | 0.66908 | 0.33392 | 0.33525 | 0.66983 | 0.33517 | 0.33479 | 0.094448 | -178.9564 | 179.149 | 0.077433 | -178.7442 | 178.8977
Line10_11_12 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.00048001 | -0.0011356 | 0.00087898 | 0.0004808 | 0.0011397 | -0.00087585 | -0.00086569 | -3.3005e-05 | -0.00044835 | 0.00086651 | 3.7282e-05 | 0.00045162 | 119.0685 | -0.19883 | -154.3277 | -60.9315 | 179.8012 | 25.6723 |  | 0.67056 | 0.33642 | 0.33435 | 0.67131 | 0.33767 | 0.33391 | 0.060825 | -178.5341 | 178.6471 | 0.044069 | -178.3253 | 178.3951
Line11_12_13 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.0004808 | -0.0011397 | 0.00087585 | 0.00048158 | 0.0011438 | -0.00087271 | -0.00086651 | -3.7283e-05 | -0.00045162 | 0.00086733 | 4.1559e-05 | 0.00045488 | 119.0684 | -0.19888 | -154.3278 | -60.9316 | 179.8011 | 25.6722 |  | 0.67131 | 0.33767 | 0.33391 | 0.67205 | 0.33893 | 0.33348 | 0.044069 | -178.3253 | 178.3951 | 0.02735 | -178.118 | 178.1424
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4244e-09 | -7.0554e-10 | -7.1286e-10 | 2.4244e-09 | 7.0554e-10 | 7.1286e-10 | -3.5291e-12 | 3.1658e-09 | -3.1157e-09 | 3.5291e-12 | -3.1658e-09 | 3.1157e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67205 | 0.33893 | 0.33348 | 0.67205 | 0.33893 | 0.33348 | 0.02735 | -178.118 | 178.1424 | 0.02735 | -178.118 | 178.1424
Line13_13_14 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.00048158 | -0.0011438 | 0.00087271 | 0.00048236 | 0.0011479 | -0.00086958 | -0.00086733 | -4.1564e-05 | -0.00045488 | 0.00086815 | 4.584e-05 | 0.00045814 | 119.0683 | -0.19909 | -154.328 | -60.9317 | 179.8009 | 25.672 |  | 0.67205 | 0.33893 | 0.33348 | 0.67279 | 0.34019 | 0.33305 | 0.02735 | -178.118 | 178.1424 | 0.010668 | -177.9123 | 177.8891
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6163e-09 | -4.7036e-10 | -4.7524e-10 | 1.6163e-09 | 4.7036e-10 | 4.7524e-10 | -2.3527e-12 | 2.1105e-09 | -2.0771e-09 | 2.3526e-12 | -2.1105e-09 | 2.0771e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67205 | 0.33893 | 0.33348 | 0.67205 | 0.33893 | 0.33348 | 0.02735 | -178.118 | 178.1424 | 0.02735 | -178.118 | 178.1424
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0813e-10 | -2.3518e-10 | -2.3762e-10 | 8.0813e-10 | 2.3518e-10 | 2.3762e-10 | -1.1763e-12 | 1.0553e-09 | -1.0386e-09 | 1.1763e-12 | -1.0553e-09 | 1.0386e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67205 | 0.33893 | 0.33348 | 0.67205 | 0.33893 | 0.33348 | 0.02735 | -178.118 | 178.1424 | 0.02735 | -178.118 | 178.1424
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.1091e-10 | -2.2575e-10 | -2.2316e-10 | 8.1091e-10 | 2.2575e-10 | 2.2316e-10 | -3.3112e-12 | 1.0506e-09 | -1.0511e-09 | 3.3112e-12 | -1.0506e-09 | 1.0511e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.66983 | 0.33518 | 0.33479 | 0.66983 | 0.33518 | 0.33479 | 0.077246 | -178.744 | 178.8971 | 0.077246 | -178.744 | 178.8971
Line17_5_19 | 0.006434 | 0.014696 | 0.012839 | 0.006434 | 0.014696 | 0.012839 | 0.0014859 | 0.0033939 | 0.0029649 | 0.0014859 | 0.0033939 | 0.0029649 | -0.0004801 | -0.0011371 | 0.00088729 | 0.00048089 | 0.0011412 | -0.00088412 | -0.00087183 | -3.2489e-05 | -0.00044504 | 0.00087265 | 3.6809e-05 | 0.00044833 | 118.9181 | -0.3807 | -154.4656 | -61.0819 | 179.6193 | 25.5344 |  | 0.66983 | 0.33518 | 0.33479 | 0.67057 | 0.33644 | 0.33434 | 0.07734 | -178.7441 | 178.8974 | 0.06027 | -178.5334 | 178.6451
Line1_1_3 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.00047845 | -0.0011274 | 0.00088525 | 0.00047923 | 0.0011315 | -0.00088212 | -0.00086406 | -2.4449e-05 | -0.00044182 | 0.00086488 | 2.8726e-05 | 0.00044509 | 119.0686 | -0.19872 | -154.3276 | -60.9314 | 179.8013 | 25.6724 |  | 0.66908 | 0.33392 | 0.33525 | 0.66982 | 0.33517 | 0.3348 | 0.094448 | -178.9564 | 179.149 | 0.077618 | -178.7445 | 178.8984
Line2_1_4 | 0.0064481 | 0.014721 | 0.012859 | 0.0064481 | 0.014721 | 0.012859 | 0.0014891 | 0.0033996 | 0.0029696 | 0.0014891 | 0.0033996 | 0.0029696 | -0.00047958 | -0.0011348 | 0.00089219 | 0.00048038 | 0.001139 | -0.00088902 | -0.00087333 | -2.9422e-05 | -0.00044171 | 0.00087416 | 3.3756e-05 | 0.00044502 | 118.8676 | -0.44156 | -154.5116 | -61.1324 | 179.5584 | 25.4884 |  | 0.66908 | 0.33392 | 0.33525 | 0.66983 | 0.33518 | 0.33479 | 0.094448 | -178.9564 | 179.149 | 0.077246 | -178.744 | 178.8971
Line3_1_5 | 0.006434 | 0.014696 | 0.012839 | 0.006434 | 0.014696 | 0.012839 | 0.0014859 | 0.0033939 | 0.0029649 | 0.0014859 | 0.0033939 | 0.0029649 | -0.0004793 | -0.001133 | 0.00089045 | 0.0004801 | 0.0011371 | -0.00088729 | -0.000871 | -2.8169e-05 | -0.00044174 | 0.00087183 | 3.2488e-05 | 0.00044504 | 118.9181 | -0.38064 | -154.4655 | -61.0819 | 179.6194 | 25.5345 |  | 0.66908 | 0.33392 | 0.33525 | 0.66983 | 0.33518 | 0.33479 | 0.094448 | -178.9564 | 179.149 | 0.07734 | -178.7441 | 178.8974
Line4_2_6 | 0.00642 | 0.014672 | 0.012819 | 0.00642 | 0.014672 | 0.012819 | 0.0014826 | 0.0033883 | 0.0029603 | 0.0014826 | 0.0033883 | 0.0029603 | -0.00047981 | -0.0011352 | 0.00088556 | 0.0004806 | 0.0011394 | -0.0008824 | -0.0008695 | -3.1225e-05 | -0.00044506 | 0.00087032 | 3.5531e-05 | 0.00044834 | 118.9686 | -0.31976 | -154.4193 | -61.0314 | 179.6802 | 25.5807 |  | 0.66983 | 0.33517 | 0.33479 | 0.67057 | 0.33643 | 0.33434 | 0.077433 | -178.7442 | 178.8977 | 0.060456 | -178.5336 | 178.6457
Line5_6_7 | 0.00642 | 0.014672 | 0.012819 | 0.00642 | 0.014672 | 0.012819 | 0.0014826 | 0.0033883 | 0.0029603 | 0.0014826 | 0.0033883 | 0.0029603 | -0.0004806 | -0.0011394 | 0.0008824 | 0.0004814 | 0.0011435 | -0.00087925 | -0.00087032 | -3.5532e-05 | -0.00044834 | 0.00087115 | 3.9837e-05 | 0.00045163 | 118.9685 | -0.31981 | -154.4194 | -61.0315 | 179.6802 | 25.5806 |  | 0.67057 | 0.33643 | 0.33434 | 0.67131 | 0.33769 | 0.3339 | 0.060456 | -178.5336 | 178.6457 | 0.043517 | -178.3246 | 178.3931
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4272e-09 | -6.9617e-10 | -6.9855e-10 | 2.4272e-09 | 6.9617e-10 | 6.9855e-10 | -5.6087e-12 | 3.1613e-09 | -3.1281e-09 | 5.6086e-12 | -3.1613e-09 | 3.1281e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67131 | 0.33769 | 0.3339 | 0.67131 | 0.33769 | 0.3339 | 0.043517 | -178.3246 | 178.3931 | 0.043517 | -178.3246 | 178.3931
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0905e-10 | -2.3206e-10 | -2.3285e-10 | 8.0905e-10 | 2.3206e-10 | 2.3285e-10 | -1.8696e-12 | 1.0538e-09 | -1.0427e-09 | 1.8695e-12 | -1.0538e-09 | 1.0427e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67131 | 0.33769 | 0.3339 | 0.67131 | 0.33769 | 0.3339 | 0.043517 | -178.3246 | 178.3931 | 0.043517 | -178.3246 | 178.3931
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.0905e-10 | -2.3206e-10 | -2.3285e-10 | 8.0905e-10 | 2.3206e-10 | 2.3285e-10 | -1.8695e-12 | 1.0538e-09 | -1.0427e-09 | 1.8694e-12 | -1.0538e-09 | 1.0427e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.67131 | 0.33769 | 0.3339 | 0.67131 | 0.33769 | 0.3339 | 0.043517 | -178.3246 | 178.3931 | 0.043517 | -178.3246 | 178.3931
Line9_3_11 | 0.006392 | 0.014623 | 0.012779 | 0.006392 | 0.014623 | 0.012779 | 0.0014762 | 0.0033771 | 0.0029512 | 0.0014762 | 0.0033771 | 0.0029512 | -0.00047923 | -0.0011315 | 0.00088212 | 0.00048001 | 0.0011356 | -0.00087898 | -0.00086488 | -2.8727e-05 | -0.00044509 | 0.00086569 | 3.3004e-05 | 0.00044835 | 119.0685 | -0.19877 | -154.3277 | -60.9315 | 179.8012 | 25.6723 |  | 0.66982 | 0.33517 | 0.3348 | 0.67056 | 0.33642 | 0.33435 | 0.077618 | -178.7445 | 178.8984 | 0.060825 | -178.5341 | 178.6471

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00011194 | 0.00025583 | 0.00022352 | 0.00011194 | 0.00025583 | 0.00022352 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | -2.3833e-05 | -5.4743e-05 | -2.884e-05 | 2.3833e-05 | 5.4744e-05 | 2.8841e-05 | -9.7099e-06 | -2.0923e-05 | -4.1912e-05 | 9.7101e-06 | 2.0924e-05 | 4.1913e-05 | 157.6265 | 38.3373 | -115.7638 | -22.3735 | -141.6627 | 64.2362 |  | 0.99549 | 0.99193 | 0.9856 | 0.9955 | 0.99196 | 0.98563 | -0.20658 | -120.7459 | 119.7035 | -0.20626 | -120.7451 | 119.7033
Line10_11_12 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3746e-05 | -5.4608e-05 | -2.882e-05 | 2.3746e-05 | 5.4609e-05 | 2.8821e-05 | -9.6267e-06 | -2.0741e-05 | -4.1738e-05 | 9.6269e-06 | 2.0742e-05 | 4.1739e-05 | 157.7264 | 38.4582 | -115.6722 | -22.2736 | -141.5418 | 64.3278 |  | 0.99551 | 0.99198 | 0.98566 | 0.99553 | 0.99201 | 0.98568 | -0.20595 | -120.7443 | 119.703 | -0.20563 | -120.7436 | 119.7028
Line11_12_13 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3746e-05 | -5.4609e-05 | -2.8821e-05 | 2.3747e-05 | 5.461e-05 | 2.8822e-05 | -9.6269e-06 | -2.0742e-05 | -4.1739e-05 | 9.6272e-06 | 2.0744e-05 | 4.174e-05 | 157.7264 | 38.4581 | -115.6723 | -22.2736 | -141.5419 | 64.3277 |  | 0.99553 | 0.99201 | 0.98568 | 0.99554 | 0.99204 | 0.98571 | -0.20563 | -120.7436 | 119.7028 | -0.20532 | -120.7428 | 119.7025
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8797e-11 | -8.5955e-11 | -1.5482e-10 | 4.8797e-11 | 8.5955e-11 | 1.5482e-10 | 3.9242e-11 | 1.4147e-10 | 5.6297e-11 | -3.9242e-11 | -1.4147e-10 | -5.6297e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99554 | 0.99204 | 0.98571 | 0.99554 | 0.99204 | 0.98571 | -0.20532 | -120.7428 | 119.7025 | -0.20532 | -120.7428 | 119.7025
Line13_13_14 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3747e-05 | -5.461e-05 | -2.8821e-05 | 2.3747e-05 | 5.4612e-05 | 2.8822e-05 | -9.6272e-06 | -2.0744e-05 | -4.174e-05 | 9.6275e-06 | 2.0745e-05 | 4.1741e-05 | 157.7262 | 38.4579 | -115.6725 | -22.2738 | -141.5421 | 64.3275 |  | 0.99554 | 0.99204 | 0.98571 | 0.99555 | 0.99207 | 0.98573 | -0.20532 | -120.7428 | 119.7025 | -0.205 | -120.7421 | 119.7023
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2531e-11 | -5.7304e-11 | -1.0321e-10 | 3.2531e-11 | 5.7304e-11 | 1.0321e-10 | 2.6161e-11 | 9.4316e-11 | 3.7531e-11 | -2.6161e-11 | -9.4316e-11 | -3.7531e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99554 | 0.99204 | 0.98571 | 0.99554 | 0.99204 | 0.98571 | -0.20532 | -120.7428 | 119.7025 | -0.20532 | -120.7428 | 119.7025
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6266e-11 | -2.8652e-11 | -5.1606e-11 | 1.6266e-11 | 2.8652e-11 | 5.1606e-11 | 1.3081e-11 | 4.7158e-11 | 1.8766e-11 | -1.3081e-11 | -4.7158e-11 | -1.8766e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99554 | 0.99204 | 0.98571 | 0.99554 | 0.99204 | 0.98571 | -0.20532 | -120.7428 | 119.7025 | -0.20532 | -120.7428 | 119.7025
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6398e-11 | -2.8948e-11 | -5.1888e-11 | 1.6398e-11 | 2.8948e-11 | 5.1888e-11 | 1.314e-11 | 4.7298e-11 | 1.8717e-11 | -1.314e-11 | -4.7298e-11 | -1.8717e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9955 | 0.99196 | 0.98563 | 0.9955 | 0.99196 | 0.98563 | -0.20626 | -120.7451 | 119.7033 | -0.20626 | -120.7451 | 119.7033
Line17_5_19 | 0.00011218 | 0.00025626 | 0.00022387 | 0.00011218 | 0.00025626 | 0.00022387 | 2.5908e-05 | 5.918e-05 | 5.17e-05 | 2.5908e-05 | 5.918e-05 | 5.17e-05 | -2.3876e-05 | -5.4813e-05 | -2.8852e-05 | 2.3877e-05 | 5.4814e-05 | 2.8853e-05 | -9.7524e-06 | -2.1017e-05 | -4.2001e-05 | 9.7526e-06 | 2.1019e-05 | 4.2002e-05 | 157.576 | 38.2763 | -115.8101 | -22.424 | -141.7237 | 64.1899 |  | 0.9955 | 0.99196 | 0.98563 | 0.99551 | 0.99198 | 0.98566 | -0.20626 | -120.7451 | 119.7033 | -0.20595 | -120.7443 | 119.703
Line1_1_3 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3746e-05 | -5.4606e-05 | -2.8818e-05 | 2.3746e-05 | 5.4607e-05 | 2.8819e-05 | -9.6262e-06 | -2.0738e-05 | -4.1736e-05 | 9.6264e-06 | 2.074e-05 | 4.1737e-05 | 157.7265 | 38.4583 | -115.6721 | -22.2735 | -141.5417 | 64.3279 |  | 0.99549 | 0.99193 | 0.9856 | 0.9955 | 0.99196 | 0.98563 | -0.20658 | -120.7459 | 119.7035 | -0.20626 | -120.7451 | 119.7033
Line2_1_4 | 0.00011243 | 0.00025668 | 0.00022421 | 0.00011243 | 0.00025668 | 0.00022421 | 2.5965e-05 | 5.9279e-05 | 5.178e-05 | 2.5965e-05 | 5.9279e-05 | 5.178e-05 | -2.392e-05 | -5.488e-05 | -2.8863e-05 | 2.392e-05 | 5.4882e-05 | 2.8863e-05 | -9.7946e-06 | -2.1109e-05 | -4.2089e-05 | 9.7949e-06 | 2.1111e-05 | 4.209e-05 | 157.5255 | 38.2154 | -115.8562 | -22.4745 | -141.7846 | 64.1438 |  | 0.99549 | 0.99193 | 0.9856 | 0.9955 | 0.99196 | 0.98563 | -0.20658 | -120.7459 | 119.7035 | -0.20626 | -120.7451 | 119.7033
Line3_1_5 | 0.00011218 | 0.00025626 | 0.00022387 | 0.00011218 | 0.00025626 | 0.00022387 | 2.5908e-05 | 5.918e-05 | 5.17e-05 | 2.5908e-05 | 5.918e-05 | 5.17e-05 | -2.3876e-05 | -5.4812e-05 | -2.8851e-05 | 2.3876e-05 | 5.4813e-05 | 2.8852e-05 | -9.7521e-06 | -2.1016e-05 | -4.2e-05 | 9.7524e-06 | 2.1017e-05 | 4.2001e-05 | 157.5761 | 38.2763 | -115.81 | -22.4239 | -141.7237 | 64.19 |  | 0.99549 | 0.99193 | 0.9856 | 0.9955 | 0.99196 | 0.98563 | -0.20658 | -120.7459 | 119.7035 | -0.20626 | -120.7451 | 119.7033
Line4_2_6 | 0.00011194 | 0.00025583 | 0.00022352 | 0.00011194 | 0.00025583 | 0.00022352 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | -2.3833e-05 | -5.4744e-05 | -2.8841e-05 | 2.3833e-05 | 5.4745e-05 | 2.8842e-05 | -9.7101e-06 | -2.0924e-05 | -4.1913e-05 | 9.7104e-06 | 2.0925e-05 | 4.1914e-05 | 157.6265 | 38.3372 | -115.7639 | -22.3735 | -141.6628 | 64.2361 |  | 0.9955 | 0.99196 | 0.98563 | 0.99551 | 0.99198 | 0.98566 | -0.20626 | -120.7451 | 119.7033 | -0.20595 | -120.7443 | 119.703
Line5_6_7 | 0.00011194 | 0.00025583 | 0.00022352 | 0.00011194 | 0.00025583 | 0.00022352 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | -2.3833e-05 | -5.4745e-05 | -2.8842e-05 | 2.3833e-05 | 5.4747e-05 | 2.8843e-05 | -9.7104e-06 | -2.0925e-05 | -4.1914e-05 | 9.7106e-06 | 2.0927e-05 | 4.1915e-05 | 157.6264 | 38.3372 | -115.7639 | -22.3736 | -141.6628 | 64.2361 |  | 0.99551 | 0.99198 | 0.98566 | 0.99553 | 0.99201 | 0.98568 | -0.20595 | -120.7443 | 119.703 | -0.20563 | -120.7436 | 119.7028
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8928e-11 | -8.6249e-11 | -1.551e-10 | 4.8928e-11 | 8.6249e-11 | 1.551e-10 | 3.9302e-11 | 1.4161e-10 | 5.625e-11 | -3.9302e-11 | -1.4161e-10 | -5.625e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99553 | 0.99201 | 0.98568 | 0.99553 | 0.99201 | 0.98568 | -0.20563 | -120.7436 | 119.7028 | -0.20563 | -120.7436 | 119.7028
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6309e-11 | -2.875e-11 | -5.1699e-11 | 1.6309e-11 | 2.875e-11 | 5.1699e-11 | 1.3101e-11 | 4.7205e-11 | 1.875e-11 | -1.3101e-11 | -4.7205e-11 | -1.875e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99553 | 0.99201 | 0.98568 | 0.99553 | 0.99201 | 0.98568 | -0.20563 | -120.7436 | 119.7028 | -0.20563 | -120.7436 | 119.7028
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6309e-11 | -2.875e-11 | -5.1699e-11 | 1.6309e-11 | 2.875e-11 | 5.1699e-11 | 1.3101e-11 | 4.7205e-11 | 1.875e-11 | -1.3101e-11 | -4.7205e-11 | -1.875e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99553 | 0.99201 | 0.98568 | 0.99553 | 0.99201 | 0.98568 | -0.20563 | -120.7436 | 119.7028 | -0.20563 | -120.7436 | 119.7028
Line9_3_11 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3746e-05 | -5.4607e-05 | -2.8819e-05 | 2.3746e-05 | 5.4608e-05 | 2.882e-05 | -9.6264e-06 | -2.074e-05 | -4.1737e-05 | 9.6267e-06 | 2.0741e-05 | 4.1738e-05 | 157.7265 | 38.4582 | -115.6722 | -22.2735 | -141.5418 | 64.3278 |  | 0.9955 | 0.99196 | 0.98563 | 0.99551 | 0.99198 | 0.98566 | -0.20626 | -120.7451 | 119.7033 | -0.20595 | -120.7443 | 119.703

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00011194 | 0.00025583 | 0.00022352 | 0.00011194 | 0.00025583 | 0.00022352 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | -2.3833e-05 | -5.4743e-05 | -2.884e-05 | 2.3833e-05 | 5.4744e-05 | 2.8841e-05 | -9.7099e-06 | -2.0923e-05 | -4.1912e-05 | 9.7101e-06 | 2.0924e-05 | 4.1913e-05 | 157.6265 | 38.3373 | -115.7638 | -22.3735 | -141.6627 | 64.2362 |  | 0.99549 | 0.99193 | 0.9856 | 0.9955 | 0.99196 | 0.98563 | -0.20658 | -120.7459 | 119.7035 | -0.20626 | -120.7451 | 119.7033
Line10_11_12 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3746e-05 | -5.4608e-05 | -2.882e-05 | 2.3746e-05 | 5.4609e-05 | 2.8821e-05 | -9.6267e-06 | -2.0741e-05 | -4.1738e-05 | 9.6269e-06 | 2.0742e-05 | 4.1739e-05 | 157.7264 | 38.4582 | -115.6722 | -22.2736 | -141.5418 | 64.3278 |  | 0.99551 | 0.99198 | 0.98566 | 0.99553 | 0.99201 | 0.98568 | -0.20595 | -120.7443 | 119.703 | -0.20563 | -120.7436 | 119.7028
Line11_12_13 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3746e-05 | -5.4609e-05 | -2.8821e-05 | 2.3747e-05 | 5.461e-05 | 2.8822e-05 | -9.6269e-06 | -2.0742e-05 | -4.1739e-05 | 9.6272e-06 | 2.0744e-05 | 4.174e-05 | 157.7264 | 38.4581 | -115.6723 | -22.2736 | -141.5419 | 64.3277 |  | 0.99553 | 0.99201 | 0.98568 | 0.99554 | 0.99204 | 0.98571 | -0.20563 | -120.7436 | 119.7028 | -0.20532 | -120.7428 | 119.7025
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8797e-11 | -8.5955e-11 | -1.5482e-10 | 4.8797e-11 | 8.5955e-11 | 1.5482e-10 | 3.9242e-11 | 1.4147e-10 | 5.6297e-11 | -3.9242e-11 | -1.4147e-10 | -5.6297e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99554 | 0.99204 | 0.98571 | 0.99554 | 0.99204 | 0.98571 | -0.20532 | -120.7428 | 119.7025 | -0.20532 | -120.7428 | 119.7025
Line13_13_14 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3747e-05 | -5.461e-05 | -2.8821e-05 | 2.3747e-05 | 5.4612e-05 | 2.8822e-05 | -9.6272e-06 | -2.0744e-05 | -4.174e-05 | 9.6275e-06 | 2.0745e-05 | 4.1741e-05 | 157.7262 | 38.4579 | -115.6725 | -22.2738 | -141.5421 | 64.3275 |  | 0.99554 | 0.99204 | 0.98571 | 0.99555 | 0.99207 | 0.98573 | -0.20532 | -120.7428 | 119.7025 | -0.205 | -120.7421 | 119.7023
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2531e-11 | -5.7304e-11 | -1.0321e-10 | 3.2531e-11 | 5.7304e-11 | 1.0321e-10 | 2.6161e-11 | 9.4316e-11 | 3.7531e-11 | -2.6161e-11 | -9.4316e-11 | -3.7531e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99554 | 0.99204 | 0.98571 | 0.99554 | 0.99204 | 0.98571 | -0.20532 | -120.7428 | 119.7025 | -0.20532 | -120.7428 | 119.7025
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6266e-11 | -2.8652e-11 | -5.1606e-11 | 1.6266e-11 | 2.8652e-11 | 5.1606e-11 | 1.3081e-11 | 4.7158e-11 | 1.8766e-11 | -1.3081e-11 | -4.7158e-11 | -1.8766e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99554 | 0.99204 | 0.98571 | 0.99554 | 0.99204 | 0.98571 | -0.20532 | -120.7428 | 119.7025 | -0.20532 | -120.7428 | 119.7025
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6398e-11 | -2.8948e-11 | -5.1888e-11 | 1.6398e-11 | 2.8948e-11 | 5.1888e-11 | 1.314e-11 | 4.7298e-11 | 1.8717e-11 | -1.314e-11 | -4.7298e-11 | -1.8717e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.9955 | 0.99196 | 0.98563 | 0.9955 | 0.99196 | 0.98563 | -0.20626 | -120.7451 | 119.7033 | -0.20626 | -120.7451 | 119.7033
Line17_5_19 | 0.00011218 | 0.00025626 | 0.00022387 | 0.00011218 | 0.00025626 | 0.00022387 | 2.5908e-05 | 5.918e-05 | 5.17e-05 | 2.5908e-05 | 5.918e-05 | 5.17e-05 | -2.3876e-05 | -5.4813e-05 | -2.8852e-05 | 2.3877e-05 | 5.4814e-05 | 2.8853e-05 | -9.7524e-06 | -2.1017e-05 | -4.2001e-05 | 9.7526e-06 | 2.1019e-05 | 4.2002e-05 | 157.576 | 38.2763 | -115.8101 | -22.424 | -141.7237 | 64.1899 |  | 0.9955 | 0.99196 | 0.98563 | 0.99551 | 0.99198 | 0.98566 | -0.20626 | -120.7451 | 119.7033 | -0.20595 | -120.7443 | 119.703
Line1_1_3 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3746e-05 | -5.4606e-05 | -2.8818e-05 | 2.3746e-05 | 5.4607e-05 | 2.8819e-05 | -9.6262e-06 | -2.0738e-05 | -4.1736e-05 | 9.6264e-06 | 2.074e-05 | 4.1737e-05 | 157.7265 | 38.4583 | -115.6721 | -22.2735 | -141.5417 | 64.3279 |  | 0.99549 | 0.99193 | 0.9856 | 0.9955 | 0.99196 | 0.98563 | -0.20658 | -120.7459 | 119.7035 | -0.20626 | -120.7451 | 119.7033
Line2_1_4 | 0.00011243 | 0.00025668 | 0.00022421 | 0.00011243 | 0.00025668 | 0.00022421 | 2.5965e-05 | 5.9279e-05 | 5.178e-05 | 2.5965e-05 | 5.9279e-05 | 5.178e-05 | -2.392e-05 | -5.488e-05 | -2.8863e-05 | 2.392e-05 | 5.4882e-05 | 2.8863e-05 | -9.7946e-06 | -2.1109e-05 | -4.2089e-05 | 9.7949e-06 | 2.1111e-05 | 4.209e-05 | 157.5255 | 38.2154 | -115.8562 | -22.4745 | -141.7846 | 64.1438 |  | 0.99549 | 0.99193 | 0.9856 | 0.9955 | 0.99196 | 0.98563 | -0.20658 | -120.7459 | 119.7035 | -0.20626 | -120.7451 | 119.7033
Line3_1_5 | 0.00011218 | 0.00025626 | 0.00022387 | 0.00011218 | 0.00025626 | 0.00022387 | 2.5908e-05 | 5.918e-05 | 5.17e-05 | 2.5908e-05 | 5.918e-05 | 5.17e-05 | -2.3876e-05 | -5.4812e-05 | -2.8851e-05 | 2.3876e-05 | 5.4813e-05 | 2.8852e-05 | -9.7521e-06 | -2.1016e-05 | -4.2e-05 | 9.7524e-06 | 2.1017e-05 | 4.2001e-05 | 157.5761 | 38.2763 | -115.81 | -22.4239 | -141.7237 | 64.19 |  | 0.99549 | 0.99193 | 0.9856 | 0.9955 | 0.99196 | 0.98563 | -0.20658 | -120.7459 | 119.7035 | -0.20626 | -120.7451 | 119.7033
Line4_2_6 | 0.00011194 | 0.00025583 | 0.00022352 | 0.00011194 | 0.00025583 | 0.00022352 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | -2.3833e-05 | -5.4744e-05 | -2.8841e-05 | 2.3833e-05 | 5.4745e-05 | 2.8842e-05 | -9.7101e-06 | -2.0924e-05 | -4.1913e-05 | 9.7104e-06 | 2.0925e-05 | 4.1914e-05 | 157.6265 | 38.3372 | -115.7639 | -22.3735 | -141.6628 | 64.2361 |  | 0.9955 | 0.99196 | 0.98563 | 0.99551 | 0.99198 | 0.98566 | -0.20626 | -120.7451 | 119.7033 | -0.20595 | -120.7443 | 119.703
Line5_6_7 | 0.00011194 | 0.00025583 | 0.00022352 | 0.00011194 | 0.00025583 | 0.00022352 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | 2.5851e-05 | 5.9082e-05 | 5.1619e-05 | -2.3833e-05 | -5.4745e-05 | -2.8842e-05 | 2.3833e-05 | 5.4747e-05 | 2.8843e-05 | -9.7104e-06 | -2.0925e-05 | -4.1914e-05 | 9.7106e-06 | 2.0927e-05 | 4.1915e-05 | 157.6264 | 38.3372 | -115.7639 | -22.3736 | -141.6628 | 64.2361 |  | 0.99551 | 0.99198 | 0.98566 | 0.99553 | 0.99201 | 0.98568 | -0.20595 | -120.7443 | 119.703 | -0.20563 | -120.7436 | 119.7028
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8928e-11 | -8.6249e-11 | -1.551e-10 | 4.8928e-11 | 8.6249e-11 | 1.551e-10 | 3.9302e-11 | 1.4161e-10 | 5.625e-11 | -3.9302e-11 | -1.4161e-10 | -5.625e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99553 | 0.99201 | 0.98568 | 0.99553 | 0.99201 | 0.98568 | -0.20563 | -120.7436 | 119.7028 | -0.20563 | -120.7436 | 119.7028
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6309e-11 | -2.875e-11 | -5.1699e-11 | 1.6309e-11 | 2.875e-11 | 5.1699e-11 | 1.3101e-11 | 4.7205e-11 | 1.875e-11 | -1.3101e-11 | -4.7205e-11 | -1.875e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99553 | 0.99201 | 0.98568 | 0.99553 | 0.99201 | 0.98568 | -0.20563 | -120.7436 | 119.7028 | -0.20563 | -120.7436 | 119.7028
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6309e-11 | -2.875e-11 | -5.1699e-11 | 1.6309e-11 | 2.875e-11 | 5.1699e-11 | 1.3101e-11 | 4.7205e-11 | 1.875e-11 | -1.3101e-11 | -4.7205e-11 | -1.875e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.99553 | 0.99201 | 0.98568 | 0.99553 | 0.99201 | 0.98568 | -0.20563 | -120.7436 | 119.7028 | -0.20563 | -120.7436 | 119.7028
Line9_3_11 | 0.00011145 | 0.00025498 | 0.00022283 | 0.00011145 | 0.00025498 | 0.00022283 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | 2.5739e-05 | 5.8886e-05 | 5.1459e-05 | -2.3746e-05 | -5.4607e-05 | -2.8819e-05 | 2.3746e-05 | 5.4608e-05 | 2.882e-05 | -9.6264e-06 | -2.074e-05 | -4.1737e-05 | 9.6267e-06 | 2.0741e-05 | 4.1738e-05 | 157.7265 | 38.4582 | -115.6722 | -22.2735 | -141.5418 | 64.3278 |  | 0.9955 | 0.99196 | 0.98563 | 0.99551 | 0.99198 | 0.98566 | -0.20626 | -120.7451 | 119.7033 | -0.20595 | -120.7443 | 119.703