## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.1655 | 2.1655 | 0 | 0 | 1.5003 | 1.5003 | 0.62119 | -0.48051 | 1.2215 | -0.94013 | -66.3744 | 113.6256 | 0.91339 | 0.70372 | -3.33 | -3.4464
Line10_11_12 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.051928 | 0.053141 | -0.1221 | 0.12452 | 109.5602 | -70.4398 | 0.95226 | 0.9717 | -3.4802 | -3.5508
Line11_12_13 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.053141 | 0.054355 | -0.12452 | 0.12695 | 109.5602 | -70.4398 | 0.9717 | 0.99113 | -3.5508 | -3.6186
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99113 | 0.99113 | -3.6186 | -3.6186
Line13_13_14 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.054355 | 0.055568 | -0.12695 | 0.12938 | 109.5602 | -70.4398 | 0.99113 | 1.0106 | -3.6186 | -3.6838
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99113 | 0.99113 | -3.6186 | -3.6186
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99113 | 0.99113 | -3.6186 | -3.6186
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93836 | 0.93836 | -3.4491 | -3.4491
Line17_5_19 | 0.24142 | 0.24142 | 0 | 0 | 0.16726 | 0.16726 | -0.059808 | 0.061557 | -0.14481 | 0.14831 | 109.0058 | -70.9942 | 0.93671 | 0.96002 | -3.4355 | -3.5358
Line1_1_3 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.049501 | 0.050715 | -0.11724 | 0.11967 | 109.5602 | -70.4398 | 0.91339 | 0.93283 | -3.33 | -3.4067
Line2_1_4 | 0.25865 | 0.25865 | 0 | 0 | 0.1792 | 0.1792 | -0.061576 | 0.063583 | -0.15165 | 0.15567 | 108.769 | -71.231 | 0.91339 | 0.93836 | -3.33 | -3.4491
Line3_1_5 | 0.24142 | 0.24142 | 0 | 0 | 0.16726 | 0.16726 | -0.05806 | 0.059808 | -0.14131 | 0.14481 | 109.0058 | -70.9942 | 0.91339 | 0.93671 | -3.33 | -3.4355
Line4_2_6 | 2.1655 | 2.1655 | 0 | 0 | 1.5003 | 1.5003 | 0.48051 | -0.33982 | 0.94013 | -0.65876 | -66.3744 | 113.6256 | 0.70372 | 0.49406 | -3.4464 | -3.6615
Line5_6_7 | 2.1655 | 2.1655 | 0 | 0 | 1.5003 | 1.5003 | 0.33982 | -0.19914 | 0.65876 | -0.37739 | -66.3744 | 113.6256 | 0.49406 | 0.28442 | -3.6615 | -4.1938
Line6_7_8 | 2.9374 | 2.9374 | 0 | 5.3526 | 2.0351 | 2.0351 | 0.25885 | -1e-07 | 0.51771 | -1e-07 | -67.6287 | 112.3713 | 0.28442 | 0 | -4.1938 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9243e-22 | 0 | 2.8476e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9243e-22 | 0 | 2.8476e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0.20111 | 0.20111 | 0 | 0 | 0.13933 | 0.13933 | -0.050715 | 0.051928 | -0.11967 | 0.1221 | 109.5602 | -70.4398 | 0.93283 | 0.95226 | -3.4067 | -3.4802

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 2.2579 | 2.2579 | 0 | 0 | 1.5643 | 1.5643 | 0.67276 | -0.51982 | 1.3243 | -1.0184 | -66.5264 | 113.4736 | 0.94951 | 0.73089 | -3.4584 | -3.5682
Line10_11_12 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.056633 | 0.057929 | -0.13079 | 0.13338 | 109.8207 | -70.1793 | 0.98969 | 1.0098 | -3.592 | -3.6548
Line11_12_13 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.057929 | 0.059225 | -0.13338 | 0.13598 | 109.8207 | -70.1793 | 1.0098 | 1.0299 | -3.6548 | -3.7151
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0299 | 1.0299 | -3.7151 | -3.7151
Line13_13_14 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.059225 | 0.060521 | -0.13598 | 0.13857 | 109.8207 | -70.1793 | 1.0299 | 1.05 | -3.7151 | -3.7731
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0299 | 1.0299 | -3.7151 | -3.7151
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0299 | 1.0299 | -3.7151 | -3.7151
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97508 | 0.97508 | -3.5655 | -3.5655
Line17_5_19 | 0.24786 | 0.24786 | 0 | 0 | 0.17173 | 0.17173 | -0.064826 | 0.066669 | -0.15409 | 0.15777 | 109.264 | -70.736 | 0.97345 | 0.9974 | -3.5531 | -3.6432
Line1_1_3 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.05404 | 0.055336 | -0.12561 | 0.1282 | 109.8207 | -70.1793 | 0.94951 | 0.9696 | -3.4584 | -3.5266
Line2_1_4 | 0.2648 | 0.2648 | 0 | 0 | 0.18346 | 0.18346 | -0.066624 | 0.068728 | -0.16095 | 0.16516 | 109.0286 | -70.9714 | 0.94951 | 0.97508 | -3.4584 | -3.5655
Line3_1_5 | 0.24786 | 0.24786 | 0 | 0 | 0.17173 | 0.17173 | -0.062983 | 0.064826 | -0.1504 | 0.15409 | 109.264 | -70.736 | 0.94951 | 0.97345 | -3.4584 | -3.5531
Line4_2_6 | 2.2579 | 2.2579 | 0 | 0 | 1.5643 | 1.5643 | 0.51982 | -0.36687 | 1.0184 | -0.71247 | -66.5264 | 113.4736 | 0.73089 | 0.51228 | -3.5682 | -3.7716
Line5_6_7 | 2.2579 | 2.2579 | 0 | 0 | 1.5643 | 1.5643 | 0.36687 | -0.21392 | 0.71247 | -0.40657 | -66.5264 | 113.4736 | 0.51228 | 0.29368 | -3.7716 | -4.2779
Line6_7_8 | 3.0331 | 3.0331 | 0 | 5.5337 | 2.1014 | 2.1014 | 0.276 | -1e-07 | 0.552 | -1e-07 | -67.7129 | 112.2871 | 0.29368 | 0 | -4.2779 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3826e-22 | 0 | -2.7324e-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3826e-22 | 0 | -2.7324e-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0.20786 | 0.20786 | 0 | 0 | 0.14401 | 0.14401 | -0.055336 | 0.056633 | -0.1282 | 0.13079 | 109.8207 | -70.1793 | 0.9696 | 0.98969 | -3.5266 | -3.592

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.086596 | 0.086596 | 0 | 0 | 0.059995 | 0.059995 | -0.01816 | 0.018385 | -0.063081 | 0.063531 | 106.0786 | -73.9214 | 1.0941 | 1.1024 | 0.018543 | -0.06091
Line10_11_12 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0037087 | 0.0040192 | -0.078293 | 0.078914 | 92.3135 | -87.6865 | 1.1121 | 1.1211 | -0.39862 | -0.60218
Line11_12_13 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0040192 | 0.0043296 | -0.078914 | 0.079535 | 92.3135 | -87.6865 | 1.1211 | 1.1302 | -0.60218 | -0.80249
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1302 | 1.1302 | -0.80249 | -0.80249
Line13_13_14 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0043296 | 0.0046401 | -0.079535 | 0.080155 | 92.3135 | -87.6865 | 1.1302 | 1.1392 | -0.80249 | -0.99961
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1302 | 1.1302 | -0.80249 | -0.80249
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1302 | 1.1302 | -0.80249 | -0.80249
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1057 | 1.1057 | -0.24429 | -0.24429
Line17_5_19 | 0.12147 | 0.12147 | 0 | 0 | 0.084155 | 0.084155 | -0.0046676 | 0.0051102 | -0.092865 | 0.09375 | 92.6485 | -87.3515 | 1.1049 | 1.1157 | -0.22889 | -0.47154
Line1_1_3 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0030878 | 0.0033983 | -0.077051 | 0.077672 | 92.3134 | -87.6866 | 1.0941 | 1.1031 | 0.018543 | -0.19174
Line2_1_4 | 0.12985 | 0.12985 | 0 | 0 | 0.089963 | 0.089963 | -0.0047636 | 0.0052694 | -0.098316 | 0.099328 | 92.7924 | -87.2076 | 1.0941 | 1.1057 | 0.018543 | -0.24429
Line3_1_5 | 0.12147 | 0.12147 | 0 | 0 | 0.084155 | 0.084155 | -0.0042249 | 0.0046676 | -0.09198 | 0.092865 | 92.6485 | -87.3515 | 1.0941 | 1.1049 | 0.018543 | -0.22889
Line4_2_6 | 0.086596 | 0.086596 | 0 | 0 | 0.059995 | 0.059995 | -0.018385 | 0.01861 | -0.063531 | 0.063981 | 106.0786 | -73.9214 | 1.1024 | 1.1106 | -0.06091 | -0.13918
Line5_6_7 | 0.086596 | 0.086596 | 0 | 0 | 0.059995 | 0.059995 | -0.01861 | 0.018835 | -0.063981 | 0.064431 | 106.0786 | -73.9214 | 1.1106 | 1.1189 | -0.13918 | -0.2163
Line6_7_8 | 0.036433 | 0.036433 | 0 | 0.066389 | 0.025242 | 0.025242 | 0.01995 | -0.019911 | 0.01999 | -0.019911 | -45.2734 | 134.7266 | 1.1189 | 1.1155 | -0.2163 | -0.27343
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0426e-10 | 0 | 6.1487e-11 | 0 | 0 | 0 | 1.1155 | 1.1155 | -0.27343 | -0.27343
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0426e-10 | 0 | 6.1487e-11 | 0 | 0 | 0 | 1.1155 | 1.1155 | -0.27343 | -0.27343
Line9_3_11 | 0.10173 | 0.10173 | 0 | 0 | 0.070478 | 0.070478 | -0.0033983 | 0.0037087 | -0.077672 | 0.078293 | 92.3134 | -87.6866 | 1.1031 | 1.1121 | -0.19174 | -0.39862

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.086049 | 0.086049 | 0 | 0 | 0.059616 | 0.059616 | -0.018151 | 0.018373 | -0.06589 | 0.066334 | 105.4174 | -74.5826 | 1.1464 | 1.1546 | 0.015822 | -0.064227
Line10_11_12 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.0040702 | 0.0043878 | -0.082919 | 0.083555 | 92.4249 | -87.5751 | 1.1646 | 1.1737 | -0.38532 | -0.58122
Line11_12_13 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.0043878 | 0.0047054 | -0.083555 | 0.08419 | 92.4249 | -87.5751 | 1.1737 | 1.1829 | -0.58122 | -0.77409
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1829 | 1.1829 | -0.77409 | -0.77409
Line13_13_14 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.0047054 | 0.005023 | -0.08419 | 0.084825 | 92.4249 | -87.5751 | 1.1829 | 1.192 | -0.77409 | -0.96401
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1829 | 1.1829 | -0.77409 | -0.77409
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1829 | 1.1829 | -0.77409 | -0.77409
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.158 | 1.158 | -0.23465 | -0.23465
Line17_5_19 | 0.12206 | 0.12206 | 0 | 0 | 0.084566 | 0.084566 | -0.0050759 | 0.0055229 | -0.09773 | 0.098624 | 92.7526 | -87.2474 | 1.1572 | 1.1681 | -0.22058 | -0.45259
Line1_1_3 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.003435 | 0.0037526 | -0.081649 | 0.082284 | 92.4249 | -87.5751 | 1.1464 | 1.1555 | 0.015822 | -0.18633
Line2_1_4 | 0.13013 | 0.13013 | 0 | 0 | 0.090154 | 0.090154 | -0.0051861 | 0.0056941 | -0.10322 | 0.10424 | 92.8921 | -87.1079 | 1.1464 | 1.158 | 0.015822 | -0.23465
Line3_1_5 | 0.12206 | 0.12206 | 0 | 0 | 0.084566 | 0.084566 | -0.004629 | 0.0050759 | -0.096836 | 0.09773 | 92.7526 | -87.2474 | 1.1464 | 1.1572 | 0.015822 | -0.22058
Line4_2_6 | 0.086049 | 0.086049 | 0 | 0 | 0.059616 | 0.059616 | -0.018373 | 0.018595 | -0.066334 | 0.066778 | 105.4174 | -74.5826 | 1.1546 | 1.1628 | -0.064227 | -0.14315
Line5_6_7 | 0.086049 | 0.086049 | 0 | 0 | 0.059616 | 0.059616 | -0.018595 | 0.018817 | -0.066778 | 0.067223 | 105.4174 | -74.5826 | 1.1628 | 1.1709 | -0.14315 | -0.22097
Line6_7_8 | 0.038128 | 0.038128 | 0 | 0.069562 | 0.026416 | 0.026416 | 0.02185 | -0.021806 | 0.021894 | -0.021806 | -45.2781 | 134.7219 | 1.1709 | 1.1674 | -0.22097 | -0.27809
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6611e-10 | 0 | 6.8562e-11 | 0 | 0 | 0 | 1.1674 | 1.1674 | -0.27809 | -0.27809
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6611e-10 | 0 | 6.8562e-11 | 0 | 0 | 0 | 1.1674 | 1.1674 | -0.27809 | -0.27809
Line9_3_11 | 0.10289 | 0.10289 | 0 | 0 | 0.071285 | 0.071285 | -0.0037526 | 0.0040702 | -0.082284 | 0.082919 | 92.4249 | -87.5751 | 1.1555 | 1.1646 | -0.18633 | -0.38532

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.6788 | 1.6788 | 0 | 0 | 1.1631 | 1.1631 | 0.65091 | -0.48857 | 0.67724 | -0.50813 | -52.7965 | 127.2035 | 0.80758 | 0.60604 | -6.661 | -6.6721
Line10_11_12 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013252 | 0.0013256 | -0.00089516 | 0.00089565 | 139.3098 | -40.6902 | 0.80825 | 0.80859 | -6.6507 | -6.6456
Line11_12_13 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013256 | 0.0013261 | -0.00089565 | 0.00089614 | 139.3097 | -40.6903 | 0.80859 | 0.80892 | -6.6456 | -6.6405
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80892 | 0.80892 | -6.6405 | -6.6405
Line13_13_14 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013261 | 0.0013266 | -0.00089614 | 0.00089663 | 139.3095 | -40.6905 | 0.80892 | 0.80926 | -6.6405 | -6.6354
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80892 | 0.80892 | -6.6405 | -6.6405
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80892 | 0.80892 | -6.6405 | -6.6405
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80792 | 0.80792 | -6.6559 | -6.6559
Line17_5_19 | 0.0028708 | 0.0028708 | 0 | 0 | 0.001989 | 0.001989 | -0.0013292 | 0.0013297 | -0.00090294 | 0.00090343 | 139.1565 | -40.8435 | 0.80792 | 0.80826 | -6.6559 | -6.6508
Line1_1_3 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013242 | 0.0013247 | -0.00089418 | 0.00089466 | 139.3099 | -40.6901 | 0.80758 | 0.80792 | -6.661 | -6.6558
Line2_1_4 | 0.0028759 | 0.0028759 | 0 | 0 | 0.0019925 | 0.0019925 | -0.0013303 | 0.0013308 | -0.00090522 | 0.00090571 | 139.1052 | -40.8948 | 0.80758 | 0.80792 | -6.661 | -6.6559
Line3_1_5 | 0.0028708 | 0.0028708 | 0 | 0 | 0.001989 | 0.001989 | -0.0013288 | 0.0013293 | -0.00090244 | 0.00090293 | 139.1566 | -40.8434 | 0.80758 | 0.80792 | -6.661 | -6.6559
Line4_2_6 | 1.6788 | 1.6788 | 0 | 0 | 1.1631 | 1.1631 | 0.48857 | -0.32622 | 0.50813 | -0.33902 | -52.7965 | 127.2035 | 0.60604 | 0.40449 | -6.6721 | -6.6945
Line5_6_7 | 1.6788 | 1.6788 | 0 | 0 | 1.1631 | 1.1631 | 0.32622 | -0.16387 | 0.33902 | -0.16991 | -52.7965 | 127.2035 | 0.40449 | 0.20295 | -6.6945 | -6.7611
Line6_7_8 | 1.6905 | 1.6905 | 0 | 2.6836 | 1.1712 | 1.1712 | 0.16461 | -1e-07 | 0.17147 | -1e-07 | -52.9302 | 127.0698 | 0.20295 | 0 | -6.7611 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7639e-22 | 0 | 8.9208e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7639e-22 | 0 | 8.9208e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0.0028558 | 0.0028558 | 0 | 0 | 0.0019785 | 0.0019785 | -0.0013247 | 0.0013252 | -0.00089467 | 0.00089515 | 139.3098 | -40.6902 | 0.80792 | 0.80825 | -6.6558 | -6.6507

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 1.5905 | 1.5905 | 0 | 0 | 1.1019 | 1.1019 | 0.5842 | -0.43849 | 0.60783 | -0.45605 | -52.7965 | 127.2035 | 0.76508 | 0.57414 | -6.661 | -6.6721
Line10_11_12 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011893 | 0.0011898 | -0.00080341 | 0.00080385 | 139.3098 | -40.6902 | 0.76571 | 0.76603 | -6.6507 | -6.6456
Line11_12_13 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011898 | 0.0011902 | -0.00080385 | 0.00080429 | 139.3097 | -40.6903 | 0.76603 | 0.76635 | -6.6456 | -6.6405
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76635 | 0.76635 | -6.6405 | -6.6405
Line13_13_14 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011902 | 0.0011906 | -0.00080429 | 0.00080473 | 139.3095 | -40.6905 | 0.76635 | 0.76667 | -6.6405 | -6.6354
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76635 | 0.76635 | -6.6405 | -6.6405
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76635 | 0.76635 | -6.6405 | -6.6405
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7654 | 0.7654 | -6.6559 | -6.6559
Line17_5_19 | 0.0027197 | 0.0027197 | 0 | 0 | 0.0018843 | 0.0018843 | -0.001193 | 0.0011934 | -0.00081039 | 0.00081084 | 139.1565 | -40.8435 | 0.7654 | 0.76572 | -6.6559 | -6.6508
Line1_1_3 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011885 | 0.0011889 | -0.00080253 | 0.00080297 | 139.3099 | -40.6901 | 0.76508 | 0.7654 | -6.661 | -6.6558
Line2_1_4 | 0.0027245 | 0.0027245 | 0 | 0 | 0.0018876 | 0.0018876 | -0.001194 | 0.0011944 | -0.00081244 | 0.00081289 | 139.1052 | -40.8948 | 0.76508 | 0.7654 | -6.661 | -6.6559
Line3_1_5 | 0.0027197 | 0.0027197 | 0 | 0 | 0.0018843 | 0.0018843 | -0.0011926 | 0.001193 | -0.00080995 | 0.00081039 | 139.1566 | -40.8434 | 0.76508 | 0.7654 | -6.661 | -6.6559
Line4_2_6 | 1.5905 | 1.5905 | 0 | 0 | 1.1019 | 1.1019 | 0.43849 | -0.29278 | 0.45605 | -0.30427 | -52.7965 | 127.2035 | 0.57414 | 0.3832 | -6.6721 | -6.6945
Line5_6_7 | 1.5905 | 1.5905 | 0 | 0 | 1.1019 | 1.1019 | 0.29278 | -0.14708 | 0.30427 | -0.15249 | -52.7965 | 127.2035 | 0.3832 | 0.19227 | -6.6945 | -6.7611
Line6_7_8 | 1.6016 | 1.6016 | 0 | 2.5424 | 1.1096 | 1.1096 | 0.14774 | -1e-07 | 0.1539 | -1e-07 | -52.9302 | 127.0698 | 0.19227 | 0 | -6.7611 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0562e-22 | 0 | 8.0069e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0562e-22 | 0 | 8.0069e-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line9_3_11 | 0.0027055 | 0.0027055 | 0 | 0 | 0.0018744 | 0.0018744 | -0.0011889 | 0.0011893 | -0.00080297 | 0.00080341 | 139.3098 | -40.6902 | 0.7654 | 0.76571 | -6.6558 | -6.6507

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.030262 | 0.030262 | 0 | 0 | 0.020966 | 0.020966 | 0.014076 | -0.014024 | 0.01402 | -0.013965 | -45.0087 | 134.9913 | 0.94759 | 0.94396 | -0.12299 | -0.12793
Line10_11_12 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8414e-05 | -1.8297e-05 | 1.8298e-05 | 147.0975 | -32.9025 | 0.9476 | 0.94761 | -0.12282 | -0.12273
Line11_12_13 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8414e-05 | -1.8298e-05 | 1.8298e-05 | 147.0975 | -32.9025 | 0.94761 | 0.94761 | -0.12273 | -0.12265
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94761 | 0.94761 | -0.12265 | -0.12265
Line13_13_14 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8415e-05 | -1.8298e-05 | 1.8298e-05 | 147.0973 | -32.9027 | 0.94761 | 0.94762 | -0.12265 | -0.12256
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94761 | 0.94761 | -0.12265 | -0.12265
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94761 | 0.94761 | -0.12265 | -0.12265
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9476 | 0.9476 | -0.12291 | -0.12291
Line17_5_19 | 5.1748e-05 | 5.1748e-05 | 0 | 0 | 3.5852e-05 | 3.5852e-05 | -2.8514e-05 | 2.8514e-05 | -1.847e-05 | 1.847e-05 | 146.9443 | -33.0557 | 0.9476 | 0.9476 | -0.12291 | -0.12282
Line1_1_3 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8414e-05 | -1.8297e-05 | 1.8297e-05 | 147.0976 | -32.9024 | 0.94759 | 0.9476 | -0.12299 | -0.12291
Line2_1_4 | 5.1839e-05 | 5.1839e-05 | 0 | 0 | 3.5915e-05 | 3.5915e-05 | -2.8548e-05 | 2.8548e-05 | -1.8528e-05 | 1.8528e-05 | 146.893 | -33.107 | 0.94759 | 0.9476 | -0.12299 | -0.12291
Line3_1_5 | 5.1748e-05 | 5.1748e-05 | 0 | 0 | 3.5852e-05 | 3.5852e-05 | -2.8514e-05 | 2.8514e-05 | -1.847e-05 | 1.847e-05 | 146.9443 | -33.0557 | 0.94759 | 0.9476 | -0.12299 | -0.12291
Line4_2_6 | 0.030262 | 0.030262 | 0 | 0 | 0.020966 | 0.020966 | 0.014024 | -0.013971 | 0.013965 | -0.01391 | -45.0087 | 134.9913 | 0.94396 | 0.94033 | -0.12793 | -0.13291
Line5_6_7 | 0.030262 | 0.030262 | 0 | 0 | 0.020966 | 0.020966 | 0.013971 | -0.013918 | 0.01391 | -0.013856 | -45.0087 | 134.9913 | 0.94033 | 0.93669 | -0.13291 | -0.13793
Line6_7_8 | 0.030473 | 0.030473 | 0 | 0.048374 | 0.021112 | 0.021112 | 0.013982 | -0.013929 | 0.013985 | -0.013929 | -45.1425 | 134.8575 | 0.93669 | 0.93304 | -0.13793 | -0.14249
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7407e-10 | 0 | 2.4248e-11 | 0 | 0 | 0 | 0.93304 | 0.93304 | -0.14249 | -0.14249
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7407e-10 | 0 | 2.4248e-11 | 0 | 0 | 0 | 0.93304 | 0.93304 | -0.14249 | -0.14249
Line9_3_11 | 5.1477e-05 | 5.1477e-05 | 0 | 0 | 3.5665e-05 | 3.5665e-05 | -2.8414e-05 | 2.8414e-05 | -1.8297e-05 | 1.8297e-05 | 147.0976 | -32.9024 | 0.9476 | 0.9476 | -0.12291 | -0.12282

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.02867 | 0.02867 | 0 | 0 | 0.019863 | 0.019863 | 0.012634 | -0.012586 | 0.012583 | -0.012534 | -45.0087 | 134.9913 | 0.89772 | 0.89428 | -0.12299 | -0.12793
Line10_11_12 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3788e-05 | 3.3788e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6422e-05 | 147.0975 | -32.9025 | 0.89773 | 0.89773 | -0.12282 | -0.12273
Line11_12_13 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3788e-05 | 3.3788e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6422e-05 | 147.0975 | -32.9025 | 0.89773 | 0.89774 | -0.12273 | -0.12265
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89774 | 0.89774 | -0.12265 | -0.12265
Line13_13_14 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3787e-05 | 3.3787e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6423e-05 | 147.0973 | -32.9027 | 0.89774 | 0.89775 | -0.12265 | -0.12256
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89774 | 0.89774 | -0.12265 | -0.12265
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89774 | 0.89774 | -0.12265 | -0.12265
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89772 | 0.89772 | -0.12291 | -0.12291
Line17_5_19 | 4.9025e-05 | 4.9025e-05 | 0 | 0 | 3.3965e-05 | 3.3965e-05 | -2.5592e-05 | 2.5592e-05 | -1.6577e-05 | 1.6577e-05 | 146.9443 | -33.0557 | 0.89772 | 0.89773 | -0.12291 | -0.12282
Line1_1_3 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3788e-05 | 3.3788e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6422e-05 | 147.0976 | -32.9024 | 0.89772 | 0.89772 | -0.12299 | -0.12291
Line2_1_4 | 4.9111e-05 | 4.9111e-05 | 0 | 0 | 3.4025e-05 | 3.4025e-05 | -2.5622e-05 | 2.5622e-05 | -1.6629e-05 | 1.6629e-05 | 146.893 | -33.107 | 0.89772 | 0.89772 | -0.12299 | -0.12291
Line3_1_5 | 4.9025e-05 | 4.9025e-05 | 0 | 0 | 3.3965e-05 | 3.3965e-05 | -2.5592e-05 | 2.5592e-05 | -1.6577e-05 | 1.6577e-05 | 146.9443 | -33.0557 | 0.89772 | 0.89772 | -0.12299 | -0.12291
Line4_2_6 | 0.02867 | 0.02867 | 0 | 0 | 0.019863 | 0.019863 | 0.012586 | -0.012539 | 0.012534 | -0.012485 | -45.0087 | 134.9913 | 0.89428 | 0.89084 | -0.12793 | -0.13291
Line5_6_7 | 0.02867 | 0.02867 | 0 | 0 | 0.019863 | 0.019863 | 0.012539 | -0.012492 | 0.012485 | -0.012435 | -45.0087 | 134.9913 | 0.89084 | 0.88739 | -0.13291 | -0.13793
Line6_7_8 | 0.028869 | 0.028869 | 0 | 0.045828 | 0.020001 | 0.020001 | 0.012549 | -0.012501 | 0.012551 | -0.012501 | -45.1425 | 134.8575 | 0.88739 | 0.88393 | -0.13793 | -0.14249
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5623e-10 | 0 | 2.1763e-11 | 0 | 0 | 0 | 0.88393 | 0.88393 | -0.14249 | -0.14249
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5623e-10 | 0 | 2.1763e-11 | 0 | 0 | 0 | 0.88393 | 0.88393 | -0.14249 | -0.14249
Line9_3_11 | 4.8768e-05 | 4.8768e-05 | 0 | 0 | 3.3788e-05 | 3.3788e-05 | -2.5502e-05 | 2.5502e-05 | -1.6422e-05 | 1.6422e-05 | 147.0976 | -32.9024 | 0.89772 | 0.89773 | -0.12291 | -0.12282

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.16797 | 1.8575 | 1.9186 | 0.16797 | 1.8575 | 1.9186 | 0.038792 | 0.42897 | 0.44307 | 0.038792 | 0.42897 | 0.44307 | -0.029841 | 0.38129 | -0.078743 | 0.030123 | -0.34679 | 0.11555 | -0.030389 | 0.19259 | 0.40365 | 0.030953 | -0.12358 | -0.33003 | 135.1206 | -153.8016 | 21.4477 | -44.8794 | 26.1984 | -158.5523 | 1.0979 | 0.9958 | 0.9282 | 1.1134 | 0.85822 | 0.78921 | 0.64151 | -127.0031 | 122.4862 | 0.89895 | -134.1869 | 130.7439
Line10_11_12 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.0023453 | -0.024374 | -6.6003e-05 | 0.0024436 | 0.024667 | 0.00042554 | -0.025447 | -0.032526 | -0.042078 | 0.025644 | 0.033112 | 0.042797 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.1158 | 1.0284 | 0.96092 | 1.1248 | 1.0447 | 0.97739 | 0.27747 | -126.6627 | 121.4757 | 0.099794 | -126.5005 | 120.9959
Line11_12_13 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.0024436 | -0.024667 | -0.00042554 | 0.002542 | 0.02496 | 0.00078507 | -0.025644 | -0.033112 | -0.042797 | 0.025841 | 0.033697 | 0.043516 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.1248 | 1.0447 | 0.97739 | 1.1337 | 1.061 | 0.99393 | 0.099794 | -126.5005 | 120.9959 | -0.075077 | -126.3433 | 120.532
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.044e-09 | 2.0361e-10 | -6.1257e-10 | -1.044e-09 | -2.0361e-10 | 6.1257e-10 | 1.7158e-11 | 1.354e-09 | -1.0659e-10 | -1.7158e-11 | -1.354e-09 | 1.0659e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1337 | 1.061 | 0.99393 | 1.1337 | 1.061 | 0.99393 | -0.075077 | -126.3433 | 120.532 | -0.075077 | -126.3433 | 120.532
Line13_13_14 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.002542 | -0.02496 | -0.00078507 | 0.0026403 | 0.025252 | 0.0011446 | -0.025841 | -0.033697 | -0.043516 | 0.026037 | 0.034283 | 0.044235 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.1337 | 1.061 | 0.99393 | 1.1427 | 1.0773 | 1.0105 | -0.075077 | -126.3433 | 120.532 | -0.2472 | -126.1909 | 120.0834
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9603e-10 | 1.3574e-10 | -4.0838e-10 | -6.9603e-10 | -1.3574e-10 | 4.0838e-10 | 1.1439e-11 | 9.0265e-10 | -7.1063e-11 | -1.1439e-11 | -9.0265e-10 | 7.1063e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1337 | 1.061 | 0.99393 | 1.1337 | 1.061 | 0.99393 | -0.075077 | -126.3433 | 120.532 | -0.075077 | -126.3433 | 120.532
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4801e-10 | 6.7869e-11 | -2.0419e-10 | -3.4801e-10 | -6.7869e-11 | 2.0419e-10 | 5.7193e-12 | 4.5132e-10 | -3.5532e-11 | -5.7193e-12 | -4.5132e-10 | 3.5532e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1337 | 1.061 | 0.99393 | 1.1337 | 1.061 | 0.99393 | -0.075077 | -126.3433 | 120.532 | -0.075077 | -126.3433 | 120.532
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4287e-10 | -9.5036e-11 | -3.5103e-10 | -2.4287e-10 | 9.5036e-11 | 3.5103e-10 | -3.1982e-11 | 4.6464e-10 | -1.1615e-10 | 3.1982e-11 | -4.6464e-10 | 1.1615e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1097 | 1.0171 | 0.94854 | 1.1097 | 1.0171 | 0.94854 | 0.42892 | -126.8146 | 121.8226 | 0.42892 | -126.8146 | 121.8226
Line17_5_19 | 0.11944 | 0.20717 | 0.22389 | 0.11944 | 0.20717 | 0.22389 | 0.027584 | 0.047845 | 0.051705 | 0.027584 | 0.047845 | 0.051705 | -0.0036004 | -0.028432 | 0.00085457 | 0.0037431 | 0.028861 | -0.00035331 | -0.030373 | -0.039404 | -0.048976 | 0.030658 | 0.040263 | 0.049978 | 97.1973 | -1.0057 | -149.1327 | -82.8027 | 178.9943 | 30.8673 | 1.1088 | 1.0156 | 0.94736 | 1.1197 | 1.0354 | 0.96663 | 0.43703 | -126.8176 | 121.867 | 0.23652 | -126.6393 | 121.2724
Line1_1_3 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.0021486 | -0.023788 | 0.00065306 | 0.0022469 | 0.024081 | -0.00029353 | -0.025054 | -0.031354 | -0.04064 | 0.02525 | 0.03194 | 0.041359 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.0979 | 0.9958 | 0.9282 | 1.1069 | 1.0121 | 0.94453 | 0.64151 | -127.0031 | 122.4862 | 0.45802 | -126.8302 | 121.9722
Line2_1_4 | 0.12831 | 0.22261 | 0.23817 | 0.12831 | 0.22261 | 0.23817 | 0.029632 | 0.051409 | 0.055004 | 0.029632 | 0.051409 | 0.055004 | -0.0040837 | -0.029724 | 0.0016783 | 0.0042483 | 0.03022 | -0.001111 | -0.032277 | -0.04168 | -0.051027 | 0.032606 | 0.042671 | 0.052162 | 97.8523 | -1.5086 | -149.3976 | -82.1477 | 178.4914 | 30.6024 | 1.0979 | 0.9958 | 0.9282 | 1.1097 | 1.0171 | 0.94854 | 0.64151 | -127.0031 | 122.4862 | 0.42892 | -126.8146 | 121.8226
Line3_1_5 | 0.11944 | 0.20717 | 0.22389 | 0.11944 | 0.20717 | 0.22389 | 0.027584 | 0.047845 | 0.051705 | 0.027584 | 0.047845 | 0.051705 | -0.0034578 | -0.028002 | 0.0013558 | 0.0036004 | 0.028432 | -0.00085457 | -0.030088 | -0.038546 | -0.047973 | 0.030373 | 0.039404 | 0.048976 | 97.1973 | -1.0057 | -149.1327 | -82.8027 | 178.9943 | 30.8673 | 1.0979 | 0.9958 | 0.9282 | 1.1088 | 1.0156 | 0.94736 | 0.64151 | -127.0031 | 122.4862 | 0.43703 | -126.8176 | 121.867
Line4_2_6 | 0.16797 | 1.8575 | 1.9186 | 0.16797 | 1.8575 | 1.9186 | 0.038792 | 0.42897 | 0.44307 | 0.038792 | 0.42897 | 0.44307 | -0.030123 | 0.34679 | -0.11555 | 0.030405 | -0.31228 | 0.15236 | -0.030953 | 0.12358 | 0.33003 | 0.031517 | -0.054579 | -0.25642 | 135.1206 | -153.8016 | 21.4477 | -44.8794 | 26.1984 | -158.5523 | 1.1134 | 0.85822 | 0.78921 | 1.1289 | 0.73902 | 0.67318 | 0.89895 | -134.1869 | 130.7439 | 1.1493 | -143.8878 | 142.166
Line5_6_7 | 0.16797 | 1.8575 | 1.9186 | 0.16797 | 1.8575 | 1.9186 | 0.038792 | 0.42897 | 0.44307 | 0.038792 | 0.42897 | 0.44307 | -0.030405 | 0.31228 | -0.15236 | 0.030688 | -0.27778 | 0.18917 | -0.031517 | 0.054579 | 0.25642 | 0.032082 | 0.014426 | -0.1828 | 135.1206 | -153.8016 | 21.4477 | -44.8794 | 26.1984 | -158.5523 | 1.1289 | 0.73902 | 0.67318 | 1.1445 | 0.64843 | 0.59372 | 1.1493 | -143.8878 | 142.166 | 1.3929 | -156.7744 | 157.4286
Line6_7_8 | 0 | 2.5094 | 2.5094 | 0 | 2.5094 | 2.5094 | 0 | 0.57952 | 0.57952 | 0 | 0.57952 | 0.57952 | 1.193e-09 | 0.37547 | -0.24954 | -1.193e-09 | -0.3125 | 0.3125 | -3.2131e-10 | 0.014991 | 0.23689 | 3.2131e-10 | 0.11095 | -0.11095 | 0 | -159.0608 | 20.9392 | 0 | 20.9392 | -159.0608 | 1.1445 | 0.64843 | 0.59372 | 1.1445 | 0.57223 | 0.57223 | 1.3929 | -156.7744 | 157.4286 | 1.3929 | -178.6071 | -178.6071
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9768e-10 | 5.3042e-11 | 1.458e-10 | -3.9768e-10 | -5.3041e-11 | -1.458e-10 | -1.0711e-10 | 1.8806e-09 | -1.9341e-09 | 1.0711e-10 | -1.8806e-09 | 1.9341e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1445 | 0.57223 | 0.57223 | 1.1445 | 0.57223 | 0.57223 | 1.3929 | -178.6071 | -178.6071 | 1.3929 | -178.6071 | -178.6071
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9768e-10 | 5.3042e-11 | 1.458e-10 | -3.9768e-10 | -5.3042e-11 | -1.458e-10 | -1.071e-10 | 1.8806e-09 | -1.9341e-09 | 1.071e-10 | -1.8806e-09 | 1.9341e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1445 | 0.57223 | 0.57223 | 1.1445 | 0.57223 | 0.57223 | 1.3929 | -178.6071 | -178.6071 | 1.3929 | -178.6071 | -178.6071
Line9_3_11 | 0.099172 | 0.17114 | 0.18961 | 0.099172 | 0.17114 | 0.18961 | 0.022903 | 0.039523 | 0.043789 | 0.022903 | 0.039523 | 0.043789 | -0.0022469 | -0.024081 | 0.00029353 | 0.0023453 | 0.024374 | 6.6004e-05 | -0.02525 | -0.03194 | -0.041359 | 0.025447 | 0.032526 | 0.042078 | 95.5431 | 0.18399 | -148.4344 | -84.4569 | -179.816 | 31.5656 | 1.1069 | 1.0121 | 0.94453 | 1.1158 | 1.0284 | 0.96092 | 0.45802 | -126.8302 | 121.9722 | 0.27747 | -126.6627 | 121.4757

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.16928 | 1.9371 | 1.9988 | 0.16928 | 1.9371 | 1.9988 | 0.039093 | 0.44736 | 0.4616 | 0.039093 | 0.44736 | 0.4616 | -0.031431 | 0.41506 | -0.087248 | 0.031718 | -0.37753 | 0.1272 | -0.032173 | 0.20941 | 0.43729 | 0.032746 | -0.13437 | -0.35739 | 134.9881 | -154.0648 | 21.3437 | -45.0119 | 25.9352 | -158.6563 | 1.1505 | 1.0392 | 0.966 | 1.1662 | 0.89577 | 0.82181 | 0.65631 | -127.292 | 122.6272 | 0.90203 | -134.4741 | 130.9352
Line10_11_12 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.002648 | -0.026745 | 0.00011666 | 0.0027486 | 0.027058 | 0.00026429 | -0.026938 | -0.0347 | -0.045057 | 0.027139 | 0.035325 | 0.045819 | 95.9246 | 0.69354 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1687 | 1.0728 | 0.99962 | 1.1777 | 1.0896 | 1.0165 | 0.31048 | -126.9299 | 121.6194 | 0.14155 | -126.7572 | 121.1406
Line11_12_13 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.0027486 | -0.027058 | -0.00026429 | 0.0028492 | 0.02737 | 0.00064524 | -0.027139 | -0.035325 | -0.045819 | 0.02734 | 0.03595 | 0.046581 | 95.9246 | 0.69354 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1777 | 1.0896 | 1.0165 | 1.1868 | 1.1064 | 1.0335 | 0.14155 | -126.7572 | 121.1406 | -0.024784 | -126.5897 | 120.6775
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1334e-09 | 1.6651e-10 | -7.5494e-10 | -1.1334e-09 | -1.6651e-10 | 7.5494e-10 | 6.2117e-12 | 1.5364e-09 | -1.4786e-10 | -6.2119e-12 | -1.5364e-09 | 1.4786e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1868 | 1.1064 | 1.0335 | 1.1868 | 1.1064 | 1.0335 | -0.024784 | -126.5897 | 120.6775 | -0.024784 | -126.5897 | 120.6775
Line13_13_14 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.0028492 | -0.02737 | -0.00064524 | 0.0029497 | 0.027683 | 0.0010262 | -0.02734 | -0.03595 | -0.046581 | 0.027542 | 0.036576 | 0.047343 | 95.9246 | 0.69354 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1868 | 1.1064 | 1.0335 | 1.1959 | 1.1232 | 1.0506 | -0.024784 | -126.5897 | 120.6775 | -0.18859 | -126.4273 | 120.2293
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5561e-10 | 1.1101e-10 | -5.0329e-10 | -7.5561e-10 | -1.1101e-10 | 5.0329e-10 | 4.141e-12 | 1.0242e-09 | -9.8573e-11 | -4.1411e-12 | -1.0242e-09 | 9.8573e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1868 | 1.1064 | 1.0335 | 1.1868 | 1.1064 | 1.0335 | -0.024784 | -126.5897 | 120.6775 | -0.024784 | -126.5897 | 120.6775
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.778e-10 | 5.5505e-11 | -2.5165e-10 | -3.778e-10 | -5.5505e-11 | 2.5165e-10 | 2.0704e-12 | 5.1212e-10 | -4.9287e-11 | -2.0705e-12 | -5.1212e-10 | 4.9287e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1868 | 1.1064 | 1.0335 | 1.1868 | 1.1064 | 1.0335 | -0.024784 | -126.5897 | 120.6775 | -0.024784 | -126.5897 | 120.6775
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6579e-10 | -1.1923e-10 | -4.0754e-10 | -2.6579e-10 | 1.1923e-10 | 4.0754e-10 | -3.7342e-11 | 5.2823e-10 | -1.3693e-10 | 3.7342e-11 | -5.2823e-10 | 1.3693e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1623 | 1.0609 | 0.9867 | 1.1623 | 1.0609 | 0.9867 | 0.45638 | -127.0909 | 121.9718 | 0.45638 | -127.0909 | 121.9718
Line17_5_19 | 0.12007 | 0.21255 | 0.22897 | 0.12007 | 0.21255 | 0.22897 | 0.02773 | 0.049087 | 0.052878 | 0.02773 | 0.049087 | 0.052878 | -0.0039869 | -0.031003 | 0.0011232 | 0.004131 | 0.031454 | -0.00059893 | -0.031961 | -0.041754 | -0.052103 | 0.032249 | 0.042658 | 0.053151 | 97.574 | -0.50057 | -149.221 | -82.426 | 179.4994 | 30.779 | 1.1615 | 1.0595 | 0.98556 | 1.1725 | 1.0797 | 1.0052 | 0.46348 | -127.0944 | 122.0139 | 0.27425 | -126.9042 | 121.4246
Line1_1_3 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.0024468 | -0.02612 | 0.00087855 | 0.0025474 | 0.026432 | -0.0004976 | -0.026536 | -0.033449 | -0.043533 | 0.026737 | 0.034074 | 0.044295 | 95.9246 | 0.69355 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1505 | 1.0392 | 0.966 | 1.1596 | 1.056 | 0.98277 | 0.65631 | -127.292 | 122.6272 | 0.48204 | -127.1081 | 122.1147
Line2_1_4 | 0.12865 | 0.2277 | 0.24293 | 0.12865 | 0.2277 | 0.24293 | 0.029712 | 0.052586 | 0.056101 | 0.029712 | 0.052586 | 0.056101 | -0.0044998 | -0.032346 | 0.0019949 | 0.0046653 | 0.032864 | -0.0014047 | -0.033887 | -0.044046 | -0.054157 | 0.034218 | 0.045083 | 0.055338 | 98.2202 | -1 | -149.4823 | -81.7798 | 179 | 30.5177 | 1.1505 | 1.0392 | 0.966 | 1.1623 | 1.0609 | 0.9867 | 0.65631 | -127.292 | 122.6272 | 0.45638 | -127.0909 | 121.9718
Line3_1_5 | 0.12007 | 0.21255 | 0.22897 | 0.12007 | 0.21255 | 0.22897 | 0.02773 | 0.049087 | 0.052878 | 0.02773 | 0.049087 | 0.052878 | -0.0038427 | -0.030551 | 0.0016475 | 0.0039869 | 0.031003 | -0.0011232 | -0.031672 | -0.040851 | -0.051054 | 0.031961 | 0.041754 | 0.052103 | 97.574 | -0.50057 | -149.221 | -82.426 | 179.4994 | 30.779 | 1.1505 | 1.0392 | 0.966 | 1.1615 | 1.0595 | 0.98556 | 0.65631 | -127.292 | 122.6272 | 0.46348 | -127.0944 | 122.0139
Line4_2_6 | 0.16928 | 1.9371 | 1.9988 | 0.16928 | 1.9371 | 1.9988 | 0.039093 | 0.44736 | 0.4616 | 0.039093 | 0.44736 | 0.4616 | -0.031718 | 0.37753 | -0.1272 | 0.032005 | -0.34001 | 0.16715 | -0.032746 | 0.13437 | 0.35739 | 0.033319 | -0.059317 | -0.27748 | 134.9881 | -154.0648 | 21.3437 | -45.0119 | 25.9352 | -158.6563 | 1.1662 | 0.89577 | 0.82181 | 1.1818 | 0.77152 | 0.70177 | 0.90203 | -134.4741 | 130.9352 | 1.1413 | -144.1689 | 142.4079
Line5_6_7 | 0.16928 | 1.9371 | 1.9988 | 0.16928 | 1.9371 | 1.9988 | 0.039093 | 0.44736 | 0.4616 | 0.039093 | 0.44736 | 0.4616 | -0.032005 | 0.34001 | -0.16715 | 0.032291 | -0.30249 | 0.2071 | -0.033319 | 0.059317 | 0.27748 | 0.033893 | 0.015732 | -0.19758 | 134.9881 | -154.0648 | 21.3437 | -45.0119 | 25.9352 | -158.6563 | 1.1818 | 0.77152 | 0.70177 | 1.1975 | 0.67707 | 0.62009 | 1.1413 | -144.1689 | 142.4079 | 1.3742 | -157.0421 | 157.6919
Line6_7_8 | 0 | 2.592 | 2.592 | 0 | 2.592 | 2.592 | 0 | 0.5986 | 0.5986 | 0 | 0.5986 | 0.5986 | 1.288e-09 | 0.40503 | -0.27066 | -1.288e-09 | -0.33784 | 0.33784 | -3.4749e-10 | 0.014729 | 0.25402 | 3.4749e-10 | 0.11964 | -0.11964 | 0 | -159.1248 | 20.8752 | 0 | 20.8752 | -159.1248 | 1.1975 | 0.67707 | 0.62009 | 1.1975 | 0.59873 | 0.59873 | 1.3742 | -157.0421 | 157.6919 | 1.3742 | -178.6258 | -178.6258
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2932e-10 | 5.7175e-11 | 1.5749e-10 | -4.2932e-10 | -5.7175e-11 | -1.5749e-10 | -1.1583e-10 | 2.0618e-09 | -2.1197e-09 | 1.1583e-10 | -2.0618e-09 | 2.1197e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1975 | 0.59873 | 0.59873 | 1.1975 | 0.59873 | 0.59873 | 1.3742 | -178.6258 | -178.6258 | 1.3742 | -178.6258 | -178.6258
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2932e-10 | 5.7175e-11 | 1.5749e-10 | -4.2932e-10 | -5.7175e-11 | -1.5749e-10 | -1.1583e-10 | 2.0618e-09 | -2.1197e-09 | 1.1583e-10 | -2.0618e-09 | 2.1197e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1975 | 0.59873 | 0.59873 | 1.1975 | 0.59873 | 0.59873 | 1.3742 | -178.6258 | -178.6258 | 1.3742 | -178.6258 | -178.6258
Line9_3_11 | 0.10029 | 0.17683 | 0.19518 | 0.10029 | 0.17683 | 0.19518 | 0.023161 | 0.040838 | 0.045075 | 0.023161 | 0.040838 | 0.045075 | -0.0025474 | -0.026432 | 0.0004976 | 0.002648 | 0.026745 | -0.00011665 | -0.026737 | -0.034074 | -0.044295 | 0.026938 | 0.0347 | 0.045057 | 95.9246 | 0.69354 | -148.5289 | -84.0754 | -179.3065 | 31.4711 | 1.1596 | 1.056 | 0.98277 | 1.1687 | 1.0728 | 0.99962 | 0.48204 | -127.1081 | 122.1147 | 0.31048 | -126.9299 | 121.6194

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11237 | 0.092717 | 0.062508 | 0.11237 | 0.092717 | 0.062508 | 0.025952 | 0.021412 | 0.014436 | 0.025952 | 0.021412 | 0.014436 | -0.01163 | 0.00075754 | -0.0075445 | 0.011757 | -0.00067158 | 0.0075836 | -0.025955 | -0.023429 | -0.013837 | 0.026207 | 0.023601 | 0.013915 | 114.2477 | -31.9579 | -121.3437 | -65.7523 | 148.0421 | 58.6563 | 1.0959 | 1.0948 | 1.0918 | 1.1068 | 1.1027 | 1.0978 | 0.11027 | -120.1059 | 120.0555 | 0.086415 | -120.3279 | 120.0667
Line10_11_12 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.00093367 | -0.0015952 | -0.001165 | 0.0010354 | 0.0016978 | 0.0012711 | -0.025924 | -0.025989 | -0.026377 | 0.026128 | 0.026194 | 0.026589 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.1137 | 1.1128 | 1.1099 | 1.1226 | 1.1218 | 1.1191 | -0.31323 | -120.508 | 119.6291 | -0.51995 | -120.7042 | 119.4212
Line11_12_13 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.0010354 | -0.0016978 | -0.0012711 | 0.0011371 | 0.0018005 | 0.0013771 | -0.026128 | -0.026194 | -0.026589 | 0.026331 | 0.026399 | 0.026802 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.1226 | 1.1218 | 1.1191 | 1.1315 | 1.1309 | 1.1282 | -0.51995 | -120.7042 | 119.4212 | -0.72342 | -120.8973 | 119.2165
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0151e-09 | 1.0075e-09 | 9.7164e-10 | -1.0151e-09 | -1.0075e-09 | -9.7164e-10 | 1.65e-10 | 2.0454e-10 | 1.7818e-10 | -1.65e-10 | -2.0454e-10 | -1.7818e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1315 | 1.1309 | 1.1282 | 1.1315 | 1.1309 | 1.1282 | -0.72342 | -120.8973 | 119.2165 | -0.72342 | -120.8973 | 119.2165
Line13_13_14 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.0011371 | -0.0018005 | -0.0013771 | 0.0012389 | 0.0019031 | 0.0014832 | -0.026331 | -0.026399 | -0.026802 | 0.026534 | 0.026605 | 0.027014 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.1315 | 1.1309 | 1.1282 | 1.1404 | 1.1399 | 1.1373 | -0.72342 | -120.8973 | 119.2165 | -0.92372 | -121.0873 | 119.0152
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7674e-10 | 6.7168e-10 | 6.4776e-10 | -6.7674e-10 | -6.7168e-10 | -6.4776e-10 | 1.1e-10 | 1.3636e-10 | 1.1878e-10 | -1.1e-10 | -1.3636e-10 | -1.1878e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1315 | 1.1309 | 1.1282 | 1.1315 | 1.1309 | 1.1282 | -0.72342 | -120.8973 | 119.2165 | -0.72342 | -120.8973 | 119.2165
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3837e-10 | 3.3584e-10 | 3.2388e-10 | -3.3837e-10 | -3.3584e-10 | -3.2388e-10 | 5.5e-11 | 6.8181e-11 | 5.9392e-11 | -5.5e-11 | -6.8181e-11 | -5.9392e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1315 | 1.1309 | 1.1282 | 1.1315 | 1.1309 | 1.1282 | -0.72342 | -120.8973 | 119.2165 | -0.72342 | -120.8973 | 119.2165
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3262e-10 | 2.2851e-10 | 2.1605e-10 | -2.3262e-10 | -2.2851e-10 | -2.1605e-10 | 1.1596e-11 | 2.6722e-11 | 1.5838e-11 | -1.1596e-11 | -2.6722e-11 | -1.5838e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1073 | 1.1063 | 1.1034 | 1.1073 | 1.1063 | 1.1034 | -0.15585 | -120.3595 | 119.7864 | -0.15585 | -120.3595 | 119.7864
Line17_5_19 | 0.12038 | 0.12109 | 0.12293 | 0.12038 | 0.12109 | 0.12293 | 0.027801 | 0.027964 | 0.028389 | 0.027801 | 0.027964 | 0.028389 | -0.0012192 | -0.0019844 | -0.0014462 | 0.0013641 | 0.0021311 | 0.0015974 | -0.030739 | -0.030852 | -0.03127 | 0.031029 | 0.031145 | 0.031572 | 92.1308 | -26.6643 | -147.5496 | -87.8692 | 153.3357 | 32.4504 | 1.1065 | 1.1056 | 1.1026 | 1.1172 | 1.1164 | 1.1135 | -0.14044 | -120.3445 | 119.8023 | -0.38638 | -120.5786 | 119.554
Line1_1_3 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.00073021 | -0.0013899 | -0.00095276 | 0.00083194 | 0.0014925 | 0.0010589 | -0.025517 | -0.025578 | -0.025953 | 0.025721 | 0.025784 | 0.026165 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.0959 | 1.0948 | 1.0918 | 1.1048 | 1.1038 | 1.1008 | 0.11027 | -120.1059 | 120.0555 | -0.10318 | -120.3086 | 119.8406
Line2_1_4 | 0.12867 | 0.12949 | 0.13138 | 0.12867 | 0.12949 | 0.13138 | 0.029716 | 0.029905 | 0.030342 | 0.029716 | 0.029905 | 0.030342 | -0.0012413 | -0.0020456 | -0.0014578 | 0.0014068 | 0.0022133 | 0.0016304 | -0.032543 | -0.032675 | -0.033094 | 0.032874 | 0.03301 | 0.033439 | 92.2946 | -26.5236 | -147.4222 | -87.7054 | 153.4764 | 32.5778 | 1.0959 | 1.0948 | 1.0918 | 1.1073 | 1.1063 | 1.1034 | 0.11027 | -120.1059 | 120.0555 | -0.15585 | -120.3595 | 119.7864
Line3_1_5 | 0.12038 | 0.12109 | 0.12293 | 0.12038 | 0.12109 | 0.12293 | 0.027801 | 0.027964 | 0.028389 | 0.027801 | 0.027964 | 0.028389 | -0.0010743 | -0.0018378 | -0.0012951 | 0.0012192 | 0.0019844 | 0.0014462 | -0.03045 | -0.030559 | -0.030968 | 0.030739 | 0.030852 | 0.03127 | 92.1308 | -26.6643 | -147.5496 | -87.8692 | 153.3357 | 32.4504 | 1.0959 | 1.0948 | 1.0918 | 1.1065 | 1.1056 | 1.1026 | 0.11027 | -120.1059 | 120.0555 | -0.14044 | -120.3445 | 119.8023
Line4_2_6 | 0.11237 | 0.092717 | 0.062508 | 0.11237 | 0.092717 | 0.062508 | 0.025952 | 0.021412 | 0.014436 | 0.025952 | 0.021412 | 0.014436 | -0.011757 | 0.00067158 | -0.0075836 | 0.011883 | -0.00058561 | 0.0076226 | -0.026207 | -0.023601 | -0.013915 | 0.02646 | 0.023773 | 0.013993 | 114.2477 | -31.9579 | -121.3437 | -65.7523 | 148.0421 | 58.6563 | 1.1068 | 1.1027 | 1.0978 | 1.1177 | 1.1106 | 1.1039 | 0.086415 | -120.3279 | 120.0667 | 0.063021 | -120.5467 | 120.0778
Line5_6_7 | 0.11237 | 0.092717 | 0.062508 | 0.11237 | 0.092717 | 0.062508 | 0.025952 | 0.021412 | 0.014436 | 0.025952 | 0.021412 | 0.014436 | -0.011883 | 0.00058561 | -0.0076226 | 0.012009 | -0.00049965 | 0.0076617 | -0.02646 | -0.023773 | -0.013993 | 0.026712 | 0.023945 | 0.014072 | 114.2477 | -31.9579 | -121.3437 | -65.7523 | 148.0421 | 58.6563 | 1.1177 | 1.1106 | 1.1039 | 1.1285 | 1.1185 | 1.1099 | 0.063021 | -120.5467 | 120.0778 | 0.040078 | -120.7625 | 120.0888
Line6_7_8 | 0 | 0.062383 | 0.062383 | 0 | 0.062383 | 0.062383 | 0 | 0.014407 | 0.014407 | 0 | 0.014407 | 0.014407 | 9.7505e-10 | 0.015578 | 0.0039578 | -9.7505e-10 | -0.015539 | -0.0039189 | -9.1178e-12 | 0.0041213 | 0.015493 | 9.1177e-12 | -0.0040434 | -0.015415 | 0 | -135.5807 | 44.4193 | 0 | 44.4193 | -135.5807 | 1.1285 | 1.1185 | 1.1099 | 1.1285 | 1.1145 | 1.104 | 0.040078 | -120.7625 | 120.0888 | 0.040078 | -120.9954 | 120.1552
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2502e-10 | 2.6438e-10 | 2.1864e-10 | -3.2502e-10 | -2.6438e-10 | -2.1864e-10 | -3.0392e-12 | 7.4546e-11 | -1.1517e-11 | 3.0391e-12 | -7.4546e-11 | 1.1517e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1285 | 1.1145 | 1.104 | 1.1285 | 1.1145 | 1.104 | 0.040078 | -120.9954 | 120.1552 | 0.040078 | -120.9954 | 120.1552
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2502e-10 | 2.6438e-10 | 2.1864e-10 | -3.2502e-10 | -2.6438e-10 | -2.1864e-10 | -3.0392e-12 | 7.4546e-11 | -1.1517e-11 | 3.0392e-12 | -7.4546e-11 | 1.1517e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1285 | 1.1145 | 1.104 | 1.1285 | 1.1145 | 1.104 | 0.040078 | -120.9954 | 120.1552 | 0.040078 | -120.9954 | 120.1552
Line9_3_11 | 0.10086 | 0.10132 | 0.103 | 0.10086 | 0.10132 | 0.103 | 0.023293 | 0.023399 | 0.023787 | 0.023293 | 0.023399 | 0.023787 | -0.00083194 | -0.0014925 | -0.0010589 | 0.00093367 | 0.0015952 | 0.001165 | -0.025721 | -0.025784 | -0.026165 | 0.025924 | 0.025989 | 0.026377 | 91.7494 | -26.9957 | -147.842 | -88.2506 | 153.0043 | 32.158 | 1.1048 | 1.1038 | 1.1008 | 1.1137 | 1.1128 | 1.1099 | -0.10318 | -120.3086 | 119.8406 | -0.31323 | -120.508 | 119.6291

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11316 | 0.093008 | 0.060636 | 0.11316 | 0.093008 | 0.060636 | 0.026132 | 0.021479 | 0.014003 | 0.026132 | 0.021479 | 0.014003 | -0.012193 | 0.0014746 | -0.0077217 | 0.012321 | -0.0013881 | 0.0077584 | -0.027421 | -0.024594 | -0.014033 | 0.027678 | 0.024767 | 0.014106 | 114.0837 | -33.5464 | -121.1225 | -65.9163 | 146.4536 | 58.8775 | 1.1484 | 1.1471 | 1.1438 | 1.1593 | 1.1549 | 1.1497 | 0.1121 | -120.1152 | 120.0551 | 0.087596 | -120.3386 | 120.0666
Line10_11_12 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.0010212 | -0.0017578 | -0.0012743 | 0.0011252 | 0.0018628 | 0.001383 | -0.027445 | -0.027521 | -0.027951 | 0.027653 | 0.027731 | 0.028168 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1663 | 1.1653 | 1.1622 | 1.1753 | 1.1745 | 1.1714 | -0.2954 | -120.501 | 119.6445 | -0.49447 | -120.6895 | 119.4441
Line11_12_13 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.0011252 | -0.0018628 | -0.001383 | 0.0012292 | 0.0019678 | 0.0014917 | -0.027653 | -0.027731 | -0.028168 | 0.027861 | 0.027941 | 0.028385 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1753 | 1.1745 | 1.1714 | 1.1843 | 1.1836 | 1.1807 | -0.49447 | -120.6895 | 119.4441 | -0.69052 | -120.875 | 119.2468
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0998e-09 | 1.0906e-09 | 1.0491e-09 | -1.0998e-09 | -1.0906e-09 | -1.0491e-09 | 1.7271e-10 | 2.1871e-10 | 1.8781e-10 | -1.7271e-10 | -2.1871e-10 | -1.8781e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1843 | 1.1836 | 1.1807 | 1.1843 | 1.1836 | 1.1807 | -0.69052 | -120.875 | 119.2468 | -0.69052 | -120.875 | 119.2468
Line13_13_14 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.0012292 | -0.0019678 | -0.0014917 | 0.0013331 | 0.0020728 | 0.0016003 | -0.027861 | -0.027941 | -0.028385 | 0.028069 | 0.028151 | 0.028603 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1843 | 1.1836 | 1.1807 | 1.1934 | 1.1928 | 1.1899 | -0.69052 | -120.875 | 119.2468 | -0.88361 | -121.0576 | 119.0525
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3318e-10 | 7.2708e-10 | 6.9942e-10 | -7.3318e-10 | -7.2708e-10 | -6.9942e-10 | 1.1514e-10 | 1.458e-10 | 1.2521e-10 | -1.1514e-10 | -1.458e-10 | -1.2521e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1843 | 1.1836 | 1.1807 | 1.1843 | 1.1836 | 1.1807 | -0.69052 | -120.875 | 119.2468 | -0.69052 | -120.875 | 119.2468
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6659e-10 | 3.6354e-10 | 3.4971e-10 | -3.6659e-10 | -3.6354e-10 | -3.4971e-10 | 5.7568e-11 | 7.2902e-11 | 6.2603e-11 | -5.7568e-11 | -7.2902e-11 | -6.2603e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1843 | 1.1836 | 1.1807 | 1.1843 | 1.1836 | 1.1807 | -0.69052 | -120.875 | 119.2468 | -0.69052 | -120.875 | 119.2468
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5418e-10 | 2.4935e-10 | 2.3498e-10 | -2.5418e-10 | -2.4935e-10 | -2.3498e-10 | 1.1565e-11 | 2.9063e-11 | 1.6411e-11 | -1.1565e-11 | -2.9063e-11 | -1.6411e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1598 | 1.1587 | 1.1555 | 1.1598 | 1.1587 | 1.1555 | -0.14166 | -120.3563 | 119.7982 | -0.14166 | -120.3563 | 119.7982
Line17_5_19 | 0.12091 | 0.12167 | 0.12361 | 0.12091 | 0.12167 | 0.12361 | 0.027923 | 0.028099 | 0.028545 | 0.027923 | 0.028099 | 0.028545 | -0.0013206 | -0.0021675 | -0.001568 | 0.0014668 | 0.0023155 | 0.0017208 | -0.032337 | -0.032464 | -0.032925 | 0.032629 | 0.032761 | 0.03323 | 92.211 | -26.523 | -147.4607 | -87.789 | 153.477 | 32.5393 | 1.1591 | 1.1579 | 1.1547 | 1.1697 | 1.1688 | 1.1657 | -0.12758 | -120.3427 | 119.8128 | -0.36288 | -120.566 | 119.575
Line1_1_3 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.0008133 | -0.0015478 | -0.001057 | 0.00091726 | 0.0016528 | 0.0011657 | -0.027029 | -0.027101 | -0.027516 | 0.027237 | 0.027311 | 0.027733 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1484 | 1.1471 | 1.1438 | 1.1574 | 1.1562 | 1.153 | 0.1121 | -120.1152 | 120.0551 | -0.09323 | -120.3096 | 119.8482
Line2_1_4 | 0.12888 | 0.12976 | 0.13174 | 0.12888 | 0.12976 | 0.13174 | 0.029763 | 0.029967 | 0.030425 | 0.029763 | 0.029967 | 0.030425 | -0.0013469 | -0.0022351 | -0.0015829 | 0.001513 | 0.0024035 | 0.0017565 | -0.034153 | -0.034302 | -0.034763 | 0.034486 | 0.034638 | 0.035111 | 92.3706 | -26.387 | -147.3378 | -87.6294 | 153.613 | 32.6622 | 1.1484 | 1.1471 | 1.1438 | 1.1598 | 1.1587 | 1.1555 | 0.1121 | -120.1152 | 120.0551 | -0.14166 | -120.3563 | 119.7982
Line3_1_5 | 0.12091 | 0.12167 | 0.12361 | 0.12091 | 0.12167 | 0.12361 | 0.027923 | 0.028099 | 0.028545 | 0.027923 | 0.028099 | 0.028545 | -0.0011744 | -0.0020195 | -0.0014152 | 0.0013206 | 0.0021675 | 0.001568 | -0.032044 | -0.032168 | -0.032619 | 0.032337 | 0.032464 | 0.032925 | 92.211 | -26.523 | -147.4607 | -87.789 | 153.477 | 32.5393 | 1.1484 | 1.1471 | 1.1438 | 1.1591 | 1.1579 | 1.1547 | 0.1121 | -120.1152 | 120.0551 | -0.12758 | -120.3427 | 119.8128
Line4_2_6 | 0.11316 | 0.093008 | 0.060636 | 0.11316 | 0.093008 | 0.060636 | 0.026132 | 0.021479 | 0.014003 | 0.026132 | 0.021479 | 0.014003 | -0.012321 | 0.0013881 | -0.0077584 | 0.012449 | -0.0013016 | 0.0077952 | -0.027678 | -0.024767 | -0.014106 | 0.027934 | 0.02494 | 0.01418 | 114.0837 | -33.5464 | -121.1225 | -65.9163 | 146.4536 | 58.8775 | 1.1593 | 1.1549 | 1.1497 | 1.1703 | 1.1627 | 1.1555 | 0.087596 | -120.3386 | 120.0666 | 0.063553 | -120.5589 | 120.078
Line5_6_7 | 0.11316 | 0.093008 | 0.060636 | 0.11316 | 0.093008 | 0.060636 | 0.026132 | 0.021479 | 0.014003 | 0.026132 | 0.021479 | 0.014003 | -0.012449 | 0.0013016 | -0.0077952 | 0.012577 | -0.0012151 | 0.007832 | -0.027934 | -0.02494 | -0.01418 | 0.02819 | 0.025113 | 0.014253 | 114.0837 | -33.5464 | -121.1225 | -65.9163 | 146.4536 | 58.8775 | 1.1703 | 1.1627 | 1.1555 | 1.1812 | 1.1706 | 1.1614 | 0.063553 | -120.5589 | 120.078 | 0.039956 | -120.7763 | 120.0893
Line6_7_8 | 0 | 0.065276 | 0.065276 | 0 | 0.065276 | 0.065276 | 0 | 0.015075 | 0.015075 | 0 | 0.015075 | 0.015075 | 1.0554e-09 | 0.01706 | 0.0043306 | -1.0554e-09 | -0.017017 | -0.004288 | -9.9674e-12 | 0.0045116 | 0.016964 | 9.9674e-12 | -0.0044264 | -0.016879 | 0 | -135.5898 | 44.4102 | 0 | 44.4102 | -135.5898 | 1.1812 | 1.1706 | 1.1614 | 1.1812 | 1.1664 | 1.1552 | 0.039956 | -120.7763 | 120.0893 | 0.039956 | -121.0093 | 120.1558
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5179e-10 | 2.8466e-10 | 2.3389e-10 | -3.5179e-10 | -2.8466e-10 | -2.3389e-10 | -3.3224e-12 | 8.2867e-11 | -1.2669e-11 | 3.3224e-12 | -8.2867e-11 | 1.2669e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 1.1664 | 1.1552 | 1.1812 | 1.1664 | 1.1552 | 0.039956 | -121.0093 | 120.1558 | 0.039956 | -121.0093 | 120.1558
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5179e-10 | 2.8466e-10 | 2.3389e-10 | -3.5179e-10 | -2.8466e-10 | -2.3389e-10 | -3.3225e-12 | 8.2867e-11 | -1.2669e-11 | 3.3225e-12 | -8.2867e-11 | 1.2669e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1812 | 1.1664 | 1.1552 | 1.1812 | 1.1664 | 1.1552 | 0.039956 | -121.0093 | 120.1558 | 0.039956 | -121.0093 | 120.1558
Line9_3_11 | 0.10196 | 0.10247 | 0.10425 | 0.10196 | 0.10247 | 0.10425 | 0.023547 | 0.023664 | 0.024075 | 0.023547 | 0.023664 | 0.024075 | -0.00091726 | -0.0016528 | -0.0011657 | 0.0010212 | 0.0017578 | 0.0012743 | -0.027237 | -0.027311 | -0.027733 | 0.027445 | 0.027521 | 0.027951 | 91.8356 | -26.8464 | -147.7451 | -88.1644 | 153.1536 | 32.2549 | 1.1574 | 1.1562 | 1.153 | 1.1663 | 1.1653 | 1.1622 | -0.09323 | -120.3096 | 119.8482 | -0.2954 | -120.501 | 119.6445

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.001827 | 1.4537 | 1.4548 | 0.001827 | 1.4537 | 1.4548 | 0.00042193 | 0.33571 | 0.33598 | 0.00042193 | 0.33571 | 0.33598 | -0.00038935 | 0.28982 | 0.035582 | 0.00038941 | -0.24924 | 0.0050549 | -9.5328e-05 | 0.072735 | 0.26586 | 9.5394e-05 | -0.030471 | -0.22353 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.95003 | 0.89006 | 0.79836 | 0.95022 | 0.74796 | 0.66549 | 0.018766 | -128.6808 | 119.5518 | 0.025854 | -135.7991 | 128.4703
Line10_11_12 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7758e-05 | -0.00050213 | -9.6592e-05 | 8.7761e-05 | 0.00050225 | 9.6678e-05 | 2.7522e-05 | -0.00010438 | -0.00037734 | -2.7519e-05 | 0.00010451 | 0.00037743 | -162.5636 | 39.5976 | -136.1076 | 17.4364 | -140.4024 | 43.8924 | 0.95008 | 0.89055 | 0.79881 | 0.9501 | 0.8908 | 0.79903 | 0.024202 | -128.659 | 119.5339 | 0.026919 | -128.6481 | 119.525
Line11_12_13 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7761e-05 | -0.00050225 | -9.6678e-05 | 8.7765e-05 | 0.00050237 | 9.6763e-05 | 2.7519e-05 | -0.00010451 | -0.00037743 | -2.7515e-05 | 0.00010463 | 0.00037752 | -162.5636 | 39.5975 | -136.1077 | 17.4364 | -140.4025 | 43.8923 | 0.9501 | 0.8908 | 0.79903 | 0.95012 | 0.89105 | 0.79925 | 0.026919 | -128.6481 | 119.525 | 0.029637 | -128.6372 | 119.516
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2766e-12 | -4.7222e-10 | -1.3251e-09 | -1.2766e-12 | 4.7222e-10 | 1.3251e-09 | -5.1358e-12 | 1.3984e-09 | 7.0549e-11 | 5.1358e-12 | -1.3984e-09 | -7.0549e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95012 | 0.89105 | 0.79925 | 0.95012 | 0.89105 | 0.79925 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line13_13_14 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7765e-05 | -0.00050237 | -9.6761e-05 | 8.7768e-05 | 0.00050249 | 9.6847e-05 | 2.7515e-05 | -0.00010463 | -0.00037752 | -2.7512e-05 | 0.00010476 | 0.00037761 | -162.5636 | 39.5973 | -136.1079 | 17.4364 | -140.4027 | 43.8921 | 0.95012 | 0.89105 | 0.79925 | 0.95014 | 0.89129 | 0.79947 | 0.029637 | -128.6372 | 119.516 | 0.032355 | -128.6264 | 119.5071
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5106e-13 | -3.1481e-10 | -8.8338e-10 | -8.5106e-13 | 3.1481e-10 | 8.8338e-10 | -3.4238e-12 | 9.3225e-10 | 4.7033e-11 | 3.4238e-12 | -9.3225e-10 | -4.7033e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95012 | 0.89105 | 0.79925 | 0.95012 | 0.89105 | 0.79925 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2555e-13 | -1.5741e-10 | -4.4169e-10 | -4.2554e-13 | 1.5741e-10 | 4.4169e-10 | -1.7119e-12 | 4.6612e-10 | 2.3516e-11 | 1.7119e-12 | -4.6612e-10 | -2.3516e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95012 | 0.89105 | 0.79925 | 0.95012 | 0.89105 | 0.79925 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9358e-13 | -1.5942e-10 | -4.4327e-10 | -1.9357e-13 | 1.5942e-10 | 4.4327e-10 | -1.2421e-12 | 4.6749e-10 | 2.2199e-11 | 1.2421e-12 | -4.6749e-10 | -2.2199e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95006 | 0.89031 | 0.79859 | 0.95006 | 0.89031 | 0.79859 | 0.021505 | -128.6699 | 119.5428 | 0.021505 | -128.6699 | 119.5428
Line17_5_19 | 0.00042299 | 0.0025055 | 0.0021203 | 0.00042299 | 0.0025055 | 0.0021203 | 9.7685e-05 | 0.00057863 | 0.00048967 | 9.7685e-05 | 0.00057863 | 0.00048967 | -8.8725e-05 | -0.00050403 | -9.5972e-05 | 8.8728e-05 | 0.00050416 | 9.6058e-05 | 2.7219e-05 | -0.00010646 | -0.00037909 | -2.7215e-05 | 0.00010659 | 0.00037918 | -162.9238 | 39.4034 | -136.2503 | 17.0762 | -140.5966 | 43.7497 | 0.95006 | 0.89031 | 0.79859 | 0.95008 | 0.89056 | 0.79881 | 0.0215 | -128.6699 | 119.5428 | 0.024234 | -128.659 | 119.5338
Line1_1_3 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7751e-05 | -0.00050189 | -9.6422e-05 | 8.7755e-05 | 0.00050201 | 9.6508e-05 | 2.7529e-05 | -0.00010413 | -0.00037716 | -2.7526e-05 | 0.00010426 | 0.00037725 | -162.5636 | 39.5977 | -136.1075 | 17.4364 | -140.4023 | 43.8925 | 0.95003 | 0.89006 | 0.79836 | 0.95005 | 0.89031 | 0.79859 | 0.018766 | -128.6808 | 119.5518 | 0.021484 | -128.6699 | 119.5429
Line2_1_4 | 0.00042427 | 0.0025095 | 0.0021233 | 0.00042427 | 0.0025095 | 0.0021233 | 9.798e-05 | 0.00057954 | 0.00049036 | 9.798e-05 | 0.00057954 | 0.00049036 | -8.9047e-05 | -0.00050459 | -9.5706e-05 | 8.905e-05 | 0.00050471 | 9.5792e-05 | 2.7117e-05 | -0.00010708 | -0.00037961 | -2.7113e-05 | 0.0001072 | 0.0003797 | -163.0445 | 39.3384 | -136.2979 | 16.9555 | -140.6616 | 43.7021 | 0.95003 | 0.89006 | 0.79836 | 0.95006 | 0.89031 | 0.79859 | 0.018766 | -128.6808 | 119.5518 | 0.021505 | -128.6699 | 119.5428
Line3_1_5 | 0.00042299 | 0.0025055 | 0.0021203 | 0.00042299 | 0.0025055 | 0.0021203 | 9.7685e-05 | 0.00057863 | 0.00048967 | 9.7685e-05 | 0.00057863 | 0.00048967 | -8.8721e-05 | -0.00050391 | -9.5886e-05 | 8.8725e-05 | 0.00050403 | 9.5973e-05 | 2.7222e-05 | -0.00010634 | -0.000379 | -2.7219e-05 | 0.00010646 | 0.00037909 | -162.9238 | 39.4034 | -136.2502 | 17.0762 | -140.5966 | 43.7498 | 0.95003 | 0.89006 | 0.79836 | 0.95006 | 0.89031 | 0.79859 | 0.018766 | -128.6808 | 119.5518 | 0.0215 | -128.6699 | 119.5428
Line4_2_6 | 0.001827 | 1.4537 | 1.4548 | 0.001827 | 1.4537 | 1.4548 | 0.00042193 | 0.33571 | 0.33598 | 0.00042193 | 0.33571 | 0.33598 | -0.00038941 | 0.24924 | -0.0050549 | 0.00038948 | -0.20867 | 0.045692 | -9.5394e-05 | 0.030471 | 0.22353 | 9.5461e-05 | 0.011792 | -0.1812 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.95022 | 0.74796 | 0.66549 | 0.9504 | 0.62257 | 0.55621 | 0.025854 | -135.7991 | 128.4703 | 0.03294 | -146.0036 | 141.3276
Line5_6_7 | 0.001827 | 1.4537 | 1.4548 | 0.001827 | 1.4537 | 1.4548 | 0.00042193 | 0.33571 | 0.33598 | 0.00042193 | 0.33571 | 0.33598 | -0.00038948 | 0.20867 | -0.045692 | 0.00038954 | -0.1681 | 0.086329 | -9.5461e-05 | -0.011792 | 0.1812 | 9.5528e-05 | 0.054055 | -0.13887 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.9504 | 0.62257 | 0.55621 | 0.95059 | 0.52597 | 0.48669 | 0.03294 | -146.0036 | 141.3276 | 0.040023 | -160.5956 | 159.042
Line6_7_8 | 0 | 1.4631 | 1.4631 | 0 | 1.4631 | 1.4631 | 0 | 0.3379 | 0.3379 | 0 | 0.3379 | 0.3379 | 6.1511e-12 | 0.16938 | -0.087176 | -6.1512e-12 | -0.12828 | 0.12828 | -6.939e-12 | -0.053813 | 0.13944 | 6.9389e-12 | 0.096628 | -0.096628 | 0 | -142.9703 | 37.0297 | 0 | 37.0297 | -142.9703 | 0.95059 | 0.52597 | 0.48669 | 0.95059 | 0.47529 | 0.47529 | 0.040023 | -160.5956 | 159.042 | 0.040023 | -179.96 | -179.96
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0505e-12 | -4.891e-13 | 1.5139e-12 | -2.0504e-12 | 4.8889e-13 | -1.514e-12 | -2.3131e-12 | 1.4332e-09 | -1.4344e-09 | 2.313e-12 | -1.4332e-09 | 1.4344e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95059 | 0.47529 | 0.47529 | 0.95059 | 0.47529 | 0.47529 | 0.040023 | -179.96 | -179.96 | 0.040023 | -179.96 | -179.96
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0504e-12 | -4.8921e-13 | 1.514e-12 | -2.0504e-12 | 4.8917e-13 | -1.514e-12 | -2.3131e-12 | 1.4332e-09 | -1.4344e-09 | 2.313e-12 | -1.4332e-09 | 1.4344e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95059 | 0.47529 | 0.47529 | 0.95059 | 0.47529 | 0.47529 | 0.040023 | -179.96 | -179.96 | 0.040023 | -179.96 | -179.96
Line9_3_11 | 0.00041918 | 0.0024937 | 0.0021114 | 0.00041918 | 0.0024937 | 0.0021114 | 9.6805e-05 | 0.00057589 | 0.00048761 | 9.6805e-05 | 0.00057589 | 0.00048761 | -8.7755e-05 | -0.00050201 | -9.6507e-05 | 8.7758e-05 | 0.00050213 | 9.6593e-05 | 2.7526e-05 | -0.00010426 | -0.00037725 | -2.7522e-05 | 0.00010438 | 0.00037734 | -162.5636 | 39.5976 | -136.1075 | 17.4364 | -140.4024 | 43.8925 | 0.95005 | 0.89031 | 0.79859 | 0.95008 | 0.89055 | 0.79881 | 0.021484 | -128.6699 | 119.5429 | 0.024202 | -128.659 | 119.5339

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0017309 | 1.3772 | 1.3783 | 0.0017309 | 1.3772 | 1.3783 | 0.00039972 | 0.31804 | 0.31829 | 0.00039972 | 0.31804 | 0.31829 | -0.00034944 | 0.26011 | 0.031935 | 0.0003495 | -0.2237 | 0.0045368 | -8.5557e-05 | 0.06528 | 0.23861 | 8.5617e-05 | -0.027348 | -0.20062 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.90003 | 0.84321 | 0.75635 | 0.90021 | 0.70859 | 0.63046 | 0.018766 | -128.6808 | 119.5518 | 0.025854 | -135.7991 | 128.4703
Line10_11_12 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.8763e-05 | -0.00045066 | -8.6692e-05 | 7.8767e-05 | 0.00045077 | 8.6769e-05 | 2.4701e-05 | -9.3684e-05 | -0.00033866 | -2.4698e-05 | 9.3796e-05 | 0.00033874 | -162.5636 | 39.5976 | -136.1076 | 17.4364 | -140.4024 | 43.8924 | 0.90007 | 0.84368 | 0.75676 | 0.90009 | 0.84392 | 0.75697 | 0.024202 | -128.659 | 119.5339 | 0.026919 | -128.6481 | 119.525
Line11_12_13 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.8767e-05 | -0.00045077 | -8.6769e-05 | 7.877e-05 | 0.00045088 | 8.6846e-05 | 2.4698e-05 | -9.3796e-05 | -0.00033874 | -2.4695e-05 | 9.3908e-05 | 0.00033882 | -162.5636 | 39.5975 | -136.1077 | 17.4364 | -140.4025 | 43.8923 | 0.90009 | 0.84392 | 0.75697 | 0.90012 | 0.84415 | 0.75718 | 0.026919 | -128.6481 | 119.525 | 0.029637 | -128.6372 | 119.516
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1458e-12 | -4.2382e-10 | -1.1893e-09 | -1.1458e-12 | 4.2382e-10 | 1.1893e-09 | -4.6094e-12 | 1.2551e-09 | 6.3318e-11 | 4.6094e-12 | -1.2551e-09 | -6.3318e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90012 | 0.84415 | 0.75718 | 0.90012 | 0.84415 | 0.75718 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line13_13_14 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.877e-05 | -0.00045088 | -8.6844e-05 | 7.8773e-05 | 0.00045099 | 8.6921e-05 | 2.4695e-05 | -9.391e-05 | -0.00033882 | -2.4692e-05 | 9.4021e-05 | 0.0003389 | -162.5636 | 39.5973 | -136.1079 | 17.4364 | -140.4027 | 43.8921 | 0.90012 | 0.84415 | 0.75718 | 0.90014 | 0.84438 | 0.75739 | 0.029637 | -128.6372 | 119.516 | 0.032355 | -128.6264 | 119.5071
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6382e-13 | -2.8255e-10 | -7.9284e-10 | -7.6382e-13 | 2.8255e-10 | 7.9284e-10 | -3.0729e-12 | 8.367e-10 | 4.2212e-11 | 3.073e-12 | -8.367e-10 | -4.2212e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90012 | 0.84415 | 0.75718 | 0.90012 | 0.84415 | 0.75718 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8191e-13 | -1.4127e-10 | -3.9642e-10 | -3.8192e-13 | 1.4127e-10 | 3.9642e-10 | -1.5364e-12 | 4.1835e-10 | 2.1106e-11 | 1.5364e-12 | -4.1835e-10 | -2.1106e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90012 | 0.84415 | 0.75718 | 0.90012 | 0.84415 | 0.75718 | 0.029637 | -128.6372 | 119.516 | 0.029637 | -128.6372 | 119.516
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7374e-13 | -1.4308e-10 | -3.9784e-10 | -1.7374e-13 | 1.4308e-10 | 3.9784e-10 | -1.1148e-12 | 4.1957e-10 | 1.9924e-11 | 1.1148e-12 | -4.1957e-10 | -1.9924e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90005 | 0.84345 | 0.75656 | 0.90005 | 0.84345 | 0.75656 | 0.021505 | -128.6699 | 119.5428 | 0.021505 | -128.6699 | 119.5428
Line17_5_19 | 0.00040072 | 0.0023737 | 0.0020087 | 0.00040072 | 0.0023737 | 0.0020087 | 9.2543e-05 | 0.00054817 | 0.0004639 | 9.2543e-05 | 0.00054817 | 0.0004639 | -7.9631e-05 | -0.00045237 | -8.6136e-05 | 7.9634e-05 | 0.00045248 | 8.6213e-05 | 2.4429e-05 | -9.5551e-05 | -0.00034023 | -2.4426e-05 | 9.5663e-05 | 0.00034031 | -162.9238 | 39.4034 | -136.2503 | 17.0762 | -140.5966 | 43.7497 | 0.90005 | 0.84345 | 0.75656 | 0.90007 | 0.84369 | 0.75676 | 0.0215 | -128.6699 | 119.5428 | 0.024234 | -128.659 | 119.5338
Line1_1_3 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.8757e-05 | -0.00045045 | -8.654e-05 | 7.876e-05 | 0.00045056 | 8.6616e-05 | 2.4708e-05 | -9.346e-05 | -0.0003385 | -2.4705e-05 | 9.3572e-05 | 0.00033858 | -162.5636 | 39.5977 | -136.1075 | 17.4364 | -140.4023 | 43.8925 | 0.90003 | 0.84321 | 0.75635 | 0.90005 | 0.84345 | 0.75655 | 0.018766 | -128.6808 | 119.5518 | 0.021484 | -128.6699 | 119.5429
Line2_1_4 | 0.00040194 | 0.0023774 | 0.0020116 | 0.00040194 | 0.0023774 | 0.0020116 | 9.2823e-05 | 0.00054904 | 0.00046456 | 9.2823e-05 | 0.00054904 | 0.00046456 | -7.992e-05 | -0.00045287 | -8.5897e-05 | 7.9923e-05 | 0.00045298 | 8.5974e-05 | 2.4337e-05 | -9.6103e-05 | -0.0003407 | -2.4334e-05 | 9.6216e-05 | 0.00034078 | -163.0445 | 39.3384 | -136.2979 | 16.9555 | -140.6616 | 43.7021 | 0.90003 | 0.84321 | 0.75635 | 0.90005 | 0.84345 | 0.75656 | 0.018766 | -128.6808 | 119.5518 | 0.021505 | -128.6699 | 119.5428
Line3_1_5 | 0.00040072 | 0.0023737 | 0.0020087 | 0.00040072 | 0.0023737 | 0.0020087 | 9.2543e-05 | 0.00054817 | 0.0004639 | 9.2543e-05 | 0.00054817 | 0.0004639 | -7.9628e-05 | -0.00045227 | -8.6059e-05 | 7.9631e-05 | 0.00045237 | 8.6136e-05 | 2.4432e-05 | -9.5438e-05 | -0.00034015 | -2.4429e-05 | 9.555e-05 | 0.00034023 | -162.9238 | 39.4034 | -136.2502 | 17.0762 | -140.5966 | 43.7498 | 0.90003 | 0.84321 | 0.75635 | 0.90005 | 0.84345 | 0.75656 | 0.018766 | -128.6808 | 119.5518 | 0.0215 | -128.6699 | 119.5428
Line4_2_6 | 0.0017309 | 1.3772 | 1.3783 | 0.0017309 | 1.3772 | 1.3783 | 0.00039972 | 0.31804 | 0.31829 | 0.00039972 | 0.31804 | 0.31829 | -0.0003495 | 0.2237 | -0.0045368 | 0.00034956 | -0.18728 | 0.041009 | -8.5617e-05 | 0.027348 | 0.20062 | 8.5677e-05 | 0.010583 | -0.16263 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.90021 | 0.70859 | 0.63046 | 0.90038 | 0.5898 | 0.52693 | 0.025854 | -135.7991 | 128.4703 | 0.03294 | -146.0036 | 141.3276
Line5_6_7 | 0.0017309 | 1.3772 | 1.3783 | 0.0017309 | 1.3772 | 1.3783 | 0.00039972 | 0.31804 | 0.31829 | 0.00039972 | 0.31804 | 0.31829 | -0.00034956 | 0.18728 | -0.041009 | 0.00034962 | -0.15087 | 0.077481 | -8.5677e-05 | -0.010583 | 0.16263 | 8.5737e-05 | 0.048515 | -0.12464 | 166.2612 | -142.7693 | 37.1748 | -13.7388 | 37.2307 | -142.8252 | 0.90038 | 0.5898 | 0.52693 | 0.90056 | 0.49829 | 0.46108 | 0.03294 | -146.0036 | 141.3276 | 0.040023 | -160.5956 | 159.042
Line6_7_8 | 0 | 1.3861 | 1.3861 | 0 | 1.3861 | 1.3861 | 0 | 0.32011 | 0.32011 | 0 | 0.32011 | 0.32011 | 5.5208e-12 | 0.15202 | -0.078241 | -5.5207e-12 | -0.11513 | 0.11513 | -6.2278e-12 | -0.048298 | 0.12515 | 6.2278e-12 | 0.086725 | -0.086725 | 0 | -142.9703 | 37.0297 | 0 | 37.0297 | -142.9703 | 0.90056 | 0.49829 | 0.46108 | 0.90056 | 0.45028 | 0.45028 | 0.040023 | -160.5956 | 159.042 | 0.040023 | -179.96 | -179.96
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8403e-12 | -4.388e-13 | 1.3588e-12 | -1.8403e-12 | 4.387e-13 | -1.3588e-12 | -2.0759e-12 | 1.2863e-09 | -1.2874e-09 | 2.0759e-12 | -1.2863e-09 | 1.2874e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90056 | 0.45028 | 0.45028 | 0.90056 | 0.45028 | 0.45028 | 0.040023 | -179.96 | -179.96 | 0.040023 | -179.96 | -179.96
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8401e-12 | -4.3887e-13 | 1.3591e-12 | -1.8402e-12 | 4.3894e-13 | -1.3591e-12 | -2.0759e-12 | 1.2863e-09 | -1.2874e-09 | 2.0759e-12 | -1.2863e-09 | 1.2874e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90056 | 0.45028 | 0.45028 | 0.90056 | 0.45028 | 0.45028 | 0.040023 | -179.96 | -179.96 | 0.040023 | -179.96 | -179.96
Line9_3_11 | 0.00039712 | 0.0023624 | 0.0020003 | 0.00039712 | 0.0023624 | 0.0020003 | 9.171e-05 | 0.00054558 | 0.00046194 | 9.171e-05 | 0.00054558 | 0.00046194 | -7.876e-05 | -0.00045056 | -8.6616e-05 | 7.8763e-05 | 0.00045066 | 8.6693e-05 | 2.4705e-05 | -9.3572e-05 | -0.00033858 | -2.4701e-05 | 9.3684e-05 | 0.00033866 | -162.5636 | 39.5976 | -136.1075 | 17.4364 | -140.4024 | 43.8925 | 0.90005 | 0.84345 | 0.75655 | 0.90007 | 0.84368 | 0.75676 | 0.021484 | -128.6699 | 119.5429 | 0.024202 | -128.659 | 119.5339

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 6.4749e-05 | 0.051518 | 0.051559 | 6.4749e-05 | 0.051518 | 0.051559 | 1.4953e-05 | 0.011898 | 0.011907 | 1.4953e-05 | 0.011898 | 0.011907 | -1.4126e-05 | 0.010908 | 0.0028963 | 1.4127e-05 | -0.010857 | -0.0028452 | -1.4974e-06 | 0.002877 | 0.010869 | 1.4975e-06 | -0.0028239 | -0.010816 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.95 | 0.94819 | 0.9447 | 0.95001 | 0.94291 | 0.93929 | 0.00066837 | -120.3052 | 119.9431 | 0.00097045 | -120.501 | 120.1256
Line10_11_12 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.89e-05 | -6.02e-06 | 2.9509e-06 | 1.8901e-05 | 6.0201e-06 | 1.3838e-06 | -4.1587e-06 | -1.5175e-05 | -1.3838e-06 | 4.1588e-06 | 1.5175e-05 | -154.8748 | 47.2863 | -128.4189 | 25.1252 | -132.7137 | 51.5811 | 0.95 | 0.9482 | 0.94472 | 0.95 | 0.94821 | 0.94473 | 0.00087212 | -120.3045 | 119.9427 | 0.000974 | -120.3041 | 119.9425
Line11_12_13 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.8901e-05 | -6.0201e-06 | 2.9509e-06 | 1.8901e-05 | 6.0202e-06 | 1.3838e-06 | -4.1589e-06 | -1.5175e-05 | -1.3838e-06 | 4.159e-06 | 1.5175e-05 | -154.8748 | 47.2863 | -128.4189 | 25.1252 | -132.7137 | 51.5811 | 0.95 | 0.94821 | 0.94473 | 0.95 | 0.94822 | 0.94474 | 0.000974 | -120.3041 | 119.9425 | 0.0010759 | -120.3038 | 119.9423
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0389e-14 | -1.8402e-11 | -5.469e-11 | -2.0389e-14 | 1.8402e-11 | 5.469e-11 | -1.8641e-13 | 5.2534e-11 | 9.9489e-12 | 1.8642e-13 | -5.2534e-11 | -9.9489e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94822 | 0.94474 | 0.95 | 0.94822 | 0.94474 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line13_13_14 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.8901e-05 | -6.0201e-06 | 2.9509e-06 | 1.8901e-05 | 6.0203e-06 | 1.3838e-06 | -4.1591e-06 | -1.5175e-05 | -1.3838e-06 | 4.1592e-06 | 1.5175e-05 | -154.8748 | 47.2861 | -128.4192 | 25.1252 | -132.7139 | 51.5808 | 0.95 | 0.94822 | 0.94474 | 0.95 | 0.94823 | 0.94475 | 0.0010759 | -120.3038 | 119.9423 | 0.0011778 | -120.3034 | 119.9421
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3592e-14 | -1.2268e-11 | -3.646e-11 | -1.3592e-14 | 1.2268e-11 | 3.646e-11 | -1.2428e-13 | 3.5023e-11 | 6.6326e-12 | 1.2428e-13 | -3.5023e-11 | -6.6326e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94822 | 0.94474 | 0.95 | 0.94822 | 0.94474 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7956e-15 | -6.1338e-12 | -1.823e-11 | -6.7958e-15 | 6.1338e-12 | 1.823e-11 | -6.2138e-14 | 1.7511e-11 | 3.3163e-12 | 6.2138e-14 | -1.7511e-11 | -3.3163e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94822 | 0.94474 | 0.95 | 0.94822 | 0.94474 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.936e-16 | -6.2251e-12 | -1.8316e-11 | -8.9367e-16 | 6.2251e-12 | 1.8316e-11 | -4.4541e-14 | 1.7573e-11 | 3.2809e-12 | 4.454e-14 | -1.7573e-11 | -3.2809e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9482 | 0.94471 | 0.95 | 0.9482 | 0.94471 | 0.00077118 | -120.3048 | 119.9429 | 0.00077118 | -120.3048 | 119.9429
Line17_5_19 | 1.4991e-05 | 8.8796e-05 | 7.5145e-05 | 1.4991e-05 | 8.8796e-05 | 7.5145e-05 | 3.4619e-06 | 2.0506e-05 | 1.7354e-05 | 3.4619e-06 | 2.0506e-05 | 1.7354e-05 | -2.9864e-06 | -1.8976e-05 | -6.0074e-06 | 2.9864e-06 | 1.8976e-05 | 6.0075e-06 | 1.3776e-06 | -4.2426e-06 | -1.5254e-05 | -1.3776e-06 | 4.2428e-06 | 1.5254e-05 | -155.235 | 47.0921 | -128.5615 | 24.765 | -132.9079 | 51.4385 | 0.95 | 0.9482 | 0.94471 | 0.95 | 0.9482 | 0.94472 | 0.00077095 | -120.3048 | 119.9429 | 0.00087353 | -120.3045 | 119.9427
Line1_1_3 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.89e-05 | -6.0198e-06 | 2.9509e-06 | 1.89e-05 | 6.0199e-06 | 1.3838e-06 | -4.1583e-06 | -1.5175e-05 | -1.3838e-06 | 4.1585e-06 | 1.5175e-05 | -154.8748 | 47.2864 | -128.4187 | 25.1252 | -132.7136 | 51.5813 | 0.95 | 0.94819 | 0.9447 | 0.95 | 0.9482 | 0.94471 | 0.00066837 | -120.3052 | 119.9431 | 0.00077024 | -120.3048 | 119.9429
Line2_1_4 | 1.5036e-05 | 8.8936e-05 | 7.5251e-05 | 1.5036e-05 | 8.8936e-05 | 7.5251e-05 | 3.4724e-06 | 2.0539e-05 | 1.7378e-05 | 3.4724e-06 | 2.0539e-05 | 1.7378e-05 | -2.9983e-06 | -1.9001e-05 | -6.0031e-06 | 2.9983e-06 | 1.9001e-05 | 6.0032e-06 | 1.3755e-06 | -4.2707e-06 | -1.5281e-05 | -1.3755e-06 | 4.2709e-06 | 1.5281e-05 | -155.3558 | 47.0271 | -128.6092 | 24.6442 | -132.9729 | 51.3908 | 0.95 | 0.94819 | 0.9447 | 0.95 | 0.9482 | 0.94471 | 0.00066837 | -120.3052 | 119.9431 | 0.00077118 | -120.3048 | 119.9429
Line3_1_5 | 1.4991e-05 | 8.8796e-05 | 7.5145e-05 | 1.4991e-05 | 8.8796e-05 | 7.5145e-05 | 3.4619e-06 | 2.0506e-05 | 1.7354e-05 | 3.4619e-06 | 2.0506e-05 | 1.7354e-05 | -2.9864e-06 | -1.8975e-05 | -6.0073e-06 | 2.9864e-06 | 1.8976e-05 | 6.0074e-06 | 1.3776e-06 | -4.2424e-06 | -1.5254e-05 | -1.3776e-06 | 4.2426e-06 | 1.5254e-05 | -155.235 | 47.0922 | -128.5615 | 24.765 | -132.9078 | 51.4385 | 0.95 | 0.94819 | 0.9447 | 0.95 | 0.9482 | 0.94471 | 0.00066837 | -120.3052 | 119.9431 | 0.00077095 | -120.3048 | 119.9429
Line4_2_6 | 6.4749e-05 | 0.051518 | 0.051559 | 6.4749e-05 | 0.051518 | 0.051559 | 1.4953e-05 | 0.011898 | 0.011907 | 1.4953e-05 | 0.011898 | 0.011907 | -1.4127e-05 | 0.010857 | 0.0028452 | 1.4127e-05 | -0.010806 | -0.0027942 | -1.4975e-06 | 0.0028239 | 0.010816 | 1.4976e-06 | -0.0027709 | -0.010763 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.95001 | 0.94291 | 0.93929 | 0.95001 | 0.93765 | 0.93389 | 0.00097045 | -120.501 | 120.1256 | 0.0012725 | -120.6989 | 120.3103
Line5_6_7 | 6.4749e-05 | 0.051518 | 0.051559 | 6.4749e-05 | 0.051518 | 0.051559 | 1.4953e-05 | 0.011898 | 0.011907 | 1.4953e-05 | 0.011898 | 0.011907 | -1.4127e-05 | 0.010806 | 0.0027942 | 1.4127e-05 | -0.010755 | -0.0027432 | -1.4976e-06 | 0.0027709 | 0.010763 | 1.4976e-06 | -0.0027178 | -0.01071 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.95001 | 0.93765 | 0.93389 | 0.95002 | 0.9324 | 0.92849 | 0.0012725 | -120.6989 | 120.3103 | 0.0015746 | -120.8991 | 120.497
Line6_7_8 | 0 | 0.051853 | 0.051853 | 0 | 0.051853 | 0.051853 | 0 | 0.011975 | 0.011975 | 0 | 0.011975 | 0.011975 | 1.8284e-13 | 0.010816 | 0.0027315 | -1.8285e-13 | -0.010764 | -0.0026799 | -2.7283e-13 | 0.0027734 | 0.010778 | 2.7283e-13 | -0.0027197 | -0.010724 | 0 | -135.2816 | 44.7184 | 0 | 44.7184 | -135.2816 | 0.95002 | 0.9324 | 0.92849 | 0.95002 | 0.92711 | 0.92309 | 0.0015746 | -120.8991 | 120.497 | 0.0015746 | -121.1018 | 120.688
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0948e-14 | -7.7203e-11 | -9.0865e-11 | -6.0946e-14 | 7.7203e-11 | 9.0865e-11 | -9.0943e-14 | 6.2097e-11 | -3.8607e-11 | 9.094e-14 | -6.2097e-11 | 3.8607e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95002 | 0.92711 | 0.92309 | 0.95002 | 0.92711 | 0.92309 | 0.0015746 | -121.1018 | 120.688 | 0.0015746 | -121.1018 | 120.688
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0948e-14 | -7.7203e-11 | -9.0865e-11 | -6.0948e-14 | 7.7203e-11 | 9.0865e-11 | -9.0947e-14 | 6.2097e-11 | -3.8607e-11 | 9.0945e-14 | -6.2097e-11 | 3.8607e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95002 | 0.92711 | 0.92309 | 0.95002 | 0.92711 | 0.92309 | 0.0015746 | -121.1018 | 120.688 | 0.0015746 | -121.1018 | 120.688
Line9_3_11 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 1.4856e-05 | 8.8376e-05 | 7.4828e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | 3.4308e-06 | 2.041e-05 | 1.7281e-05 | -2.9509e-06 | -1.89e-05 | -6.0199e-06 | 2.9509e-06 | 1.89e-05 | 6.02e-06 | 1.3838e-06 | -4.1585e-06 | -1.5175e-05 | -1.3838e-06 | 4.1587e-06 | 1.5175e-05 | -154.8748 | 47.2864 | -128.4188 | 25.1252 | -132.7136 | 51.5812 | 0.95 | 0.9482 | 0.94471 | 0.95 | 0.9482 | 0.94472 | 0.00077024 | -120.3048 | 119.9429 | 0.00087212 | -120.3045 | 119.9427

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 6.1342e-05 | 0.048807 | 0.048845 | 6.1342e-05 | 0.048807 | 0.048845 | 1.4166e-05 | 0.011271 | 0.01128 | 1.4166e-05 | 0.011271 | 0.01128 | -1.2679e-05 | 0.0097901 | 0.0025994 | 1.2679e-05 | -0.0097444 | -0.0025536 | -1.3439e-06 | 0.0025822 | 0.0097553 | 1.344e-06 | -0.0025345 | -0.0097076 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.9 | 0.89828 | 0.89498 | 0.90001 | 0.89329 | 0.88985 | 0.00066837 | -120.3052 | 119.9431 | 0.00097045 | -120.501 | 120.1256
Line10_11_12 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.403e-06 | 2.6484e-06 | 1.6963e-05 | 5.4031e-06 | 1.242e-06 | -3.7325e-06 | -1.362e-05 | -1.242e-06 | 3.7326e-06 | 1.362e-05 | -154.8748 | 47.2863 | -128.4189 | 25.1252 | -132.7137 | 51.5811 | 0.9 | 0.8983 | 0.895 | 0.9 | 0.89831 | 0.89501 | 0.00087212 | -120.3045 | 119.9427 | 0.000974 | -120.3041 | 119.9425
Line11_12_13 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.4031e-06 | 2.6484e-06 | 1.6963e-05 | 5.4032e-06 | 1.242e-06 | -3.7326e-06 | -1.362e-05 | -1.242e-06 | 3.7328e-06 | 1.362e-05 | -154.8748 | 47.2863 | -128.4189 | 25.1252 | -132.7137 | 51.5811 | 0.9 | 0.89831 | 0.89501 | 0.9 | 0.89832 | 0.89501 | 0.000974 | -120.3041 | 119.9425 | 0.0010759 | -120.3038 | 119.9423
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8299e-14 | -1.6515e-11 | -4.9085e-11 | -1.8299e-14 | 1.6515e-11 | 4.9085e-11 | -1.6731e-13 | 4.715e-11 | 8.9292e-12 | 1.6731e-13 | -4.715e-11 | -8.9292e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89832 | 0.89501 | 0.9 | 0.89832 | 0.89501 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line13_13_14 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.4031e-06 | 2.6484e-06 | 1.6964e-05 | 5.4032e-06 | 1.242e-06 | -3.7328e-06 | -1.362e-05 | -1.242e-06 | 3.733e-06 | 1.362e-05 | -154.8748 | 47.2861 | -128.4192 | 25.1252 | -132.7139 | 51.5808 | 0.9 | 0.89832 | 0.89501 | 0.9 | 0.89832 | 0.89502 | 0.0010759 | -120.3038 | 119.9423 | 0.0011778 | -120.3034 | 119.9421
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2199e-14 | -1.101e-11 | -3.2723e-11 | -1.2199e-14 | 1.101e-11 | 3.2723e-11 | -1.1154e-13 | 3.1433e-11 | 5.9528e-12 | 1.1154e-13 | -3.1433e-11 | -5.9528e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89832 | 0.89501 | 0.9 | 0.89832 | 0.89501 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1001e-15 | -5.5052e-12 | -1.6362e-11 | -6.0998e-15 | 5.5052e-12 | 1.6362e-11 | -5.5769e-14 | 1.5717e-11 | 2.9764e-12 | 5.577e-14 | -1.5717e-11 | -2.9764e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89832 | 0.89501 | 0.9 | 0.89832 | 0.89501 | 0.0010759 | -120.3038 | 119.9423 | 0.0010759 | -120.3038 | 119.9423
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0126e-16 | -5.587e-12 | -1.6439e-11 | -8.014e-16 | 5.587e-12 | 1.6439e-11 | -3.9976e-14 | 1.5772e-11 | 2.9446e-12 | 3.9976e-14 | -1.5772e-11 | -2.9446e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89829 | 0.89499 | 0.9 | 0.89829 | 0.89499 | 0.00077118 | -120.3048 | 119.9429 | 0.00077118 | -120.3048 | 119.9429
Line17_5_19 | 1.4202e-05 | 8.4122e-05 | 7.119e-05 | 1.4202e-05 | 8.4122e-05 | 7.119e-05 | 3.2797e-06 | 1.9427e-05 | 1.6441e-05 | 3.2797e-06 | 1.9427e-05 | 1.6441e-05 | -2.6803e-06 | -1.7031e-05 | -5.3917e-06 | 2.6803e-06 | 1.7031e-05 | 5.3918e-06 | 1.2364e-06 | -3.8078e-06 | -1.3691e-05 | -1.2364e-06 | 3.8079e-06 | 1.3691e-05 | -155.235 | 47.0921 | -128.5615 | 24.765 | -132.9079 | 51.4385 | 0.9 | 0.89829 | 0.89499 | 0.9 | 0.8983 | 0.895 | 0.00077095 | -120.3048 | 119.9429 | 0.00087353 | -120.3045 | 119.9427
Line1_1_3 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.4028e-06 | 2.6484e-06 | 1.6963e-05 | 5.4029e-06 | 1.242e-06 | -3.7321e-06 | -1.362e-05 | -1.242e-06 | 3.7323e-06 | 1.362e-05 | -154.8748 | 47.2864 | -128.4187 | 25.1252 | -132.7136 | 51.5813 | 0.9 | 0.89828 | 0.89498 | 0.9 | 0.89829 | 0.89499 | 0.00066837 | -120.3052 | 119.9431 | 0.00077024 | -120.3048 | 119.9429
Line2_1_4 | 1.4245e-05 | 8.4255e-05 | 7.129e-05 | 1.4245e-05 | 8.4255e-05 | 7.129e-05 | 3.2896e-06 | 1.9458e-05 | 1.6464e-05 | 3.2896e-06 | 1.9458e-05 | 1.6464e-05 | -2.691e-06 | -1.7053e-05 | -5.3878e-06 | 2.691e-06 | 1.7053e-05 | 5.3879e-06 | 1.2345e-06 | -3.833e-06 | -1.3714e-05 | -1.2345e-06 | 3.8331e-06 | 1.3715e-05 | -155.3558 | 47.0271 | -128.6092 | 24.6442 | -132.9729 | 51.3908 | 0.9 | 0.89828 | 0.89498 | 0.9 | 0.89829 | 0.89499 | 0.00066837 | -120.3052 | 119.9431 | 0.00077118 | -120.3048 | 119.9429
Line3_1_5 | 1.4202e-05 | 8.4122e-05 | 7.119e-05 | 1.4202e-05 | 8.4122e-05 | 7.119e-05 | 3.2797e-06 | 1.9427e-05 | 1.6441e-05 | 3.2797e-06 | 1.9427e-05 | 1.6441e-05 | -2.6803e-06 | -1.7031e-05 | -5.3916e-06 | 2.6803e-06 | 1.7031e-05 | 5.3917e-06 | 1.2364e-06 | -3.8076e-06 | -1.3691e-05 | -1.2364e-06 | 3.8078e-06 | 1.3691e-05 | -155.235 | 47.0922 | -128.5615 | 24.765 | -132.9078 | 51.4385 | 0.9 | 0.89828 | 0.89498 | 0.9 | 0.89829 | 0.89499 | 0.00066837 | -120.3052 | 119.9431 | 0.00077095 | -120.3048 | 119.9429
Line4_2_6 | 6.1342e-05 | 0.048807 | 0.048845 | 6.1342e-05 | 0.048807 | 0.048845 | 1.4166e-05 | 0.011271 | 0.01128 | 1.4166e-05 | 0.011271 | 0.01128 | -1.2679e-05 | 0.0097444 | 0.0025536 | 1.2679e-05 | -0.0096987 | -0.0025078 | -1.344e-06 | 0.0025345 | 0.0097076 | 1.3441e-06 | -0.0024869 | -0.0096599 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.90001 | 0.89329 | 0.88985 | 0.90001 | 0.8883 | 0.88473 | 0.00097045 | -120.501 | 120.1256 | 0.0012725 | -120.6989 | 120.3103
Line5_6_7 | 6.1342e-05 | 0.048807 | 0.048845 | 6.1342e-05 | 0.048807 | 0.048845 | 1.4166e-05 | 0.011271 | 0.01128 | 1.4166e-05 | 0.011271 | 0.01128 | -1.2679e-05 | 0.0096987 | 0.0025078 | 1.2679e-05 | -0.0096529 | -0.002462 | -1.3441e-06 | 0.0024869 | 0.0096599 | 1.3441e-06 | -0.0024392 | -0.0096122 | 173.9499 | -135.0805 | 44.8636 | -6.0501 | 44.9195 | -135.1364 | 0.90001 | 0.8883 | 0.88473 | 0.90002 | 0.88333 | 0.87962 | 0.0012725 | -120.6989 | 120.3103 | 0.0015746 | -120.8991 | 120.497
Line6_7_8 | 0 | 0.049124 | 0.049124 | 0 | 0.049124 | 0.049124 | 0 | 0.011345 | 0.011345 | 0 | 0.011345 | 0.011345 | 1.641e-13 | 0.009707 | 0.0024516 | -1.641e-13 | -0.0096607 | -0.0024052 | -2.4486e-13 | 0.0024892 | 0.0096733 | 2.4486e-13 | -0.0024409 | -0.009625 | 0 | -135.2816 | 44.7184 | 0 | 44.7184 | -135.2816 | 0.90002 | 0.88333 | 0.87962 | 0.90002 | 0.87832 | 0.8745 | 0.0015746 | -120.8991 | 120.497 | 0.0015746 | -121.1018 | 120.688
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4699e-14 | -6.929e-11 | -8.1552e-11 | -5.4697e-14 | 6.929e-11 | 8.1552e-11 | -8.162e-14 | 5.5733e-11 | -3.465e-11 | 8.162e-14 | -5.5733e-11 | 3.465e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90002 | 0.87832 | 0.8745 | 0.90002 | 0.87832 | 0.8745 | 0.0015746 | -121.1018 | 120.688 | 0.0015746 | -121.1018 | 120.688
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4705e-14 | -6.929e-11 | -8.1552e-11 | -5.4701e-14 | 6.929e-11 | 8.1552e-11 | -8.1622e-14 | 5.5733e-11 | -3.465e-11 | 8.162e-14 | -5.5733e-11 | 3.465e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90002 | 0.87832 | 0.8745 | 0.90002 | 0.87832 | 0.8745 | 0.0015746 | -121.1018 | 120.688 | 0.0015746 | -121.1018 | 120.688
Line9_3_11 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 1.4074e-05 | 8.3725e-05 | 7.089e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | 3.2502e-06 | 1.9335e-05 | 1.6371e-05 | -2.6484e-06 | -1.6963e-05 | -5.4029e-06 | 2.6484e-06 | 1.6963e-05 | 5.403e-06 | 1.242e-06 | -3.7323e-06 | -1.362e-05 | -1.242e-06 | 3.7324e-06 | 1.362e-05 | -154.8748 | 47.2864 | -128.4188 | 25.1252 | -132.7136 | 51.5812 | 0.9 | 0.89829 | 0.89499 | 0.9 | 0.8983 | 0.895 | 0.00077024 | -120.3048 | 119.9429 | 0.00087212 | -120.3045 | 119.9427

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.1904 | 0.2035 | 0.12133 | 2.1904 | 0.2035 | 0.12133 | 0.50585 | 0.046997 | 0.02802 | 0.50585 | 0.046997 | 0.02802 | 0.1859 | -0.054967 | 0.022161 | -0.1449 | 0.054879 | -0.021118 | 0.35433 | 0.00898 | -0.022477 | -0.27301 | -0.0067306 | 0.022834 | -69.0079 | 66.0916 | 171.5652 | 110.9921 | -113.9084 | -8.4348 |  | 0.791 | 1.1851 | 1.1265 | 0.61101 | 1.1765 | 1.11 | -6.692 | -123.187 | 126.1595 | -6.9643 | -120.9004 | 124.3293
Line10_11_12 | 0.36559 | 0.10238 | 0.17198 | 0.36559 | 0.10238 | 0.17198 | 0.084429 | 0.023643 | 0.039716 | 0.084429 | 0.023643 | 0.039717 | -0.031305 | -0.026657 | 0.041011 | 0.032356 | 0.026806 | -0.041045 | -0.063918 | 0.0095223 | -0.018871 | 0.065847 | -0.0095313 | 0.019284 | 109.2375 | 76.6422 | 149.9425 | -70.7625 | -103.3578 | -30.0575 |  | 0.84299 | 1.1973 | 1.1367 | 0.86898 | 1.2034 | 1.1418 | -6.8563 | -123.0156 | 125.2338 | -6.931 | -122.9312 | 124.7771
Line11_12_13 | 0.36559 | 0.10238 | 0.17198 | 0.36559 | 0.10238 | 0.17198 | 0.084429 | 0.023643 | 0.039717 | 0.084429 | 0.023643 | 0.039717 | -0.032356 | -0.026806 | 0.041045 | 0.033407 | 0.026956 | -0.04108 | -0.065847 | 0.0095313 | -0.019284 | 0.067776 | -0.0095403 | 0.019698 | 109.2375 | 76.6422 | 149.9425 | -70.7625 | -103.3578 | -30.0575 |  | 0.86898 | 1.2034 | 1.1418 | 0.89498 | 1.2095 | 1.1471 | -6.931 | -122.9312 | 124.7771 | -7.0014 | -122.8476 | 124.3246
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5575e-08 | 2.7651e-08 | -4.1273e-08 | -9.9e-09 | -1.9147e-08 | 2.7094e-08 | 3.0483e-08 | -3.7227e-08 | -9.3471e-09 | -2.0742e-08 | 2.4587e-08 | 6.5644e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89498 | 1.2095 | 1.1471 | 0.89498 | 1.2095 | 1.1471 | -7.0014 | -122.8476 | 124.3246 | -7.0014 | -122.8477 | 124.3246
Line13_13_14 | 0.36559 | 0.10238 | 0.17198 | 0.36559 | 0.10238 | 0.17198 | 0.084429 | 0.023643 | 0.039717 | 0.084429 | 0.023643 | 0.039717 | -0.033407 | -0.026956 | 0.04108 | 0.034459 | 0.027106 | -0.041114 | -0.067776 | 0.0095404 | -0.019698 | 0.069705 | -0.0095494 | 0.020112 | 109.2375 | 76.6423 | 149.9424 | -70.7625 | -103.3577 | -30.0576 |  | 0.89498 | 1.2095 | 1.1471 | 0.92098 | 1.2156 | 1.1524 | -7.0014 | -122.8476 | 124.3246 | -7.0679 | -122.7649 | 123.8763
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0383e-08 | 1.8434e-08 | -2.7515e-08 | -4.7085e-09 | -9.9297e-09 | 1.3337e-08 | 2.0322e-08 | -2.4818e-08 | -6.2314e-09 | -1.0581e-08 | 1.2178e-08 | 3.4487e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89498 | 1.2095 | 1.1471 | 0.89498 | 1.2095 | 1.1471 | -7.0014 | -122.8477 | 124.3246 | -7.0014 | -122.8477 | 124.3246
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1915e-09 | 9.2169e-09 | -1.3758e-08 | 4.8302e-10 | -7.1288e-10 | -4.2092e-10 | 1.0161e-08 | -1.2409e-08 | -3.1157e-09 | -4.2001e-10 | -2.3133e-10 | 3.3302e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.89498 | 1.2095 | 1.1471 | 0.89498 | 1.2095 | 1.1471 | -7.0014 | -122.8477 | 124.3246 | -7.0014 | -122.8477 | 124.3246
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7785e-09 | 1.1168e-08 | -1.5605e-08 | 6.6041e-10 | -6.3582e-10 | -3.6541e-10 | 1.1148e-08 | -1.3708e-08 | -4.92e-09 | -3.8117e-10 | -2.4515e-10 | 4.2649e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82374 | 1.1938 | 1.1329 | 0.82374 | 1.1938 | 1.1329 | -6.9031 | -123.0576 | 125.6113 | -6.9031 | -123.0576 | 125.6113
Line17_5_19 | 0.43185 | 0.12849 | 0.19296 | 0.43185 | 0.12849 | 0.19296 | 0.099731 | 0.029675 | 0.044563 | 0.099731 | 0.029675 | 0.044563 | -0.033037 | -0.034367 | 0.046474 | 0.034488 | 0.034611 | -0.046542 | -0.075002 | 0.0084887 | -0.019677 | 0.077715 | -0.0084754 | 0.020205 | 106.9104 | 70.8038 | 148.5818 | -73.0896 | -109.1962 | -31.4182 |  | 0.82177 | 1.1929 | 1.1325 | 0.85253 | 1.2008 | 1.1386 | -6.8622 | -123.0706 | 125.6344 | -7.0202 | -122.9557 | 125.1147
Line1_1_3 | 0.36559 | 0.10238 | 0.17198 | 0.36559 | 0.10238 | 0.17198 | 0.084429 | 0.023643 | 0.039716 | 0.084429 | 0.023643 | 0.039716 | -0.029202 | -0.026357 | 0.040943 | 0.030253 | 0.026507 | -0.040977 | -0.060061 | 0.0095043 | -0.018043 | 0.061989 | -0.0095133 | 0.018457 | 109.2375 | 76.6421 | 149.9425 | -70.7625 | -103.3578 | -30.0575 |  | 0.791 | 1.1851 | 1.1265 | 0.817 | 1.1912 | 1.1316 | -6.692 | -123.187 | 126.1595 | -6.7767 | -123.1008 | 125.6946
Line2_1_4 | 0.4592 | 0.14005 | 0.20072 | 0.4592 | 0.14005 | 0.20072 | 0.10605 | 0.032344 | 0.046355 | 0.10605 | 0.032344 | 0.046355 | -0.032313 | -0.037539 | 0.048437 | 0.033947 | 0.037831 | -0.048522 | -0.077411 | 0.0077486 | -0.019515 | 0.08049 | -0.00772 | 0.02009 | 105.9649 | 68.4761 | 148.1033 | -74.0351 | -111.5239 | -31.8967 |  | 0.791 | 1.1851 | 1.1265 | 0.82374 | 1.1938 | 1.1329 | -6.692 | -123.187 | 126.1595 | -6.9031 | -123.0576 | 125.6113
Line3_1_5 | 0.43185 | 0.12849 | 0.19296 | 0.43185 | 0.12849 | 0.19296 | 0.099731 | 0.029675 | 0.044563 | 0.099731 | 0.029675 | 0.044563 | -0.031586 | -0.034124 | 0.046407 | 0.033037 | 0.034367 | -0.046474 | -0.072288 | 0.0085021 | -0.019148 | 0.075002 | -0.0084887 | 0.019677 | 106.9104 | 70.8037 | 148.5818 | -73.0896 | -109.1962 | -31.4182 |  | 0.791 | 1.1851 | 1.1265 | 0.82177 | 1.1929 | 1.1325 | -6.692 | -123.187 | 126.1595 | -6.8622 | -123.0706 | 125.6344
Line4_2_6 | 2.1904 | 0.2035 | 0.12133 | 2.1904 | 0.2035 | 0.12133 | 0.50585 | 0.046997 | 0.02802 | 0.50585 | 0.046997 | 0.02802 | 0.1449 | -0.054879 | 0.021118 | -0.10389 | 0.054792 | -0.020074 | 0.27301 | 0.0067306 | -0.022834 | -0.1917 | -0.0044812 | 0.02319 | -69.0079 | 66.0916 | 171.5652 | 110.9921 | -113.9084 | -8.4349 |  | 0.61101 | 1.1765 | 1.11 | 0.43104 | 1.1698 | 1.0947 | -6.9643 | -120.9004 | 124.3293 | -7.4638 | -118.5839 | 122.4459
Line5_6_7 | 2.1904 | 0.2035 | 0.12133 | 2.1904 | 0.2035 | 0.12133 | 0.50585 | 0.046997 | 0.02802 | 0.50585 | 0.046997 | 0.02802 | 0.10389 | -0.054792 | 0.020074 | -0.062889 | 0.054705 | -0.019031 | 0.1917 | 0.0044812 | -0.02319 | -0.11038 | -0.0022318 | 0.023547 | -69.0079 | 66.0916 | 171.5651 | 110.9921 | -113.9084 | -8.4349 |  | 0.43104 | 1.1698 | 1.0947 | 0.25115 | 1.165 | 1.0805 | -7.4638 | -118.5839 | 122.4459 | -8.6794 | -116.2446 | 120.5109
Line6_7_8 | 3.1126 | 0 | 0 | 3.1126 | 0 | 0 | 0.71882 | 0 | 0 | 0.71882 | 0 | 0 | 0.080735 | 7.782e-08 | -7.94e-08 | -4.6335e-15 | -5.4685e-08 | 5.3333e-08 | 0.16147 | -5.3683e-08 | -3.2463e-08 | 6.9253e-14 | 3.4087e-08 | 1.9873e-08 | -72.1143 | 0 | 0 | 107.8857 | 0 | 0 |  | 0.25115 | 1.165 | 1.0805 | 0 | 1.1508 | 1.0495 | -8.6794 | -116.2446 | 120.5109 | 0 | -113.8597 | 118.3851
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8393e-22 | 2.7117e-08 | -2.6666e-08 | -7.9042e-18 | -4.5083e-10 | 3.2438e-13 | -2.4073e-21 | -1.6806e-08 | -9.9933e-09 | 8.2091e-18 | 4.7391e-10 | -1.1387e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.1508 | 1.0495 | 0 | 1.1508 | 1.0495 | 0 | -113.8597 | 118.3851 | 0 | -113.8597 | 118.3851
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8393e-22 | 2.7117e-08 | -2.6666e-08 | -7.9042e-18 | -4.5083e-10 | 3.2452e-13 | -2.4073e-21 | -1.6806e-08 | -9.9933e-09 | 8.2091e-18 | 4.7392e-10 | -1.1387e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.1508 | 1.0495 | 0 | 1.1508 | 1.0495 | 0 | -113.8597 | 118.3851 | 0 | -113.8597 | 118.3851
Line9_3_11 | 0.36559 | 0.10238 | 0.17198 | 0.36559 | 0.10238 | 0.17198 | 0.084429 | 0.023643 | 0.039716 | 0.084429 | 0.023643 | 0.039716 | -0.030253 | -0.026507 | 0.040977 | 0.031305 | 0.026657 | -0.041011 | -0.061989 | 0.0095133 | -0.018457 | 0.063918 | -0.0095223 | 0.018871 | 109.2375 | 76.6422 | 149.9425 | -70.7625 | -103.3578 | -30.0575 |  | 0.817 | 1.1912 | 1.1316 | 0.84299 | 1.1973 | 1.1367 | -6.7767 | -123.1008 | 125.6946 | -6.8563 | -123.0156 | 125.2338

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 2.2724 | 0.20856 | 0.12455 | 2.2724 | 0.20856 | 0.12455 | 0.52479 | 0.048165 | 0.028763 | 0.52479 | 0.048165 | 0.028763 | 0.19925 | -0.058996 | 0.024867 | -0.15511 | 0.058926 | -0.023762 | 0.38057 | 0.010511 | -0.023171 | -0.29302 | -0.0081239 | 0.02358 | -69.2729 | 66.8271 | 169.2869 | 110.7271 | -113.1729 | -10.7131 |  | 0.81857 | 1.2442 | 1.1817 | 0.63177 | 1.235 | 1.1638 | -6.9072 | -123.2752 | 126.3087 | -7.1672 | -121.0225 | 124.5068
Line10_11_12 | 0.37833 | 0.10818 | 0.17653 | 0.37833 | 0.10818 | 0.17653 | 0.087371 | 0.024983 | 0.040768 | 0.087372 | 0.024983 | 0.040768 | -0.033609 | -0.029366 | 0.044555 | 0.03473 | 0.029527 | -0.044594 | -0.068398 | 0.011086 | -0.019367 | 0.070461 | -0.011094 | 0.019796 | 109.1077 | 77.5913 | 148.9025 | -70.8923 | -102.4087 | -31.0975 |  | 0.87225 | 1.2564 | 1.1917 | 0.89909 | 1.2625 | 1.1968 | -7.0607 | -123.0916 | 125.4089 | -7.1305 | -123.0011 | 124.9647
Line11_12_13 | 0.37833 | 0.10818 | 0.17653 | 0.37833 | 0.10818 | 0.17653 | 0.087372 | 0.024983 | 0.040768 | 0.087372 | 0.024983 | 0.040768 | -0.03473 | -0.029527 | 0.044594 | 0.03585 | 0.029688 | -0.044633 | -0.070461 | 0.011094 | -0.019796 | 0.072524 | -0.011101 | 0.020226 | 109.1077 | 77.5913 | 148.9025 | -70.8923 | -102.4087 | -31.0975 |  | 0.89909 | 1.2625 | 1.1968 | 0.92594 | 1.2687 | 1.202 | -7.1305 | -123.0011 | 124.9647 | -7.1964 | -122.9115 | 124.5243
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7388e-08 | 3.1678e-08 | -4.6984e-08 | -1.103e-08 | -2.191e-08 | 3.0858e-08 | 3.4328e-08 | -4.2338e-08 | -1.1111e-08 | -2.3353e-08 | 2.7965e-08 | 7.7896e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.92594 | 1.2687 | 1.202 | 0.92594 | 1.2687 | 1.202 | -7.1964 | -122.9115 | 124.5243 | -7.1964 | -122.9115 | 124.5243
Line13_13_14 | 0.37833 | 0.10818 | 0.17653 | 0.37833 | 0.10818 | 0.17653 | 0.087372 | 0.024983 | 0.040768 | 0.087372 | 0.024983 | 0.040768 | -0.03585 | -0.029688 | 0.044633 | 0.03697 | 0.029848 | -0.044672 | -0.072524 | 0.011101 | -0.020226 | 0.074586 | -0.011109 | 0.020655 | 109.1077 | 77.5914 | 148.9025 | -70.8923 | -102.4086 | -31.0976 |  | 0.92594 | 1.2687 | 1.202 | 0.95278 | 1.2748 | 1.2072 | -7.1964 | -122.9115 | 124.5243 | -7.2585 | -122.8227 | 124.0877
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1592e-08 | 2.1119e-08 | -3.1323e-08 | -5.2345e-09 | -1.1351e-08 | 1.5197e-08 | 2.2885e-08 | -2.8225e-08 | -7.4072e-09 | -1.191e-08 | 1.3853e-08 | 4.086e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.92594 | 1.2687 | 1.202 | 0.92594 | 1.2687 | 1.202 | -7.1964 | -122.9115 | 124.5243 | -7.1964 | -122.9115 | 124.5243
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.796e-09 | 1.0559e-08 | -1.5661e-08 | 5.6155e-10 | -7.9119e-10 | -4.645e-10 | 1.1443e-08 | -1.4113e-08 | -3.7036e-09 | -4.6784e-10 | -2.599e-10 | 3.8242e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.92594 | 1.2687 | 1.202 | 0.92594 | 1.2687 | 1.202 | -7.1964 | -122.9115 | 124.5243 | -7.1964 | -122.9115 | 124.5243
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3263e-09 | 1.2704e-08 | -1.7662e-08 | 7.4822e-10 | -7.0955e-10 | -4.0744e-10 | 1.2471e-08 | -1.5522e-08 | -5.7069e-09 | -4.2519e-10 | -2.7681e-10 | 4.8256e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.85206 | 1.2528 | 1.1879 | 0.85206 | 1.2528 | 1.1879 | -7.107 | -123.1403 | 125.7803 | -7.107 | -123.1403 | 125.7803
Line17_5_19 | 0.44397 | 0.13426 | 0.19705 | 0.44397 | 0.13426 | 0.19705 | 0.10253 | 0.031005 | 0.045506 | 0.10253 | 0.031006 | 0.045506 | -0.035319 | -0.037483 | 0.0502 | 0.036846 | 0.03774 | -0.050274 | -0.079688 | 0.010099 | -0.020009 | 0.082551 | -0.010083 | 0.020551 | 106.8352 | 71.9261 | 147.5326 | -73.1648 | -108.0739 | -32.4674 |  | 0.85013 | 1.252 | 1.1875 | 0.88169 | 1.2599 | 1.1935 | -7.0683 | -123.153 | 125.8014 | -7.2178 | -123.0323 | 125.299
Line1_1_3 | 0.37833 | 0.10818 | 0.17653 | 0.37833 | 0.10818 | 0.17653 | 0.087371 | 0.024983 | 0.040768 | 0.087371 | 0.024983 | 0.040768 | -0.031369 | -0.029044 | 0.044477 | 0.032489 | 0.029205 | -0.044516 | -0.064273 | 0.011071 | -0.018508 | 0.066336 | -0.011079 | 0.018938 | 109.1077 | 77.5912 | 148.9025 | -70.8923 | -102.4087 | -31.0975 |  | 0.81857 | 1.2442 | 1.1817 | 0.84541 | 1.2503 | 1.1866 | -6.9072 | -123.2752 | 126.3087 | -6.9863 | -123.1829 | 125.8569
Line2_1_4 | 0.47083 | 0.14565 | 0.20458 | 0.47083 | 0.14565 | 0.20458 | 0.10873 | 0.033636 | 0.047246 | 0.10873 | 0.033636 | 0.047246 | -0.034529 | -0.040783 | 0.052212 | 0.036239 | 0.041089 | -0.052303 | -0.082035 | 0.0093817 | -0.01977 | 0.085266 | -0.0093503 | 0.020358 | 105.9191 | 69.6796 | 147.0483 | -74.0809 | -110.3204 | -32.9517 |  | 0.81857 | 1.2442 | 1.1817 | 0.85206 | 1.2528 | 1.1879 | -6.9072 | -123.2752 | 126.3087 | -7.107 | -123.1403 | 125.7803
Line3_1_5 | 0.44397 | 0.13426 | 0.19705 | 0.44397 | 0.13426 | 0.19705 | 0.10253 | 0.031005 | 0.045506 | 0.10253 | 0.031005 | 0.045506 | -0.033792 | -0.037226 | 0.050127 | 0.035319 | 0.037483 | -0.0502 | -0.076825 | 0.010115 | -0.019467 | 0.079688 | -0.010099 | 0.020009 | 106.8352 | 71.9261 | 147.5326 | -73.1648 | -108.0739 | -32.4674 |  | 0.81857 | 1.2442 | 1.1817 | 0.85013 | 1.252 | 1.1875 | -6.9072 | -123.2752 | 126.3087 | -7.0683 | -123.153 | 125.8014
Line4_2_6 | 2.2724 | 0.20856 | 0.12455 | 2.2724 | 0.20856 | 0.12455 | 0.52479 | 0.048165 | 0.028763 | 0.52479 | 0.048165 | 0.028763 | 0.15511 | -0.058926 | 0.023762 | -0.11097 | 0.058856 | -0.022657 | 0.29302 | 0.0081239 | -0.02358 | -0.20547 | -0.0057365 | 0.023989 | -69.2729 | 66.8271 | 169.2869 | 110.7271 | -113.1728 | -10.7131 |  | 0.63177 | 1.235 | 1.1638 | 0.44499 | 1.2278 | 1.1472 | -7.1672 | -121.0225 | 124.5068 | -7.6455 | -118.7396 | 122.6507
Line5_6_7 | 2.2724 | 0.20856 | 0.12455 | 2.2724 | 0.20856 | 0.12455 | 0.52479 | 0.048165 | 0.028763 | 0.52479 | 0.048165 | 0.028763 | 0.11097 | -0.058856 | 0.022657 | -0.066835 | 0.058787 | -0.021552 | 0.20547 | 0.0057365 | -0.023989 | -0.11793 | -0.0033491 | 0.024398 | -69.2729 | 66.8272 | 169.2869 | 110.7271 | -113.1728 | -10.7132 |  | 0.44499 | 1.2278 | 1.1472 | 0.25829 | 1.2225 | 1.1318 | -7.6455 | -118.7396 | 122.6507 | -8.8157 | -116.4335 | 120.742
Line6_7_8 | 3.2011 | 0 | 0 | 3.2011 | 0 | 0 | 0.73927 | 0 | 0 | 0.73927 | 0 | 0 | 0.085393 | 8.6265e-08 | -8.7977e-08 | 1.2604e-15 | -6.0569e-08 | 5.9059e-08 | 0.17079 | -5.9949e-08 | -3.6363e-08 | 2.9931e-14 | 3.8099e-08 | 2.2336e-08 | -72.2506 | 0 | 0 | 107.7494 | 0 | 0 |  | 0.25829 | 1.2225 | 1.1318 | 0 | 1.2079 | 1.0996 | -8.8157 | -116.4335 | 120.742 | 0 | -114.0973 | 118.6663
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1279e-22 | 3.0032e-08 | -2.9529e-08 | -8.799e-18 | -5.0353e-10 | 3.518e-13 | -1.1119e-21 | -1.8799e-08 | -1.1219e-08 | 9.0272e-18 | 5.01e-10 | -1.0323e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.2079 | 1.0996 | 0 | 1.2079 | 1.0996 | 0 | -114.0973 | 118.6663 | 0 | -114.0973 | 118.6663
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1279e-22 | 3.0032e-08 | -2.9529e-08 | -8.799e-18 | -5.0353e-10 | 3.517e-13 | -1.1119e-21 | -1.8799e-08 | -1.1219e-08 | 9.0272e-18 | 5.01e-10 | -1.0323e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.2079 | 1.0996 | 0 | 1.2079 | 1.0996 | 0 | -114.0973 | 118.6663 | 0 | -114.0973 | 118.6663
Line9_3_11 | 0.37833 | 0.10818 | 0.17653 | 0.37833 | 0.10818 | 0.17653 | 0.087371 | 0.024983 | 0.040768 | 0.087371 | 0.024983 | 0.040768 | -0.032489 | -0.029205 | 0.044516 | 0.033609 | 0.029366 | -0.044555 | -0.066336 | 0.011079 | -0.018938 | 0.068398 | -0.011086 | 0.019367 | 109.1077 | 77.5913 | 148.9025 | -70.8923 | -102.4087 | -31.0975 |  | 0.84541 | 1.2503 | 1.1866 | 0.87225 | 1.2564 | 1.1917 | -6.9863 | -123.1829 | 125.8569 | -7.0607 | -123.0916 | 125.4089

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.088169 | 0.11042 | 0.11198 | 0.088169 | 0.11042 | 0.11198 | 0.020362 | 0.0255 | 0.02586 | 0.020362 | 0.0255 | 0.02586 | -0.0061429 | -0.011438 | -0.010802 | 0.0062198 | 0.011552 | 0.010936 | -0.021396 | -0.025536 | -0.026193 | 0.021559 | 0.025775 | 0.026439 | 105.9788 | -5.7873 | -127.4194 | -74.0212 | 174.2127 | 52.5806 |  | 1.0932 | 1.0973 | 1.0956 | 1.102 | 1.1076 | 1.1064 | -0.040402 | -119.9162 | 120.1686 | -0.1142 | -119.9278 | 120.1087
Line10_11_12 | 0.10301 | 0.09912 | 0.10158 | 0.10301 | 0.09912 | 0.10158 | 0.023789 | 0.022891 | 0.02346 | 0.023789 | 0.022891 | 0.02346 | -0.0016134 | -0.00098803 | -0.0004497 | 0.0017205 | 0.0010878 | 0.00055031 | -0.026389 | -0.025502 | -0.026115 | 0.026599 | 0.0257 | 0.026322 | 93.0437 | -28.1172 | -149.2775 | -86.9563 | 151.8828 | 30.7225 |  | 1.1114 | 1.1149 | 1.1133 | 1.1204 | 1.1237 | 1.1222 | -0.455 | -120.3359 | 119.736 | -0.65727 | -120.5409 | 119.5248
Line11_12_13 | 0.10301 | 0.09912 | 0.10158 | 0.10301 | 0.09912 | 0.10158 | 0.023789 | 0.022891 | 0.02346 | 0.023789 | 0.022891 | 0.02346 | -0.0017205 | -0.0010878 | -0.00055031 | 0.0018276 | 0.0011876 | 0.00065092 | -0.026599 | -0.0257 | -0.026322 | 0.026809 | 0.025899 | 0.026529 | 93.0437 | -28.1172 | -149.2775 | -86.9563 | 151.8828 | 30.7225 |  | 1.1204 | 1.1237 | 1.1222 | 1.1295 | 1.1326 | 1.1311 | -0.65727 | -120.5409 | 119.5248 | -0.85628 | -120.7426 | 119.3169
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3779e-09 | 1.1106e-09 | 5.4203e-10 | -1.2485e-09 | -1.0838e-09 | -6.9819e-10 | 5.1049e-10 | -3.2546e-10 | 3.3288e-10 | -4.0532e-10 | 1.6046e-10 | -2.7384e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1295 | 1.1326 | 1.1311 | 1.1295 | 1.1326 | 1.1311 | -0.85628 | -120.7426 | 119.3169 | -0.85628 | -120.7426 | 119.3169
Line13_13_14 | 0.10301 | 0.09912 | 0.10158 | 0.10301 | 0.09912 | 0.10158 | 0.023789 | 0.022891 | 0.02346 | 0.023789 | 0.022891 | 0.02346 | -0.0018276 | -0.0011876 | -0.00065092 | 0.0019347 | 0.0012873 | 0.00075153 | -0.026809 | -0.025899 | -0.026529 | 0.027018 | 0.026097 | 0.026735 | 93.0437 | -28.1172 | -149.2775 | -86.9563 | 151.8828 | 30.7225 |  | 1.1295 | 1.1326 | 1.1311 | 1.1387 | 1.1415 | 1.1401 | -0.85628 | -120.7426 | 119.3169 | -1.0521 | -120.9412 | 119.1123
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1858e-10 | 7.4039e-10 | 3.6136e-10 | -7.8923e-10 | -7.1359e-10 | -5.1751e-10 | 3.4033e-10 | -2.1697e-10 | 2.2192e-10 | -2.3515e-10 | 5.1973e-11 | -1.6288e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1295 | 1.1326 | 1.1311 | 1.1295 | 1.1326 | 1.1311 | -0.85628 | -120.7426 | 119.3169 | -0.85628 | -120.7426 | 119.3169
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5929e-10 | 3.702e-10 | 1.8068e-10 | -3.2994e-10 | -3.4339e-10 | -3.3683e-10 | 1.7016e-10 | -1.0849e-10 | 1.1096e-10 | -6.4989e-11 | -5.6513e-11 | -5.1916e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1295 | 1.1326 | 1.1311 | 1.1295 | 1.1326 | 1.1311 | -0.85628 | -120.7426 | 119.3169 | -0.85628 | -120.7426 | 119.3169
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6089e-10 | 2.8121e-10 | 4.937e-11 | -2.2223e-10 | -2.3805e-10 | -2.3119e-10 | 1.5172e-10 | -1.7184e-10 | 6.2624e-11 | -2.2447e-11 | -1.3409e-11 | -7.6985e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1048 | 1.1086 | 1.107 | 1.1048 | 1.1086 | 1.107 | -0.30235 | -120.18 | 119.8965 | -0.30235 | -120.18 | 119.8965
Line17_5_19 | 0.12307 | 0.11839 | 0.1211 | 0.12307 | 0.11839 | 0.1211 | 0.028423 | 0.027341 | 0.027966 | 0.028423 | 0.027341 | 0.027966 | -0.0019588 | -0.0013055 | -0.00063131 | 0.0021114 | 0.001448 | 0.0007744 | -0.03132 | -0.030261 | -0.03093 | 0.031619 | 0.030544 | 0.031224 | 93.2918 | -27.6944 | -148.9184 | -86.7082 | 152.3056 | 31.0816 |  | 1.1041 | 1.1078 | 1.1062 | 1.1149 | 1.1184 | 1.1168 | -0.28681 | -120.1647 | 119.9123 | -0.52842 | -120.4085 | 119.6609
Line1_1_3 | 0.10301 | 0.09912 | 0.10158 | 0.10301 | 0.09912 | 0.10158 | 0.023789 | 0.022891 | 0.02346 | 0.023789 | 0.022891 | 0.02346 | -0.0013992 | -0.0007885 | -0.00024847 | 0.0015063 | 0.00088827 | 0.00034908 | -0.02597 | -0.025105 | -0.025702 | 0.026179 | 0.025303 | 0.025909 | 93.0437 | -28.1172 | -149.2775 | -86.9563 | 151.8828 | 30.7225 |  | 1.0932 | 1.0973 | 1.0956 | 1.1023 | 1.1061 | 1.1045 | -0.040402 | -119.9162 | 120.1686 | -0.24941 | -120.1277 | 119.9506
Line2_1_4 | 0.13159 | 0.12658 | 0.12937 | 0.13159 | 0.12658 | 0.12937 | 0.03039 | 0.029233 | 0.029876 | 0.03039 | 0.029233 | 0.029876 | -0.0019932 | -0.0013437 | -0.00061118 | 0.0021675 | 0.0015066 | 0.00077454 | -0.033164 | -0.032048 | -0.032727 | 0.033506 | 0.032372 | 0.033062 | 93.399 | -27.5153 | -148.7615 | -86.601 | 152.4847 | 31.2385 |  | 1.0932 | 1.0973 | 1.0956 | 1.1048 | 1.1086 | 1.107 | -0.040402 | -119.9162 | 120.1686 | -0.30235 | -120.18 | 119.8965
Line3_1_5 | 0.12307 | 0.11839 | 0.1211 | 0.12307 | 0.11839 | 0.1211 | 0.028423 | 0.027341 | 0.027966 | 0.028423 | 0.027341 | 0.027966 | -0.0018061 | -0.001163 | -0.00048822 | 0.0019588 | 0.0013055 | 0.00063131 | -0.03102 | -0.029978 | -0.030636 | 0.03132 | 0.030261 | 0.03093 | 93.2918 | -27.6944 | -148.9184 | -86.7082 | 152.3056 | 31.0816 |  | 1.0932 | 1.0973 | 1.0956 | 1.1041 | 1.1078 | 1.1062 | -0.040402 | -119.9162 | 120.1686 | -0.28681 | -120.1647 | 119.9123
Line4_2_6 | 0.088169 | 0.11042 | 0.11198 | 0.088169 | 0.11042 | 0.11198 | 0.020362 | 0.0255 | 0.02586 | 0.020362 | 0.0255 | 0.02586 | -0.0062198 | -0.011552 | -0.010936 | 0.0062967 | 0.011665 | 0.01107 | -0.021559 | -0.025775 | -0.026439 | 0.021722 | 0.026015 | 0.026685 | 105.9788 | -5.7873 | -127.4194 | -74.0212 | 174.2127 | 52.5806 |  | 1.102 | 1.1076 | 1.1064 | 1.1107 | 1.118 | 1.1171 | -0.1142 | -119.9278 | 120.1087 | -0.18684 | -119.9392 | 120.0499
Line5_6_7 | 0.088169 | 0.11042 | 0.11198 | 0.088169 | 0.11042 | 0.11198 | 0.020362 | 0.0255 | 0.02586 | 0.020362 | 0.0255 | 0.02586 | -0.0062967 | -0.011665 | -0.01107 | 0.0063736 | 0.011779 | 0.011204 | -0.021722 | -0.026015 | -0.026685 | 0.021885 | 0.026254 | 0.026931 | 105.9788 | -5.7873 | -127.4194 | -74.0212 | 174.2127 | 52.5806 |  | 1.1107 | 1.118 | 1.1171 | 1.1195 | 1.1284 | 1.1279 | -0.18684 | -119.9392 | 120.0499 | -0.25835 | -119.9504 | 119.9922
Line6_7_8 | 0.036471 | 0 | 0 | 0.036471 | 0 | 0 | 0.0084225 | 0 | 0 | 0.0084225 | 0 | 0 | 0.0066616 | 1.4153e-09 | -8.1744e-11 | -0.0066505 | -1.2783e-09 | -2.4908e-10 | 0.0066727 | -9.6735e-10 | 9.8087e-11 | -0.0066505 | 6.6339e-10 | -6.4417e-11 | -45.306 | 0 | 0 | 134.694 | 0 | 0 |  | 1.1195 | 1.1284 | 1.1279 | 1.1167 | 1.128 | 1.1278 | -0.25835 | -119.9504 | 119.9922 | -0.30598 | -119.9304 | 119.963
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7567e-10 | 4.7788e-10 | -3.6299e-11 | -2.7307e-10 | -3.2251e-10 | -3.2167e-10 | 3.1511e-10 | -3.2906e-10 | 3.0805e-11 | -2.2959e-11 | 5.2765e-12 | -2.8058e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1167 | 1.128 | 1.1278 | 1.1167 | 1.128 | 1.1278 | -0.30598 | -119.9304 | 119.963 | -0.30598 | -119.9304 | 119.963
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7568e-10 | 4.7788e-10 | -3.6299e-11 | -2.7307e-10 | -3.2251e-10 | -3.2167e-10 | 3.1511e-10 | -3.2906e-10 | 3.0806e-11 | -2.2959e-11 | 5.2765e-12 | -2.8059e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1167 | 1.128 | 1.1278 | 1.1167 | 1.128 | 1.1278 | -0.30598 | -119.9304 | 119.963 | -0.30598 | -119.9304 | 119.963
Line9_3_11 | 0.10301 | 0.09912 | 0.10158 | 0.10301 | 0.09912 | 0.10158 | 0.023789 | 0.022891 | 0.02346 | 0.023789 | 0.022891 | 0.02346 | -0.0015063 | -0.00088827 | -0.00034908 | 0.0016134 | 0.00098803 | 0.0004497 | -0.026179 | -0.025303 | -0.025909 | 0.026389 | 0.025502 | 0.026115 | 93.0437 | -28.1172 | -149.2775 | -86.9563 | 151.8828 | 30.7225 |  | 1.1023 | 1.1061 | 1.1045 | 1.1114 | 1.1149 | 1.1133 | -0.24941 | -120.1277 | 119.9506 | -0.455 | -120.3359 | 119.736

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.087712 | 0.11111 | 0.11275 | 0.087712 | 0.11111 | 0.11275 | 0.020256 | 0.025659 | 0.026038 | 0.020256 | 0.025659 | 0.026038 | -0.0061587 | -0.011992 | -0.011288 | 0.0062347 | 0.012107 | 0.011424 | -0.02237 | -0.026957 | -0.02768 | 0.022532 | 0.027199 | 0.027929 | 105.3474 | -5.933 | -127.6418 | -74.6526 | 174.067 | 52.3582 |  | 1.1454 | 1.1498 | 1.148 | 1.1541 | 1.1603 | 1.1589 | -0.045696 | -119.9154 | 120.1731 | -0.11996 | -119.9274 | 120.1125
Line10_11_12 | 0.10426 | 0.10012 | 0.10272 | 0.10426 | 0.10012 | 0.10272 | 0.024078 | 0.023122 | 0.023722 | 0.024078 | 0.023122 | 0.023722 | -0.0017717 | -0.0010826 | -0.00048273 | 0.0018814 | 0.0011845 | 0.00058547 | -0.027965 | -0.026978 | -0.027655 | 0.02818 | 0.027181 | 0.027866 | 93.1808 | -28.0212 | -149.2437 | -86.8192 | 151.9788 | 30.7563 |  | 1.1638 | 1.1677 | 1.166 | 1.173 | 1.1766 | 1.175 | -0.44433 | -120.3192 | 119.7563 | -0.63896 | -120.5165 | 119.5527
Line11_12_13 | 0.10426 | 0.10012 | 0.10272 | 0.10426 | 0.10012 | 0.10272 | 0.024078 | 0.023122 | 0.023722 | 0.024078 | 0.023122 | 0.023722 | -0.0018814 | -0.0011845 | -0.00058547 | 0.0019912 | 0.0012864 | 0.00068822 | -0.02818 | -0.027181 | -0.027866 | 0.028394 | 0.027383 | 0.028077 | 93.1808 | -28.0212 | -149.2437 | -86.8192 | 151.9788 | 30.7563 |  | 1.173 | 1.1766 | 1.175 | 1.1822 | 1.1856 | 1.184 | -0.63896 | -120.5165 | 119.5527 | -0.83057 | -120.7108 | 119.3522
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5182e-09 | 1.2126e-09 | 5.5105e-10 | -1.3688e-09 | -1.1808e-09 | -7.322e-10 | 5.7456e-10 | -3.9501e-10 | 3.6485e-10 | -4.5216e-10 | 2.0402e-10 | -2.9722e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1822 | 1.1856 | 1.184 | 1.1822 | 1.1856 | 1.184 | -0.83057 | -120.7108 | 119.3522 | -0.83057 | -120.7108 | 119.3522
Line13_13_14 | 0.10426 | 0.10012 | 0.10272 | 0.10426 | 0.10012 | 0.10272 | 0.024078 | 0.023122 | 0.023722 | 0.024078 | 0.023122 | 0.023722 | -0.0019912 | -0.0012864 | -0.00068822 | 0.0021009 | 0.0013882 | 0.00079097 | -0.028394 | -0.027383 | -0.028077 | 0.028609 | 0.027586 | 0.028289 | 93.1808 | -28.0212 | -149.2437 | -86.8192 | 151.9788 | 30.7563 |  | 1.1822 | 1.1856 | 1.184 | 1.1914 | 1.1945 | 1.193 | -0.83057 | -120.7108 | 119.3522 | -1.0192 | -120.9021 | 119.1547
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0121e-09 | 8.0843e-10 | 3.6737e-10 | -8.628e-10 | -7.7659e-10 | -5.4852e-10 | 3.8304e-10 | -2.6334e-10 | 2.4324e-10 | -2.6064e-10 | 7.2353e-11 | -1.7561e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1822 | 1.1856 | 1.184 | 1.1822 | 1.1856 | 1.184 | -0.83057 | -120.7108 | 119.3522 | -0.83057 | -120.7108 | 119.3522
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0605e-10 | 4.0422e-10 | 1.8368e-10 | -3.5674e-10 | -3.7238e-10 | -3.6483e-10 | 1.9152e-10 | -1.3167e-10 | 1.2162e-10 | -6.9117e-11 | -5.9317e-11 | -5.3989e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1822 | 1.1856 | 1.184 | 1.1822 | 1.1856 | 1.184 | -0.83057 | -120.7108 | 119.3522 | -0.83057 | -120.7108 | 119.3522
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.016e-10 | 3.1063e-10 | 4.2892e-11 | -2.4215e-10 | -2.6042e-10 | -2.5255e-10 | 1.7334e-10 | -1.9973e-10 | 6.9893e-11 | -2.4054e-11 | -1.3645e-11 | -7.0769e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1571 | 1.1612 | 1.1594 | 1.1571 | 1.1612 | 1.1594 | -0.29532 | -120.1669 | 119.9133 | -0.29532 | -120.1669 | 119.9133
Line17_5_19 | 0.12376 | 0.11882 | 0.12165 | 0.12376 | 0.11882 | 0.12165 | 0.028581 | 0.027439 | 0.028094 | 0.028581 | 0.027439 | 0.028094 | -0.0021332 | -0.001416 | -0.00067123 | 0.0022876 | 0.0015596 | 0.00081546 | -0.03298 | -0.03181 | -0.032545 | 0.033282 | 0.032095 | 0.032842 | 93.4198 | -27.6042 | -148.8907 | -86.5802 | 152.3958 | 31.1093 |  | 1.1563 | 1.1604 | 1.1587 | 1.1673 | 1.1711 | 1.1694 | -0.2811 | -120.1529 | 119.9278 | -0.5121 | -120.3862 | 119.6869
Line1_1_3 | 0.10426 | 0.10012 | 0.10272 | 0.10426 | 0.10012 | 0.10272 | 0.024078 | 0.023122 | 0.023722 | 0.024078 | 0.023122 | 0.023722 | -0.0015522 | -0.00087883 | -0.00027723 | 0.001662 | 0.00098071 | 0.00037998 | -0.027535 | -0.026573 | -0.027232 | 0.02775 | 0.026775 | 0.027443 | 93.1808 | -28.0212 | -149.2437 | -86.8192 | 151.9788 | 30.7563 |  | 1.1454 | 1.1498 | 1.148 | 1.1546 | 1.1588 | 1.157 | -0.045696 | -119.9154 | 120.1731 | -0.2466 | -120.1189 | 119.9631
Line2_1_4 | 0.13196 | 0.12669 | 0.1296 | 0.13196 | 0.12669 | 0.1296 | 0.030475 | 0.029258 | 0.02993 | 0.030475 | 0.029258 | 0.02993 | -0.0021722 | -0.0014593 | -0.000653 | 0.0023476 | 0.0016226 | 0.00081677 | -0.034839 | -0.03361 | -0.034355 | 0.035183 | 0.033934 | 0.034692 | 93.5221 | -27.4293 | -148.738 | -86.4779 | 152.5707 | 31.262 |  | 1.1454 | 1.1498 | 1.148 | 1.1571 | 1.1612 | 1.1594 | -0.045696 | -119.9154 | 120.1731 | -0.29532 | -120.1669 | 119.9133
Line3_1_5 | 0.12376 | 0.11882 | 0.12165 | 0.12376 | 0.11882 | 0.12165 | 0.028581 | 0.027439 | 0.028094 | 0.028581 | 0.027439 | 0.028094 | -0.0019789 | -0.0012724 | -0.000527 | 0.0021332 | 0.001416 | 0.00067123 | -0.032677 | -0.031525 | -0.032249 | 0.03298 | 0.03181 | 0.032545 | 93.4198 | -27.6042 | -148.8907 | -86.5802 | 152.3958 | 31.1093 |  | 1.1454 | 1.1498 | 1.148 | 1.1563 | 1.1604 | 1.1587 | -0.045696 | -119.9154 | 120.1731 | -0.2811 | -120.1529 | 119.9278
Line4_2_6 | 0.087712 | 0.11111 | 0.11275 | 0.087712 | 0.11111 | 0.11275 | 0.020256 | 0.025659 | 0.026038 | 0.020256 | 0.025659 | 0.026038 | -0.0062347 | -0.012107 | -0.011424 | 0.0063107 | 0.012221 | 0.01156 | -0.022532 | -0.027199 | -0.027929 | 0.022693 | 0.027441 | 0.028178 | 105.3474 | -5.933 | -127.6418 | -74.6526 | 174.067 | 52.3582 |  | 1.1541 | 1.1603 | 1.1589 | 1.1628 | 1.1707 | 1.1697 | -0.11996 | -119.9274 | 120.1125 | -0.1931 | -119.9391 | 120.053
Line5_6_7 | 0.087712 | 0.11111 | 0.11275 | 0.087712 | 0.11111 | 0.11275 | 0.020256 | 0.025659 | 0.026038 | 0.020256 | 0.025659 | 0.026038 | -0.0063107 | -0.012221 | -0.01156 | 0.0063867 | 0.012336 | 0.011696 | -0.022693 | -0.027441 | -0.028178 | 0.022855 | 0.027683 | 0.028427 | 105.3474 | -5.933 | -127.6418 | -74.6526 | 174.067 | 52.3582 |  | 1.1628 | 1.1707 | 1.1697 | 1.1715 | 1.1811 | 1.1805 | -0.1931 | -119.9391 | 120.053 | -0.26517 | -119.9506 | 119.9946
Line6_7_8 | 0.038166 | 0 | 0 | 0.038166 | 0 | 0 | 0.0088142 | 0 | 0 | 0.0088142 | 0 | 0 | 0.0072955 | 1.5496e-09 | -1.3647e-10 | -0.0072834 | -1.3958e-09 | -2.3723e-10 | 0.0073077 | -1.0924e-09 | 1.1348e-10 | -0.0072834 | 7.4849e-10 | -7.4406e-11 | -45.3128 | 0 | 0 | 134.6872 | 0 | 0 |  | 1.1715 | 1.1811 | 1.1805 | 1.1686 | 1.1807 | 1.1804 | -0.26517 | -119.9506 | 119.9946 | -0.31279 | -119.9306 | 119.9653
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2352e-10 | 5.2326e-10 | -5.54e-11 | -2.9403e-10 | -3.4931e-10 | -3.4803e-10 | 3.5423e-10 | -3.7136e-10 | 3.5763e-11 | -2.5732e-11 | 5.7678e-12 | -2.8797e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1686 | 1.1807 | 1.1804 | 1.1686 | 1.1807 | 1.1804 | -0.31279 | -119.9306 | 119.9653 | -0.31279 | -119.9306 | 119.9653
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2352e-10 | 5.2326e-10 | -5.54e-11 | -2.9403e-10 | -3.4931e-10 | -3.4803e-10 | 3.5423e-10 | -3.7136e-10 | 3.5763e-11 | -2.5731e-11 | 5.7679e-12 | -2.8798e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1686 | 1.1807 | 1.1804 | 1.1686 | 1.1807 | 1.1804 | -0.31279 | -119.9306 | 119.9653 | -0.31279 | -119.9306 | 119.9653
Line9_3_11 | 0.10426 | 0.10012 | 0.10272 | 0.10426 | 0.10012 | 0.10272 | 0.024078 | 0.023122 | 0.023722 | 0.024078 | 0.023122 | 0.023722 | -0.001662 | -0.00098071 | -0.00037998 | 0.0017717 | 0.0010826 | 0.00048273 | -0.02775 | -0.026775 | -0.027443 | 0.027965 | 0.026978 | 0.027655 | 93.1808 | -28.0212 | -149.2437 | -86.8192 | 151.9788 | 30.7563 |  | 1.1546 | 1.1588 | 1.157 | 1.1638 | 1.1677 | 1.166 | -0.2466 | -120.1189 | 119.9631 | -0.44433 | -120.3192 | 119.7563

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.26722 | 0.023972 | 0.023706 | 0.26722 | 0.023973 | 0.023706 | 0.061711 | 0.0055362 | 0.0054746 | 0.061711 | 0.0055362 | 0.0054747 | 0.0048377 | -0.0044011 | 0.0047098 | -0.0036486 | 0.0044256 | -0.0046857 | 0.0049624 | 0.0074861 | 0.0067874 | -0.0037363 | -0.0074543 | -0.0067563 | -77.6357 | 93.607 | 94.2078 | 102.3643 | -86.393 | -85.7922 |  | 0.1123 | 1.5686 | 1.509 | 0.084624 | 1.5659 | 1.5018 | -31.9066 | -145.9416 | 149.451 | -31.9554 | -145.6958 | 149.4654
Line10_11_12 | 0.024297 | 0.023887 | 0.023805 | 0.024297 | 0.023888 | 0.023806 | 0.0056111 | 0.0055165 | 0.0054976 | 0.0056112 | 0.0055166 | 0.0054977 | -0.00038448 | -0.0043258 | 0.0047167 | 0.00039021 | 0.0043313 | -0.0047114 | -0.00051983 | 0.0074893 | 0.0068061 | 0.00052583 | -0.0074837 | -0.0068006 | 94.3925 | 94.148 | 94.1907 | -85.6075 | -85.852 | -85.8093 |  | 0.11523 | 1.5678 | 1.5062 | 0.11669 | 1.5674 | 1.5048 | -32.0953 | -145.8414 | 149.4681 | -32.1862 | -145.7913 | 149.4767
Line11_12_13 | 0.024297 | 0.023888 | 0.023806 | 0.024297 | 0.023888 | 0.023806 | 0.0056112 | 0.0055166 | 0.0054977 | 0.0056112 | 0.0055167 | 0.0054977 | -0.00039021 | -0.0043313 | 0.0047114 | 0.00039594 | 0.0043368 | -0.0047061 | -0.00052583 | 0.0074837 | 0.0068006 | 0.00053182 | -0.0074781 | -0.006795 | 94.3924 | 94.1479 | 94.1907 | -85.6076 | -85.8521 | -85.8093 |  | 0.11669 | 1.5674 | 1.5048 | 0.11816 | 1.567 | 1.5034 | -32.1862 | -145.7913 | 149.4767 | -32.2748 | -145.7411 | 149.4853
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3796e-08 | 1.7658e-07 | -1.6782e-07 | -8.9002e-09 | -1.2181e-07 | 1.0815e-07 | 2.0542e-08 | -2.7654e-07 | -2.6634e-07 | -1.3915e-08 | 1.8199e-07 | 1.8014e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11816 | 1.567 | 1.5034 | 0.11816 | 1.567 | 1.5034 | -32.2748 | -145.7411 | 149.4853 | -32.2748 | -145.7411 | 149.4853
Line13_13_14 | 0.024298 | 0.023889 | 0.023807 | 0.024299 | 0.023889 | 0.023807 | 0.0056114 | 0.0055169 | 0.0054979 | 0.0056115 | 0.0055169 | 0.005498 | -0.00039595 | -0.004337 | 0.0047062 | 0.00040168 | 0.0043425 | -0.0047009 | -0.00053184 | 0.0074784 | 0.0067953 | 0.00053784 | -0.0074728 | -0.0067898 | 94.3923 | 94.1478 | 94.1906 | -85.6077 | -85.8522 | -85.8094 |  | 0.11816 | 1.567 | 1.5034 | 0.11963 | 1.5666 | 1.502 | -32.2748 | -145.7411 | 149.4853 | -32.3612 | -145.6909 | 149.4939
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1971e-09 | 1.1772e-07 | -1.1188e-07 | -4.3017e-09 | -6.2946e-08 | 5.2209e-08 | 1.3695e-08 | -1.8436e-07 | -1.7756e-07 | -7.0672e-09 | 8.981e-08 | 9.1357e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11816 | 1.567 | 1.5034 | 0.11816 | 1.567 | 1.5034 | -32.2748 | -145.7411 | 149.4853 | -32.2748 | -145.7411 | 149.4853
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5985e-09 | 5.8859e-08 | -5.5939e-08 | 2.9681e-10 | -4.0868e-09 | -3.7292e-09 | 6.8474e-09 | -9.2181e-08 | -8.8779e-08 | -2.1978e-10 | -2.3706e-09 | 2.5777e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11816 | 1.567 | 1.5034 | 0.11816 | 1.567 | 1.5034 | -32.2748 | -145.7411 | 149.4853 | -32.2748 | -145.7411 | 149.4853
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3896e-09 | 5.9213e-08 | -5.6026e-08 | 2.886e-10 | -4.103e-09 | -3.7617e-09 | 6.6543e-09 | -9.2541e-08 | -8.9537e-08 | -2.1005e-10 | -2.3853e-09 | 2.5828e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11377 | 1.5682 | 1.5076 | 0.11377 | 1.5682 | 1.5076 | -32.0062 | -145.8912 | 149.4598 | -32.0062 | -145.8912 | 149.4598
Line17_5_19 | 0.02439 | 0.023979 | 0.023896 | 0.02439 | 0.023979 | 0.023896 | 0.0056326 | 0.0055376 | 0.0055185 | 0.0056326 | 0.0055377 | 0.0055186 | -0.00037841 | -0.0043638 | 0.0047156 | 0.00038418 | 0.0043694 | -0.0047103 | -0.00051716 | 0.007508 | 0.0068545 | 0.0005232 | -0.0075024 | -0.0068489 | 94.1884 | 93.9427 | 93.9863 | -85.8116 | -86.0573 | -86.0137 |  | 0.11377 | 1.5682 | 1.5076 | 0.11524 | 1.5678 | 1.5062 | -32.0052 | -145.8913 | 149.4597 | -32.1012 | -145.8409 | 149.4685
Line1_1_3 | 0.024296 | 0.023887 | 0.023805 | 0.024296 | 0.023887 | 0.023805 | 0.0056109 | 0.0055164 | 0.0054975 | 0.005611 | 0.0055164 | 0.0054975 | -0.00037303 | -0.0043147 | 0.0047274 | 0.00037876 | 0.0043203 | -0.0047221 | -0.00050783 | 0.0075004 | 0.0068171 | 0.00051383 | -0.0074948 | -0.0068116 | 94.3925 | 94.148 | 94.1908 | -85.6075 | -85.852 | -85.8092 |  | 0.1123 | 1.5686 | 1.509 | 0.11377 | 1.5682 | 1.5076 | -31.9066 | -145.9416 | 149.451 | -32.0022 | -145.8915 | 149.4595
Line2_1_4 | 0.02442 | 0.024008 | 0.023925 | 0.02442 | 0.024009 | 0.023926 | 0.0056395 | 0.0055445 | 0.0055253 | 0.0056396 | 0.0055445 | 0.0055254 | -0.0003725 | -0.0043727 | 0.0047187 | 0.00037828 | 0.0043783 | -0.0047133 | -0.0005122 | 0.0075178 | 0.0068743 | 0.00051826 | -0.0075122 | -0.0068687 | 94.1201 | 93.874 | 93.9178 | -85.8799 | -86.126 | -86.0822 |  | 0.1123 | 1.5686 | 1.509 | 0.11377 | 1.5682 | 1.5076 | -31.9066 | -145.9416 | 149.451 | -32.0062 | -145.8912 | 149.4598
Line3_1_5 | 0.024389 | 0.023978 | 0.023896 | 0.02439 | 0.023979 | 0.023896 | 0.0056325 | 0.0055375 | 0.0055185 | 0.0056326 | 0.0055376 | 0.0055185 | -0.00037264 | -0.0043582 | 0.004721 | 0.00037841 | 0.0043638 | -0.0047156 | -0.00051111 | 0.0075136 | 0.0068601 | 0.00051716 | -0.007508 | -0.0068545 | 94.1884 | 93.9427 | 93.9863 | -85.8116 | -86.0573 | -86.0137 |  | 0.1123 | 1.5686 | 1.509 | 0.11377 | 1.5682 | 1.5076 | -31.9066 | -145.9416 | 149.451 | -32.0052 | -145.8913 | 149.4597
Line4_2_6 | 0.26722 | 0.023973 | 0.023706 | 0.26722 | 0.023973 | 0.023706 | 0.061711 | 0.0055362 | 0.0054747 | 0.061711 | 0.0055363 | 0.0054748 | 0.0036486 | -0.0044256 | 0.0046857 | -0.0024595 | 0.00445 | -0.0046615 | 0.0037363 | 0.0074543 | 0.0067563 | -0.0025102 | -0.0074225 | -0.0067251 | -77.6357 | 93.6069 | 94.2078 | 102.3643 | -86.3931 | -85.7922 |  | 0.084624 | 1.5659 | 1.5018 | 0.056948 | 1.5632 | 1.4946 | -31.9554 | -145.6958 | 149.4654 | -32.0518 | -145.449 | 149.48
Line5_6_7 | 0.26722 | 0.023973 | 0.023706 | 0.26722 | 0.023973 | 0.023707 | 0.061711 | 0.0055363 | 0.0054748 | 0.061711 | 0.0055364 | 0.0054748 | 0.0024595 | -0.00445 | 0.0046615 | -0.0012705 | 0.0044745 | -0.0046373 | 0.0025102 | 0.0074225 | 0.0067251 | -0.0012841 | -0.0073907 | -0.0066939 | -77.6357 | 93.6069 | 94.2077 | 102.3643 | -86.3931 | -85.7923 |  | 0.056948 | 1.5632 | 1.4946 | 0.029272 | 1.5605 | 1.4874 | -32.0518 | -145.449 | 149.48 | -32.3306 | -145.2015 | 149.4948
Line6_7_8 | 0.2926 | 0 | 0 | 0.29259 | 0 | 0 | 0.067572 | 0 | 0 | 0.067572 | 0 | 0 | 0.0013698 | 1.869e-07 | -1.6602e-07 | 1.3266e-15 | -1.2928e-07 | 1.0665e-07 | 0.0014269 | -2.7766e-07 | -2.7242e-07 | -9.2041e-15 | 1.8221e-07 | 1.837e-07 | -78.4997 | 0 | 0 | 101.5003 | 0 | 0 |  | 0.029272 | 1.5605 | 1.4874 | 0 | 1.5583 | 1.4815 | -32.3306 | -145.2015 | 149.4948 | 0 | -145.0031 | 149.502
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.246e-21 | 6.2646e-08 | -5.5106e-08 | -2.1999e-17 | -3.9841e-09 | -3.5567e-09 | 9.2594e-21 | -9.2254e-08 | -9.0577e-08 | 2.3461e-17 | -2.2942e-09 | 2.5414e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.5583 | 1.4815 | 0 | 1.5583 | 1.4815 | 0 | -145.0031 | 149.502 | 0 | -145.0031 | 149.502
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.246e-21 | 6.2646e-08 | -5.5106e-08 | -2.1999e-17 | -3.9841e-09 | -3.5567e-09 | 9.2594e-21 | -9.2254e-08 | -9.0577e-08 | 2.3461e-17 | -2.2942e-09 | 2.5414e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.5583 | 1.4815 | 0 | 1.5583 | 1.4815 | 0 | -145.0031 | 149.502 | 0 | -145.0031 | 149.502
Line9_3_11 | 0.024296 | 0.023887 | 0.023805 | 0.024297 | 0.023887 | 0.023805 | 0.005611 | 0.0055164 | 0.0054975 | 0.0056111 | 0.0055165 | 0.0054976 | -0.00037876 | -0.0043203 | 0.0047221 | 0.00038448 | 0.0043258 | -0.0047167 | -0.00051383 | 0.0074948 | 0.0068116 | 0.00051983 | -0.0074893 | -0.0068061 | 94.3925 | 94.148 | 94.1908 | -85.6075 | -85.852 | -85.8092 |  | 0.11377 | 1.5682 | 1.5076 | 0.11523 | 1.5678 | 1.5062 | -32.0022 | -145.8915 | 149.4595 | -32.0953 | -145.8414 | 149.4681

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.25315 | 0.022711 | 0.022458 | 0.25315 | 0.022711 | 0.022458 | 0.058463 | 0.0052448 | 0.0051865 | 0.058463 | 0.0052449 | 0.0051866 | 0.0043418 | -0.00395 | 0.0042271 | -0.0032746 | 0.003972 | -0.0042054 | 0.0044538 | 0.0067188 | 0.0060918 | -0.0033533 | -0.0066903 | -0.0060638 | -77.6357 | 93.607 | 94.2078 | 102.3643 | -86.393 | -85.7922 |  | 0.10639 | 1.486 | 1.4296 | 0.08017 | 1.4835 | 1.4228 | -31.9066 | -145.9416 | 149.451 | -31.9554 | -145.6958 | 149.4654
Line10_11_12 | 0.023018 | 0.02263 | 0.022552 | 0.023018 | 0.02263 | 0.022553 | 0.0053158 | 0.0052262 | 0.0052082 | 0.0053158 | 0.0052262 | 0.0052083 | -0.00034507 | -0.0038824 | 0.0042333 | 0.00035021 | 0.0038874 | -0.0042285 | -0.00046655 | 0.0067217 | 0.0061085 | 0.00047193 | -0.0067167 | -0.0061035 | 94.3925 | 94.148 | 94.1907 | -85.6075 | -85.852 | -85.8093 |  | 0.10917 | 1.4853 | 1.427 | 0.11055 | 1.4849 | 1.4256 | -32.0953 | -145.8414 | 149.4681 | -32.1862 | -145.7913 | 149.4767
Line11_12_13 | 0.023018 | 0.02263 | 0.022553 | 0.023019 | 0.022631 | 0.022553 | 0.0053158 | 0.0052262 | 0.0052083 | 0.0053159 | 0.0052263 | 0.0052084 | -0.00035021 | -0.0038874 | 0.0042285 | 0.00035535 | 0.0038923 | -0.0042237 | -0.00047193 | 0.0067167 | 0.0061036 | 0.00047732 | -0.0067117 | -0.0060986 | 94.3924 | 94.1479 | 94.1907 | -85.6076 | -85.8521 | -85.8093 |  | 0.11055 | 1.4849 | 1.4256 | 0.11194 | 1.4845 | 1.4243 | -32.1862 | -145.7913 | 149.4767 | -32.2748 | -145.7411 | 149.4853
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2382e-08 | 1.5848e-07 | -1.5062e-07 | -7.988e-09 | -1.0932e-07 | 9.7063e-08 | 1.8437e-08 | -2.482e-07 | -2.3904e-07 | -1.2488e-08 | 1.6334e-07 | 1.6167e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11194 | 1.4845 | 1.4243 | 0.11194 | 1.4845 | 1.4243 | -32.2748 | -145.7411 | 149.4853 | -32.2748 | -145.7411 | 149.4853
Line13_13_14 | 0.023019 | 0.022631 | 0.022554 | 0.02302 | 0.022632 | 0.022554 | 0.0053161 | 0.0052265 | 0.0052086 | 0.0053162 | 0.0052266 | 0.0052086 | -0.00035537 | -0.0038925 | 0.0042239 | 0.00036051 | 0.0038974 | -0.0042191 | -0.00047733 | 0.0067119 | 0.0060988 | 0.00048272 | -0.0067069 | -0.0060939 | 94.3923 | 94.1478 | 94.1906 | -85.6077 | -85.8522 | -85.8094 |  | 0.11194 | 1.4845 | 1.4243 | 0.11333 | 1.4842 | 1.423 | -32.2748 | -145.7411 | 149.4853 | -32.3612 | -145.6909 | 149.4939
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2544e-09 | 1.0565e-07 | -1.0041e-07 | -3.8608e-09 | -5.6495e-08 | 4.6858e-08 | 1.2291e-08 | -1.6547e-07 | -1.5936e-07 | -6.3428e-09 | 8.0605e-08 | 8.1994e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11194 | 1.4845 | 1.4243 | 0.11194 | 1.4845 | 1.4243 | -32.2748 | -145.7411 | 149.4853 | -32.2748 | -145.7411 | 149.4853
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1272e-09 | 5.2827e-08 | -5.0205e-08 | 2.6639e-10 | -3.668e-09 | -3.347e-09 | 6.1456e-09 | -8.2733e-08 | -7.968e-08 | -1.9726e-10 | -2.1277e-09 | 2.3135e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.11194 | 1.4845 | 1.4243 | 0.11194 | 1.4845 | 1.4243 | -32.2748 | -145.7411 | 149.4853 | -32.2748 | -145.7411 | 149.4853
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9397e-09 | 5.3144e-08 | -5.0284e-08 | 2.5902e-10 | -3.6825e-09 | -3.3761e-09 | 5.9723e-09 | -8.3056e-08 | -8.036e-08 | -1.8852e-10 | -2.1408e-09 | 2.3181e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.10778 | 1.4857 | 1.4283 | 0.10778 | 1.4857 | 1.4283 | -32.0062 | -145.8912 | 149.4598 | -32.0062 | -145.8912 | 149.4598
Line17_5_19 | 0.023106 | 0.022716 | 0.022638 | 0.023106 | 0.022717 | 0.022639 | 0.0053361 | 0.0052461 | 0.0052281 | 0.0053362 | 0.0052462 | 0.0052281 | -0.00033963 | -0.0039165 | 0.0042323 | 0.00034481 | 0.0039215 | -0.0042275 | -0.00046415 | 0.0067385 | 0.006152 | 0.00046958 | -0.0067334 | -0.006147 | 94.1884 | 93.9427 | 93.9863 | -85.8116 | -86.0573 | -86.0137 |  | 0.10778 | 1.4857 | 1.4283 | 0.10917 | 1.4853 | 1.427 | -32.0052 | -145.8913 | 149.4597 | -32.1012 | -145.8409 | 149.4685
Line1_1_3 | 0.023017 | 0.022629 | 0.022552 | 0.023018 | 0.02263 | 0.022552 | 0.0053156 | 0.005226 | 0.0052081 | 0.0053157 | 0.0052261 | 0.0052082 | -0.0003348 | -0.0038725 | 0.0042429 | 0.00033994 | 0.0038775 | -0.0042381 | -0.00045578 | 0.0067317 | 0.0061184 | 0.00046117 | -0.0067267 | -0.0061135 | 94.3925 | 94.148 | 94.1908 | -85.6075 | -85.852 | -85.8092 |  | 0.10639 | 1.486 | 1.4296 | 0.10778 | 1.4857 | 1.4283 | -31.9066 | -145.9416 | 149.451 | -32.0022 | -145.8915 | 149.4595
Line2_1_4 | 0.023135 | 0.022745 | 0.022666 | 0.023135 | 0.022745 | 0.022666 | 0.0053427 | 0.0052527 | 0.0052345 | 0.0053428 | 0.0052527 | 0.0052346 | -0.00033432 | -0.0039245 | 0.0042351 | 0.00033951 | 0.0039295 | -0.0042302 | -0.0004597 | 0.0067473 | 0.0061697 | 0.00046514 | -0.0067422 | -0.0061647 | 94.1201 | 93.874 | 93.9178 | -85.8799 | -86.126 | -86.0822 |  | 0.10639 | 1.486 | 1.4296 | 0.10778 | 1.4857 | 1.4283 | -31.9066 | -145.9416 | 149.451 | -32.0062 | -145.8912 | 149.4598
Line3_1_5 | 0.023106 | 0.022716 | 0.022638 | 0.023106 | 0.022716 | 0.022638 | 0.005336 | 0.0052461 | 0.005228 | 0.0053361 | 0.0052461 | 0.0052281 | -0.00033445 | -0.0039115 | 0.0042372 | 0.00033963 | 0.0039165 | -0.0042323 | -0.00045873 | 0.0067435 | 0.006157 | 0.00046415 | -0.0067385 | -0.006152 | 94.1884 | 93.9427 | 93.9863 | -85.8116 | -86.0573 | -86.0137 |  | 0.10639 | 1.486 | 1.4296 | 0.10778 | 1.4857 | 1.4283 | -31.9066 | -145.9416 | 149.451 | -32.0052 | -145.8913 | 149.4597
Line4_2_6 | 0.25315 | 0.022711 | 0.022458 | 0.25315 | 0.022711 | 0.022459 | 0.058463 | 0.0052449 | 0.0051866 | 0.058463 | 0.0052449 | 0.0051866 | 0.0032746 | -0.003972 | 0.0042054 | -0.0022075 | 0.0039939 | -0.0041837 | 0.0033533 | 0.0066903 | 0.0060638 | -0.0022529 | -0.0066618 | -0.0060358 | -77.6357 | 93.6069 | 94.2078 | 102.3643 | -86.3931 | -85.7922 |  | 0.08017 | 1.4835 | 1.4228 | 0.053951 | 1.4809 | 1.416 | -31.9554 | -145.6958 | 149.4654 | -32.0518 | -145.449 | 149.48
Line5_6_7 | 0.25315 | 0.022711 | 0.022459 | 0.25315 | 0.022711 | 0.022459 | 0.058463 | 0.0052449 | 0.0051866 | 0.058463 | 0.005245 | 0.0051867 | 0.0022075 | -0.0039939 | 0.0041837 | -0.0011403 | 0.0040159 | -0.004162 | 0.0022529 | 0.0066618 | 0.0060358 | -0.0011525 | -0.0066332 | -0.0060078 | -77.6357 | 93.6069 | 94.2077 | 102.3643 | -86.3931 | -85.7923 |  | 0.053951 | 1.4809 | 1.416 | 0.027731 | 1.4784 | 1.4091 | -32.0518 | -145.449 | 149.48 | -32.3306 | -145.2015 | 149.4948
Line6_7_8 | 0.2772 | 0 | 0 | 0.2772 | 0 | 0 | 0.064016 | 0 | 0 | 0.064016 | 0 | 0 | 0.0012294 | 1.6774e-07 | -1.49e-07 | 1.1937e-15 | -1.1603e-07 | 9.5723e-08 | 0.0012806 | -2.4921e-07 | -2.445e-07 | -8.2354e-15 | 1.6354e-07 | 1.6487e-07 | -78.4997 | 0 | 0 | 101.5003 | 0 | 0 |  | 0.027731 | 1.4784 | 1.4091 | 0 | 1.4762 | 1.4036 | -32.3306 | -145.2015 | 149.4948 | 0 | -145.0031 | 149.502
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9113e-21 | 5.6226e-08 | -4.9458e-08 | -1.9744e-17 | -3.5757e-09 | -3.1922e-09 | 8.2835e-21 | -8.2798e-08 | -8.1294e-08 | 2.1057e-17 | -2.0591e-09 | 2.2809e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.4762 | 1.4036 | 0 | 1.4762 | 1.4036 | 0 | -145.0031 | 149.502 | 0 | -145.0031 | 149.502
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9113e-21 | 5.6226e-08 | -4.9458e-08 | -1.9744e-17 | -3.5757e-09 | -3.1922e-09 | 8.2835e-21 | -8.2798e-08 | -8.1294e-08 | 2.1057e-17 | -2.0591e-09 | 2.2809e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1.4762 | 1.4036 | 0 | 1.4762 | 1.4036 | 0 | -145.0031 | 149.502 | 0 | -145.0031 | 149.502
Line9_3_11 | 0.023018 | 0.02263 | 0.022552 | 0.023018 | 0.02263 | 0.022552 | 0.0053157 | 0.0052261 | 0.0052082 | 0.0053158 | 0.0052262 | 0.0052082 | -0.00033994 | -0.0038775 | 0.0042381 | 0.00034508 | 0.0038824 | -0.0042333 | -0.00046117 | 0.0067267 | 0.0061135 | 0.00046655 | -0.0067217 | -0.0061085 | 94.3925 | 94.148 | 94.1908 | -85.6075 | -85.852 | -85.8092 |  | 0.10778 | 1.4857 | 1.4283 | 0.10917 | 1.4853 | 1.427 | -32.0022 | -145.8915 | 149.4595 | -32.0953 | -145.8414 | 149.4681

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.025996 | 0.0023321 | 0.0023062 | 0.025996 | 0.0023322 | 0.0023063 | 0.0060036 | 0.00053859 | 0.0005326 | 0.0060036 | 0.00053859 | 0.00053261 | 0.0038011 | -0.00022426 | 0.00050458 | -0.0037898 | 0.0002245 | -0.00050435 | 0.0036907 | 0.00050329 | 1.9833e-06 | -0.0036791 | -0.00050299 | -1.6874e-06 | -47.214 | 124.0287 | 124.6295 | 132.786 | -55.9713 | -55.3705 |  | 0.88248 | 1.023 | 0.94739 | 0.87979 | 1.0227 | 0.94696 | -3.0582 | -121.9538 | 124.8547 | -3.0635 | -121.919 | 124.8212
Line10_11_12 | 0.0023637 | 0.0023239 | 0.0023159 | 0.0023637 | 0.0023239 | 0.0023159 | 0.00054588 | 0.00053667 | 0.00053483 | 0.00054588 | 0.00053668 | 0.00053484 | -0.00029584 | -0.00021882 | 0.00050659 | 0.0002959 | 0.00021888 | -0.00050654 | -0.00038038 | 0.00050348 | 2.0363e-06 | 0.00038044 | -0.00050343 | -1.9832e-06 | 124.8142 | 124.5697 | 124.6125 | -55.1858 | -55.4303 | -55.3875 |  | 0.88277 | 1.0229 | 0.9472 | 0.88291 | 1.0229 | 0.9471 | -3.0601 | -121.9394 | 124.8428 | -3.0611 | -121.9322 | 124.8368
Line11_12_13 | 0.0023637 | 0.0023239 | 0.0023159 | 0.0023638 | 0.0023239 | 0.002316 | 0.00054588 | 0.00053668 | 0.00053484 | 0.00054589 | 0.00053669 | 0.00053485 | -0.0002959 | -0.00021888 | 0.00050654 | 0.00029596 | 0.00021893 | -0.0005065 | -0.00038044 | 0.00050343 | 1.9835e-06 | 0.0003805 | -0.00050339 | -1.9304e-06 | 124.8141 | 124.5696 | 124.6124 | -55.1859 | -55.4304 | -55.3876 |  | 0.88291 | 1.0229 | 0.9471 | 0.88305 | 1.0228 | 0.947 | -3.0611 | -121.9322 | 124.8368 | -3.062 | -121.925 | 124.8308
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0343e-08 | 9.1182e-09 | -1.9269e-08 | -6.6829e-09 | -6.3539e-09 | 1.2845e-08 | 1.472e-08 | -1.8734e-08 | -9.1187e-10 | -9.9778e-09 | 1.2369e-08 | 8.8571e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.88305 | 1.0228 | 0.947 | 0.88305 | 1.0228 | 0.947 | -3.062 | -121.925 | 124.8308 | -3.062 | -121.925 | 124.8308
Line13_13_14 | 0.0023639 | 0.002324 | 0.002316 | 0.0023639 | 0.002324 | 0.0023161 | 0.00054591 | 0.00053671 | 0.00053487 | 0.00054592 | 0.00053671 | 0.00053487 | -0.00029597 | -0.00021894 | 0.00050652 | 0.00029603 | 0.000219 | -0.00050647 | -0.00038052 | 0.0005034 | 1.9315e-06 | 0.00038058 | -0.00050336 | -1.8784e-06 | 124.814 | 124.5695 | 124.6123 | -55.186 | -55.4305 | -55.3877 |  | 0.88305 | 1.0228 | 0.947 | 0.8832 | 1.0228 | 0.94691 | -3.062 | -121.925 | 124.8308 | -3.063 | -121.9179 | 124.8248
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8953e-09 | 6.0788e-09 | -1.2846e-08 | -3.2353e-09 | -3.3145e-09 | 6.4217e-09 | 9.8135e-09 | -1.2489e-08 | -6.0791e-10 | -5.071e-09 | 6.1249e-09 | 5.8175e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.88305 | 1.0228 | 0.947 | 0.88305 | 1.0228 | 0.947 | -3.062 | -121.925 | 124.8308 | -3.062 | -121.925 | 124.8308
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4476e-09 | 3.0394e-09 | -6.423e-09 | 2.1237e-10 | -2.7511e-10 | -1.3165e-12 | 4.9067e-09 | -6.2446e-09 | -3.0396e-10 | -1.6431e-10 | -1.1968e-10 | 2.778e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.88305 | 1.0228 | 0.947 | 0.88305 | 1.0228 | 0.947 | -3.062 | -121.925 | 124.8308 | -3.062 | -121.925 | 124.8308
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4411e-09 | 3.0713e-09 | -6.4478e-09 | 2.1366e-10 | -2.758e-10 | -2.401e-12 | 4.9352e-09 | -6.2592e-09 | -3.302e-10 | -1.6408e-10 | -1.2104e-10 | 2.7891e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.88263 | 1.023 | 0.94729 | 0.88263 | 1.023 | 0.94729 | -3.0592 | -121.9465 | 124.8487 | -3.0592 | -121.9465 | 124.8487
Line17_5_19 | 0.0023728 | 0.0023328 | 0.0023247 | 0.0023728 | 0.0023328 | 0.0023247 | 0.00054796 | 0.00053873 | 0.00053687 | 0.00054797 | 0.00053873 | 0.00053688 | -0.00029556 | -0.00022142 | 0.00050856 | 0.00029562 | 0.00022147 | -0.00050851 | -0.00038283 | 0.00050467 | 3.9125e-06 | 0.00038289 | -0.00050462 | -3.859e-06 | 124.6101 | 124.3644 | 124.408 | -55.3899 | -55.6356 | -55.592 |  | 0.88263 | 1.023 | 0.94729 | 0.88277 | 1.0229 | 0.94719 | -3.0592 | -121.9465 | 124.8487 | -3.0602 | -121.9393 | 124.8428
Line1_1_3 | 0.0023636 | 0.0023238 | 0.0023158 | 0.0023637 | 0.0023238 | 0.0023159 | 0.00054586 | 0.00053666 | 0.00053482 | 0.00054587 | 0.00053667 | 0.00053483 | -0.00029573 | -0.00021872 | 0.00050668 | 0.00029578 | 0.00021877 | -0.00050663 | -0.00038025 | 0.00050358 | 2.142e-06 | 0.00038032 | -0.00050353 | -2.0889e-06 | 124.8143 | 124.5697 | 124.6125 | -55.1857 | -55.4303 | -55.3875 |  | 0.88248 | 1.023 | 0.94739 | 0.88262 | 1.023 | 0.94729 | -3.0582 | -121.9538 | 124.8547 | -3.0592 | -121.9466 | 124.8488
Line2_1_4 | 0.0023757 | 0.0023356 | 0.0023276 | 0.0023757 | 0.0023357 | 0.0023276 | 0.00054864 | 0.00053939 | 0.00053753 | 0.00054865 | 0.0005394 | 0.00053754 | -0.00029541 | -0.00022225 | 0.00050923 | 0.00029547 | 0.0002223 | -0.00050919 | -0.0003836 | 0.00050508 | 4.5791e-06 | 0.00038366 | -0.00050503 | -4.5255e-06 | 124.5418 | 124.2957 | 124.3395 | -55.4582 | -55.7043 | -55.6605 |  | 0.88248 | 1.023 | 0.94739 | 0.88263 | 1.023 | 0.94729 | -3.0582 | -121.9538 | 124.8547 | -3.0592 | -121.9465 | 124.8487
Line3_1_5 | 0.0023727 | 0.0023327 | 0.0023247 | 0.0023728 | 0.0023328 | 0.0023247 | 0.00054796 | 0.00053872 | 0.00053686 | 0.00054796 | 0.00053873 | 0.00053687 | -0.0002955 | -0.00022136 | 0.0005086 | 0.00029556 | 0.00022142 | -0.00050856 | -0.00038277 | 0.00050472 | 3.9657e-06 | 0.00038283 | -0.00050467 | -3.9122e-06 | 124.6101 | 124.3645 | 124.408 | -55.3899 | -55.6355 | -55.592 |  | 0.88248 | 1.023 | 0.94739 | 0.88263 | 1.023 | 0.94729 | -3.0582 | -121.9538 | 124.8547 | -3.0592 | -121.9465 | 124.8487
Line4_2_6 | 0.025996 | 0.0023322 | 0.0023063 | 0.025996 | 0.0023322 | 0.0023063 | 0.0060036 | 0.00053859 | 0.00053261 | 0.0060036 | 0.0005386 | 0.00053261 | 0.0037898 | -0.0002245 | 0.00050435 | -0.0037786 | 0.00022473 | -0.00050413 | 0.0036791 | 0.00050299 | 1.6877e-06 | -0.0036675 | -0.0005027 | -1.3918e-06 | -47.214 | 124.0287 | 124.6295 | 132.786 | -55.9713 | -55.3705 |  | 0.87979 | 1.0227 | 0.94696 | 0.8771 | 1.0224 | 0.94652 | -3.0635 | -121.919 | 124.8212 | -3.0688 | -121.8843 | 124.7877
Line5_6_7 | 0.025996 | 0.0023322 | 0.0023063 | 0.025996 | 0.0023322 | 0.0023063 | 0.0060036 | 0.0005386 | 0.00053261 | 0.0060036 | 0.00053861 | 0.00053262 | 0.0037786 | -0.00022473 | 0.00050413 | -0.0037673 | 0.00022496 | -0.00050391 | 0.0036675 | 0.0005027 | 1.3921e-06 | -0.0036559 | -0.0005024 | -1.0962e-06 | -47.214 | 124.0286 | 124.6295 | 132.786 | -55.9714 | -55.3705 |  | 0.8771 | 1.0224 | 0.94652 | 0.87441 | 1.022 | 0.94609 | -3.0688 | -121.8843 | 124.7877 | -3.0742 | -121.8495 | 124.7541
Line6_7_8 | 0.028465 | 0 | 0 | 0.028465 | 0 | 0 | 0.0065737 | 0 | 0 | 0.0065737 | 0 | 0 | 0.0040643 | 9.6402e-09 | -1.9705e-08 | -0.0040513 | -6.7158e-09 | 1.3148e-08 | 0.0040648 | -1.9022e-08 | -1.1979e-09 | -0.0040513 | 1.257e-08 | 1.0724e-09 | -48.078 | 0 | 0 | 131.922 | 0 | 0 |  | 0.87441 | 1.022 | 0.94609 | 0.87156 | 1.0217 | 0.94575 | -3.0742 | -121.8495 | 124.7541 | -3.078 | -121.8218 | 124.7264
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3702e-09 | 3.2226e-09 | -6.5721e-09 | 2.4629e-10 | -2.7056e-10 | 3.5284e-12 | 5.0186e-09 | -6.3415e-09 | -4.0049e-10 | -1.6301e-10 | -1.1315e-10 | 2.7145e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.87156 | 1.0217 | 0.94575 | 0.87156 | 1.0217 | 0.94575 | -3.078 | -121.8218 | 124.7264 | -3.078 | -121.8218 | 124.7264
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3702e-09 | 3.2226e-09 | -6.5721e-09 | 2.4629e-10 | -2.7056e-10 | 3.5284e-12 | 5.0186e-09 | -6.3415e-09 | -4.0049e-10 | -1.6301e-10 | -1.1315e-10 | 2.7145e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.87156 | 1.0217 | 0.94575 | 0.87156 | 1.0217 | 0.94575 | -3.078 | -121.8218 | 124.7264 | -3.078 | -121.8218 | 124.7264
Line9_3_11 | 0.0023637 | 0.0023238 | 0.0023159 | 0.0023637 | 0.0023239 | 0.0023159 | 0.00054587 | 0.00053667 | 0.00053483 | 0.00054588 | 0.00053667 | 0.00053483 | -0.00029578 | -0.00021877 | 0.00050663 | 0.00029584 | 0.00021882 | -0.00050659 | -0.00038032 | 0.00050353 | 2.0891e-06 | 0.00038038 | -0.00050348 | -2.036e-06 | 124.8142 | 124.5697 | 124.6125 | -55.1858 | -55.4303 | -55.3875 |  | 0.88262 | 1.023 | 0.94729 | 0.88277 | 1.0229 | 0.9472 | -3.0592 | -121.9466 | 124.8488 | -3.0601 | -121.9394 | 124.8428

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.024628 | 0.0022094 | 0.0021848 | 0.024628 | 0.0022094 | 0.0021849 | 0.0056876 | 0.00051024 | 0.00050457 | 0.0056876 | 0.00051025 | 0.00050457 | 0.0034115 | -0.00020128 | 0.00045286 | -0.0034014 | 0.00020149 | -0.00045266 | 0.0033124 | 0.0004517 | 1.78e-06 | -0.003302 | -0.00045144 | -1.5144e-06 | -47.214 | 124.0287 | 124.6295 | 132.786 | -55.9713 | -55.3705 |  | 0.83604 | 0.96919 | 0.89753 | 0.83349 | 0.96887 | 0.89712 | -3.0582 | -121.9538 | 124.8547 | -3.0635 | -121.919 | 124.8212
Line10_11_12 | 0.0022393 | 0.0022016 | 0.002194 | 0.0022393 | 0.0022016 | 0.002194 | 0.00051714 | 0.00050843 | 0.00050668 | 0.00051715 | 0.00050843 | 0.00050669 | -0.00026552 | -0.0001964 | 0.00045467 | 0.00026557 | 0.00019645 | -0.00045463 | -0.00034139 | 0.00045188 | 1.8276e-06 | 0.00034145 | -0.00045183 | -1.7799e-06 | 124.8142 | 124.5697 | 124.6125 | -55.1858 | -55.4303 | -55.3875 |  | 0.83631 | 0.96909 | 0.89734 | 0.83644 | 0.96904 | 0.89725 | -3.0601 | -121.9394 | 124.8428 | -3.0611 | -121.9322 | 124.8368
Line11_12_13 | 0.0022393 | 0.0022016 | 0.002194 | 0.0022394 | 0.0022016 | 0.0021941 | 0.00051715 | 0.00050843 | 0.00050669 | 0.00051716 | 0.00050844 | 0.0005067 | -0.00026557 | -0.00019645 | 0.00045463 | 0.00026562 | 0.00019649 | -0.00045459 | -0.00034145 | 0.00045183 | 1.7802e-06 | 0.0003415 | -0.00045179 | -1.7325e-06 | 124.8141 | 124.5696 | 124.6124 | -55.1859 | -55.4304 | -55.3876 |  | 0.83644 | 0.96904 | 0.89725 | 0.83658 | 0.96899 | 0.89716 | -3.0611 | -121.9322 | 124.8368 | -3.062 | -121.925 | 124.8308
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2828e-09 | 8.1836e-09 | -1.7294e-08 | -5.9979e-09 | -5.7027e-09 | 1.1528e-08 | 1.3211e-08 | -1.6814e-08 | -8.1841e-10 | -8.9551e-09 | 1.1102e-08 | 7.9493e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.83658 | 0.96899 | 0.89716 | 0.83658 | 0.96899 | 0.89716 | -3.062 | -121.925 | 124.8308 | -3.062 | -121.925 | 124.8308
Line13_13_14 | 0.0022394 | 0.0022017 | 0.0021941 | 0.0022395 | 0.0022017 | 0.0021942 | 0.00051718 | 0.00050846 | 0.00050672 | 0.00051718 | 0.00050847 | 0.00050672 | -0.00026563 | -0.0001965 | 0.0004546 | 0.00026568 | 0.00019655 | -0.00045456 | -0.00034151 | 0.00045181 | 1.7336e-06 | 0.00034157 | -0.00045177 | -1.6859e-06 | 124.814 | 124.5695 | 124.6123 | -55.186 | -55.4305 | -55.3877 |  | 0.83658 | 0.96899 | 0.89716 | 0.83671 | 0.96894 | 0.89707 | -3.062 | -121.925 | 124.8308 | -3.063 | -121.9179 | 124.8248
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1885e-09 | 5.4557e-09 | -1.1529e-08 | -2.9037e-09 | -2.9748e-09 | 5.7635e-09 | 8.8076e-09 | -1.1209e-08 | -5.4561e-10 | -4.5513e-09 | 5.4971e-09 | 5.2213e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.83658 | 0.96899 | 0.89716 | 0.83658 | 0.96899 | 0.89716 | -3.062 | -121.925 | 124.8308 | -3.062 | -121.925 | 124.8308
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0943e-09 | 2.7279e-09 | -5.7647e-09 | 1.9061e-10 | -2.4691e-10 | -1.1815e-12 | 4.4038e-09 | -5.6045e-09 | -2.728e-10 | -1.4747e-10 | -1.0742e-10 | 2.4932e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.83658 | 0.96899 | 0.89716 | 0.83658 | 0.96899 | 0.89716 | -3.062 | -121.925 | 124.8308 | -3.062 | -121.925 | 124.8308
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0884e-09 | 2.7565e-09 | -5.787e-09 | 1.9176e-10 | -2.4753e-10 | -2.1549e-12 | 4.4294e-09 | -5.6177e-09 | -2.9635e-10 | -1.4726e-10 | -1.0863e-10 | 2.5033e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.83617 | 0.96914 | 0.89743 | 0.83617 | 0.96914 | 0.89743 | -3.0592 | -121.9465 | 124.8487 | -3.0592 | -121.9465 | 124.8487
Line17_5_19 | 0.0022479 | 0.00221 | 0.0022024 | 0.0022479 | 0.00221 | 0.0022024 | 0.00051912 | 0.00051037 | 0.00050861 | 0.00051913 | 0.00051038 | 0.00050862 | -0.00026527 | -0.00019873 | 0.00045643 | 0.00026532 | 0.00019877 | -0.00045639 | -0.00034359 | 0.00045294 | 3.5115e-06 | 0.00034365 | -0.0004529 | -3.4635e-06 | 124.6101 | 124.3644 | 124.408 | -55.3899 | -55.6356 | -55.592 |  | 0.83617 | 0.96914 | 0.89743 | 0.83631 | 0.96909 | 0.89734 | -3.0592 | -121.9465 | 124.8487 | -3.0602 | -121.9393 | 124.8428
Line1_1_3 | 0.0022392 | 0.0022015 | 0.002194 | 0.0022393 | 0.0022015 | 0.002194 | 0.00051713 | 0.00050842 | 0.00050667 | 0.00051714 | 0.00050842 | 0.00050668 | -0.00026542 | -0.0001963 | 0.00045475 | 0.00026547 | 0.00019635 | -0.00045471 | -0.00034128 | 0.00045196 | 1.9224e-06 | 0.00034134 | -0.00045192 | -1.8748e-06 | 124.8143 | 124.5697 | 124.6125 | -55.1857 | -55.4303 | -55.3875 |  | 0.83604 | 0.96919 | 0.89753 | 0.83617 | 0.96914 | 0.89743 | -3.0582 | -121.9538 | 124.8547 | -3.0592 | -121.9466 | 124.8488
Line2_1_4 | 0.0022507 | 0.0022127 | 0.0022051 | 0.0022507 | 0.0022127 | 0.0022051 | 0.00051977 | 0.000511 | 0.00050924 | 0.00051977 | 0.00051101 | 0.00050925 | -0.00026513 | -0.00019947 | 0.00045704 | 0.00026519 | 0.00019952 | -0.000457 | -0.00034428 | 0.00045332 | 4.1098e-06 | 0.00034434 | -0.00045327 | -4.0617e-06 | 124.5418 | 124.2957 | 124.3395 | -55.4582 | -55.7043 | -55.6605 |  | 0.83604 | 0.96919 | 0.89753 | 0.83617 | 0.96914 | 0.89743 | -3.0582 | -121.9538 | 124.8547 | -3.0592 | -121.9465 | 124.8487
Line3_1_5 | 0.0022478 | 0.0022099 | 0.0022023 | 0.0022479 | 0.00221 | 0.0022024 | 0.00051912 | 0.00051037 | 0.00050861 | 0.00051912 | 0.00051037 | 0.00050861 | -0.00026521 | -0.00019868 | 0.00045647 | 0.00026527 | 0.00019872 | -0.00045643 | -0.00034354 | 0.00045299 | 3.5593e-06 | 0.00034359 | -0.00045294 | -3.5113e-06 | 124.6101 | 124.3645 | 124.408 | -55.3899 | -55.6355 | -55.592 |  | 0.83604 | 0.96919 | 0.89753 | 0.83617 | 0.96914 | 0.89743 | -3.0582 | -121.9538 | 124.8547 | -3.0592 | -121.9465 | 124.8487
Line4_2_6 | 0.024628 | 0.0022094 | 0.0021849 | 0.024628 | 0.0022095 | 0.0021849 | 0.0056876 | 0.00051025 | 0.00050457 | 0.0056876 | 0.00051025 | 0.00050458 | 0.0034014 | -0.00020149 | 0.00045266 | -0.0033913 | 0.0002017 | -0.00045246 | 0.003302 | 0.00045144 | 1.5147e-06 | -0.0032916 | -0.00045117 | -1.2492e-06 | -47.214 | 124.0287 | 124.6295 | 132.786 | -55.9713 | -55.3705 |  | 0.83349 | 0.96887 | 0.89712 | 0.83094 | 0.96855 | 0.89671 | -3.0635 | -121.919 | 124.8212 | -3.0688 | -121.8843 | 124.7877
Line5_6_7 | 0.024628 | 0.0022095 | 0.0021849 | 0.024628 | 0.0022095 | 0.0021849 | 0.0056876 | 0.00051025 | 0.00050458 | 0.0056876 | 0.00051026 | 0.00050459 | 0.0033913 | -0.0002017 | 0.00045246 | -0.0033812 | 0.00020191 | -0.00045226 | 0.0032916 | 0.00045117 | 1.2494e-06 | -0.0032812 | -0.00045091 | -9.8387e-07 | -47.214 | 124.0286 | 124.6295 | 132.786 | -55.9714 | -55.3705 |  | 0.83094 | 0.96855 | 0.89671 | 0.82839 | 0.96823 | 0.8963 | -3.0688 | -121.8843 | 124.7877 | -3.0742 | -121.8495 | 124.7541
Line6_7_8 | 0.026967 | 0 | 0 | 0.026967 | 0 | 0 | 0.0062278 | 0 | 0 | 0.0062278 | 0 | 0 | 0.0036477 | 8.6521e-09 | -1.7685e-08 | -0.0036361 | -6.0274e-09 | 1.18e-08 | 0.0036482 | -1.7073e-08 | -1.0752e-09 | -0.0036361 | 1.1281e-08 | 9.6251e-10 | -48.078 | 0 | 0 | 131.922 | 0 | 0 |  | 0.82839 | 0.96823 | 0.8963 | 0.82569 | 0.96796 | 0.89598 | -3.0742 | -121.8495 | 124.7541 | -3.078 | -121.8218 | 124.7264
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0248e-09 | 2.8923e-09 | -5.8985e-09 | 2.2105e-10 | -2.4283e-10 | 3.1667e-12 | 4.5043e-09 | -5.6915e-09 | -3.5944e-10 | -1.4631e-10 | -1.0155e-10 | 2.4363e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82569 | 0.96796 | 0.89598 | 0.82569 | 0.96796 | 0.89598 | -3.078 | -121.8218 | 124.7264 | -3.078 | -121.8218 | 124.7264
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0248e-09 | 2.8923e-09 | -5.8985e-09 | 2.2105e-10 | -2.4283e-10 | 3.1667e-12 | 4.5043e-09 | -5.6915e-09 | -3.5944e-10 | -1.4631e-10 | -1.0155e-10 | 2.4363e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82569 | 0.96796 | 0.89598 | 0.82569 | 0.96796 | 0.89598 | -3.078 | -121.8218 | 124.7264 | -3.078 | -121.8218 | 124.7264
Line9_3_11 | 0.0022393 | 0.0022015 | 0.002194 | 0.0022393 | 0.0022016 | 0.002194 | 0.00051714 | 0.00050842 | 0.00050668 | 0.00051714 | 0.00050843 | 0.00050668 | -0.00026547 | -0.00019635 | 0.00045471 | 0.00026552 | 0.0001964 | -0.00045467 | -0.00034134 | 0.00045192 | 1.875e-06 | 0.00034139 | -0.00045188 | -1.8274e-06 | 124.8142 | 124.5697 | 124.6125 | -55.1858 | -55.4303 | -55.3875 |  | 0.83617 | 0.96914 | 0.89743 | 0.83631 | 0.96909 | 0.89734 | -3.0592 | -121.9466 | 124.8488 | -3.0601 | -121.9394 | 124.8428

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.095872 | 2.0723 | 2.2779 | 0.095872 | 2.0723 | 2.2779 | 0.022141 | 0.47859 | 0.52606 | 0.022141 | 0.47859 | 0.52606 | -0.023451 | 0.12519 | 0.26646 | 0.022938 | -0.098985 | -0.20507 | 0.013362 | 0.37075 | 0.38477 | -0.012693 | -0.28526 | -0.29675 | -147.8904 | 172.038 | 52.2977 | 32.1096 | -7.962 | -127.7023 |  | 1.2191 | 0.81765 | 0.88968 | 1.1841 | 0.63091 | 0.68569 | 2.4363 | -116.6196 | 107.5937 | 3.1508 | -117.0989 | 107.652
Line10_11_12 | 0.081269 | 0.33637 | 0.32517 | 0.081269 | 0.33637 | 0.32517 | 0.018768 | 0.077681 | 0.075095 | 0.018768 | 0.077681 | 0.075095 | 0.014752 | 0.012535 | -0.060203 | -0.014825 | -0.012059 | 0.061375 | 0.017616 | -0.065675 | -0.036107 | -0.017618 | 0.067479 | 0.037456 | -47.8936 | -38.8785 | -102.4085 | 132.1063 | 141.1215 | 77.5915 |  | 1.2242 | 0.8607 | 0.93482 | 1.2268 | 0.88242 | 0.95748 | 2.1636 | -118.0732 | 108.5446 | 2.0281 | -118.7466 | 108.9863
Line11_12_13 | 0.081269 | 0.33637 | 0.32517 | 0.081269 | 0.33637 | 0.32517 | 0.018768 | 0.077681 | 0.075095 | 0.018768 | 0.077682 | 0.075095 | 0.014825 | 0.012059 | -0.061375 | -0.014897 | -0.011583 | 0.062548 | 0.017618 | -0.067479 | -0.037456 | -0.017621 | 0.069282 | 0.038806 | -47.8937 | -38.8785 | -102.4085 | 132.1063 | 141.1215 | 77.5915 |  | 1.2268 | 0.88242 | 0.95748 | 1.2294 | 0.90425 | 0.9802 | 2.0281 | -118.7466 | 108.9863 | 1.8932 | -119.3876 | 109.4076
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4246e-08 | -2.5179e-08 | 3.985e-08 | 8.6861e-09 | 1.7269e-08 | -2.638e-08 | -4.8354e-08 | 2.8661e-08 | 8.8802e-10 | 3.2392e-08 | -1.907e-08 | -1.2857e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2294 | 0.90425 | 0.9802 | 1.2294 | 0.90425 | 0.9802 | 1.8932 | -119.3876 | 109.4076 | 1.8932 | -119.3876 | 109.4076
Line13_13_14 | 0.081269 | 0.33637 | 0.32517 | 0.081269 | 0.33637 | 0.32517 | 0.018768 | 0.077682 | 0.075095 | 0.018768 | 0.077682 | 0.075095 | 0.014898 | 0.011583 | -0.062548 | -0.01497 | -0.011107 | 0.06372 | 0.017621 | -0.069282 | -0.038806 | -0.017623 | 0.071086 | 0.040155 | -47.8937 | -38.8785 | -102.4085 | 132.1062 | 141.1214 | 77.5916 |  | 1.2294 | 0.90425 | 0.9802 | 1.232 | 0.9262 | 1.003 | 1.8932 | -119.3876 | 109.4076 | 1.7588 | -119.9983 | 109.8098
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.4975e-09 | -1.6786e-08 | 2.6567e-08 | 3.9373e-09 | 8.876e-09 | -1.3097e-08 | -3.2236e-08 | 1.9107e-08 | 5.9201e-10 | 1.6274e-08 | -9.5164e-09 | -9.897e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2294 | 0.90425 | 0.9802 | 1.2294 | 0.90425 | 0.9802 | 1.8932 | -119.3876 | 109.4076 | 1.8932 | -119.3876 | 109.4076
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7487e-09 | -8.3929e-09 | 1.3283e-08 | -8.1141e-10 | 4.8303e-10 | 1.8656e-10 | -1.6118e-08 | 9.5536e-09 | 2.9601e-10 | 1.5637e-10 | 3.7208e-11 | -6.937e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2294 | 0.90425 | 0.9802 | 1.2294 | 0.90425 | 0.9802 | 1.8932 | -119.3876 | 109.4076 | 1.8932 | -119.3876 | 109.4076
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4306e-09 | -1.0113e-08 | 1.4324e-08 | -7.8065e-10 | 6.3424e-10 | 3.6559e-10 | -1.9034e-08 | 9.4664e-09 | 8.2007e-10 | 1.9027e-10 | 1.362e-10 | -7.2748e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2232 | 0.84417 | 0.91909 | 1.2232 | 0.84417 | 0.91909 | 2.3156 | -117.5981 | 108.1359 | 2.3156 | -117.5981 | 108.1359
Line17_5_19 | 0.085136 | 0.39274 | 0.38962 | 0.085136 | 0.39274 | 0.38962 | 0.019661 | 0.090699 | 0.089978 | 0.019661 | 0.090699 | 0.089978 | 0.012496 | 0.017252 | -0.069133 | -0.012578 | -0.016621 | 0.070795 | 0.020537 | -0.07446 | -0.045043 | -0.02057 | 0.076948 | 0.047008 | -56.3721 | -40.5736 | -104.9629 | 123.6279 | 139.4264 | 75.0371 |  | 1.2227 | 0.8427 | 0.91703 | 1.2263 | 0.86795 | 0.94446 | 2.3095 | -117.5286 | 108.123 | 2.1833 | -118.3849 | 108.6217
Line1_1_3 | 0.081269 | 0.33637 | 0.32517 | 0.081269 | 0.33637 | 0.32517 | 0.018768 | 0.077681 | 0.075095 | 0.018768 | 0.077681 | 0.075095 | 0.014606 | 0.013486 | -0.057858 | -0.014679 | -0.01301 | 0.059031 | 0.017611 | -0.062068 | -0.033407 | -0.017614 | 0.063872 | 0.034757 | -47.8936 | -38.8785 | -102.4085 | 132.1064 | 141.1215 | 77.5915 |  | 1.2191 | 0.81765 | 0.88968 | 1.2216 | 0.83911 | 0.91222 | 2.4363 | -116.6196 | 107.5937 | 2.2997 | -117.365 | 108.0809
Line2_1_4 | 0.085919 | 0.41567 | 0.41675 | 0.085919 | 0.41567 | 0.41675 | 0.019842 | 0.095995 | 0.096245 | 0.019842 | 0.095995 | 0.096245 | 0.01109 | 0.019816 | -0.071315 | -0.011173 | -0.019117 | 0.073205 | 0.021497 | -0.075948 | -0.047394 | -0.021546 | 0.07875 | 0.049656 | -60.2758 | -41.2429 | -106.0134 | 119.7242 | 138.7571 | 73.9866 |  | 1.2191 | 0.81765 | 0.88968 | 1.2232 | 0.84417 | 0.91909 | 2.4363 | -116.6196 | 107.5937 | 2.3156 | -117.5981 | 108.1359
Line3_1_5 | 0.085136 | 0.39274 | 0.38962 | 0.085136 | 0.39274 | 0.38962 | 0.019661 | 0.090699 | 0.089978 | 0.019661 | 0.090699 | 0.089978 | 0.012413 | 0.017883 | -0.067472 | -0.012496 | -0.017252 | 0.069133 | 0.020503 | -0.071971 | -0.043078 | -0.020537 | 0.07446 | 0.045043 | -56.372 | -40.5736 | -104.9629 | 123.628 | 139.4264 | 75.0371 |  | 1.2191 | 0.81765 | 0.88968 | 1.2227 | 0.8427 | 0.91703 | 2.4363 | -116.6196 | 107.5937 | 2.3095 | -117.5286 | 108.123
Line4_2_6 | 0.095872 | 2.0723 | 2.2779 | 0.095872 | 2.0723 | 2.2779 | 0.022141 | 0.47859 | 0.52606 | 0.022141 | 0.47859 | 0.52606 | -0.022938 | 0.098985 | 0.20507 | 0.022426 | -0.072784 | -0.14367 | 0.012693 | 0.28526 | 0.29675 | -0.012025 | -0.19976 | -0.20874 | -147.8904 | 172.038 | 52.2977 | 32.1097 | -7.962 | -127.7023 |  | 1.1841 | 0.63091 | 0.68569 | 1.1493 | 0.44425 | 0.4817 | 3.1508 | -117.0989 | 107.652 | 3.9087 | -117.9811 | 107.7597
Line5_6_7 | 0.095872 | 2.0723 | 2.2779 | 0.095872 | 2.0723 | 2.2779 | 0.022141 | 0.47859 | 0.52606 | 0.022141 | 0.47859 | 0.52606 | -0.022426 | 0.072784 | 0.14367 | 0.021913 | -0.046582 | -0.082268 | 0.012025 | 0.19976 | 0.20874 | -0.011357 | -0.11427 | -0.12073 | -147.8903 | 172.038 | 52.2977 | 32.1097 | -7.962 | -127.7023 |  | 1.1493 | 0.44425 | 0.4817 | 1.1147 | 0.25784 | 0.27771 | 3.9087 | -117.9811 | 107.7597 | 4.7137 | -120.1402 | 108.0257
Line6_7_8 | 0 | 2.9001 | 3.1801 | 0 | 2.9001 | 3.1801 | 0 | 0.66976 | 0.73442 | 0 | 0.66976 | 0.73442 | -1.8646e-09 | 0.047455 | 0.11855 | -1.9696e-10 | 3.5895e-14 | 4.0719e-15 | -9.7942e-08 | 0.16605 | 0.16596 | 6.4169e-08 | 4.5513e-15 | 1.4858e-15 | 0 | 165.8093 | 53.5645 | 0 | -14.1907 | -126.4355 |  | 1.1147 | 0.25784 | 0.27771 | 1.062 | 0 | 0 | 4.7137 | -120.1402 | 108.0257 | 5.5049 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5654e-11 | -2.6454e-22 | -1.4674e-22 | -6.5654e-11 | -1.1552e-19 | -5.871e-18 | -3.1889e-08 | -1.7558e-21 | 4.8818e-23 | 3.9224e-10 | 1.7218e-17 | -2.7782e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.062 | 0 | 0 | 1.062 | 0 | 0 | 5.5049 | 0 | 0 | 5.5049 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5654e-11 | -2.6454e-22 | -1.4674e-22 | -6.5654e-11 | -1.1552e-19 | -5.871e-18 | -3.1889e-08 | -1.7558e-21 | 4.8818e-23 | 3.9224e-10 | 1.7218e-17 | -2.7782e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.062 | 0 | 0 | 1.062 | 0 | 0 | 5.5049 | 0 | 0 | 5.5049 | 0 | 0
Line9_3_11 | 0.081269 | 0.33637 | 0.32517 | 0.081269 | 0.33637 | 0.32517 | 0.018768 | 0.077681 | 0.075095 | 0.018768 | 0.077681 | 0.075095 | 0.014679 | 0.01301 | -0.059031 | -0.014752 | -0.012535 | 0.060203 | 0.017614 | -0.063872 | -0.034757 | -0.017616 | 0.065675 | 0.036107 | -47.8936 | -38.8785 | -102.4085 | 132.1064 | 141.1215 | 77.5915 |  | 1.2216 | 0.83911 | 0.91222 | 1.2242 | 0.8607 | 0.93482 | 2.2997 | -117.365 | 108.0809 | 2.1636 | -118.0732 | 108.5446

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.098134 | 2.1528 | 2.3704 | 0.098134 | 2.1528 | 2.3704 | 0.022663 | 0.49718 | 0.54743 | 0.022663 | 0.49718 | 0.54743 | -0.024633 | 0.13506 | 0.28719 | 0.024116 | -0.10663 | -0.22078 | 0.015329 | 0.39958 | 0.41634 | -0.014597 | -0.30718 | -0.32084 | -145.6432 | 172.1207 | 51.8523 | 34.3569 | -7.8793 | -128.1477 |  | 1.2802 | 0.84837 | 0.92393 | 1.2439 | 0.65401 | 0.71145 | 2.4637 | -116.555 | 107.2548 | 3.1713 | -117.023 | 107.3191
Line10_11_12 | 0.084914 | 0.34606 | 0.33692 | 0.084914 | 0.34606 | 0.33692 | 0.01961 | 0.079919 | 0.077807 | 0.01961 | 0.079919 | 0.077807 | 0.015415 | 0.013609 | -0.064869 | -0.015488 | -0.013112 | 0.066123 | 0.01994 | -0.070031 | -0.038664 | -0.019946 | 0.071941 | 0.040113 | -50.0815 | -38.9917 | -102.5808 | 129.9185 | 141.0083 | 77.4192 |  | 1.2852 | 0.89267 | 0.97057 | 1.2878 | 0.91501 | 0.99398 | 2.2127 | -117.9949 | 108.2154 | 2.088 | -118.6623 | 108.6619
Line11_12_13 | 0.084914 | 0.34606 | 0.33692 | 0.084914 | 0.34606 | 0.33692 | 0.01961 | 0.079919 | 0.077807 | 0.01961 | 0.079919 | 0.077807 | 0.015488 | 0.013112 | -0.066123 | -0.015562 | -0.012615 | 0.067377 | 0.019946 | -0.071941 | -0.040113 | -0.019951 | 0.073852 | 0.041562 | -50.0815 | -38.9917 | -102.5808 | 129.9185 | 141.0083 | 77.4193 |  | 1.2878 | 0.91501 | 0.99398 | 1.2903 | 0.93747 | 1.0174 | 2.088 | -118.6623 | 108.6619 | 1.9637 | -119.2979 | 109.0878
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5773e-08 | -2.8557e-08 | 4.4664e-08 | 9.6119e-09 | 1.9597e-08 | -2.9542e-08 | -5.5041e-08 | 3.1891e-08 | 1.0569e-09 | 3.6872e-08 | -2.1214e-08 | -1.4815e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2903 | 0.93747 | 1.0174 | 1.2903 | 0.93747 | 1.0174 | 1.9637 | -119.2979 | 109.0878 | 1.9637 | -119.2979 | 109.0878
Line13_13_14 | 0.084914 | 0.34606 | 0.33692 | 0.084914 | 0.34606 | 0.33692 | 0.01961 | 0.079919 | 0.077807 | 0.01961 | 0.079919 | 0.077807 | 0.015562 | 0.012616 | -0.067377 | -0.015636 | -0.012119 | 0.068631 | 0.019951 | -0.073852 | -0.041562 | -0.019957 | 0.075762 | 0.043011 | -50.0816 | -38.9917 | -102.5807 | 129.9184 | 141.0083 | 77.4193 |  | 1.2903 | 0.93747 | 1.0174 | 1.2928 | 0.96004 | 1.041 | 1.9637 | -119.2979 | 109.0878 | 1.84 | -119.9036 | 109.4944
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0515e-08 | -1.9038e-08 | 2.9776e-08 | 4.3542e-09 | 1.0078e-08 | -1.4654e-08 | -3.6694e-08 | 2.1261e-08 | 7.0462e-10 | 1.8525e-08 | -1.0584e-08 | -1.1292e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2903 | 0.93747 | 1.0174 | 1.2903 | 0.93747 | 1.0174 | 1.9637 | -119.2979 | 109.0878 | 1.9637 | -119.2979 | 109.0878
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2577e-09 | -9.5191e-09 | 1.4888e-08 | -9.0341e-10 | 5.584e-10 | 2.3377e-10 | -1.8347e-08 | 1.063e-08 | 3.5231e-10 | 1.7833e-10 | 4.6334e-11 | -7.7685e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2903 | 0.93747 | 1.0174 | 1.2903 | 0.93747 | 1.0174 | 1.9637 | -119.2979 | 109.0878 | 1.9637 | -119.2979 | 109.0878
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8808e-09 | -1.136e-08 | 1.5972e-08 | -8.7189e-10 | 7.1752e-10 | 4.2381e-10 | -2.1521e-08 | 1.0482e-08 | 9.0957e-10 | 2.1286e-10 | 1.531e-10 | -8.1312e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.2842 | 0.87543 | 0.954 | 1.2842 | 0.87543 | 0.954 | 2.3552 | -117.5148 | 107.8003 | 2.3552 | -117.5148 | 107.8003
Line17_5_19 | 0.089188 | 0.40161 | 0.40083 | 0.089188 | 0.40161 | 0.40083 | 0.020597 | 0.092749 | 0.092569 | 0.020597 | 0.092749 | 0.092569 | 0.012922 | 0.0185 | -0.07403 | -0.013004 | -0.017849 | 0.075783 | 0.023069 | -0.078923 | -0.047806 | -0.023106 | 0.081526 | 0.049885 | -58.3956 | -40.6418 | -105.0654 | 121.6044 | 139.3582 | 74.9346 |  | 1.2837 | 0.87399 | 0.95198 | 1.2873 | 0.89981 | 0.98011 | 2.3488 | -117.4491 | 107.7878 | 2.2346 | -118.2922 | 108.2902
Line1_1_3 | 0.084913 | 0.34606 | 0.33692 | 0.084914 | 0.34606 | 0.33692 | 0.01961 | 0.079919 | 0.077807 | 0.01961 | 0.079919 | 0.077807 | 0.015267 | 0.014602 | -0.06236 | -0.015341 | -0.014105 | 0.063615 | 0.019929 | -0.06621 | -0.035766 | -0.019934 | 0.06812 | 0.037215 | -50.0815 | -38.9917 | -102.5808 | 129.9185 | 141.0083 | 77.4192 |  | 1.2802 | 0.84837 | 0.92393 | 1.2827 | 0.87045 | 0.94722 | 2.4637 | -116.555 | 107.2548 | 2.3379 | -117.2932 | 107.747
Line2_1_4 | 0.090204 | 0.42404 | 0.42749 | 0.090204 | 0.42404 | 0.42749 | 0.020832 | 0.097927 | 0.098726 | 0.020832 | 0.097927 | 0.098726 | 0.011429 | 0.021129 | -0.076209 | -0.011511 | -0.020411 | 0.078193 | 0.024096 | -0.080347 | -0.050124 | -0.02415 | 0.083263 | 0.052502 | -62.1609 | -41.2889 | -106.0788 | 117.8391 | 138.7111 | 73.9212 |  | 1.2802 | 0.84837 | 0.92393 | 1.2842 | 0.87543 | 0.954 | 2.4637 | -116.555 | 107.2548 | 2.3552 | -117.5148 | 107.8003
Line3_1_5 | 0.089188 | 0.40161 | 0.40083 | 0.089188 | 0.40161 | 0.40083 | 0.020597 | 0.092749 | 0.092569 | 0.020597 | 0.092749 | 0.092569 | 0.01284 | 0.019151 | -0.072277 | -0.012922 | -0.0185 | 0.07403 | 0.023031 | -0.076319 | -0.045727 | -0.023069 | 0.078923 | 0.047806 | -58.3956 | -40.6418 | -105.0654 | 121.6044 | 139.3582 | 74.9346 |  | 1.2802 | 0.84837 | 0.92393 | 1.2837 | 0.87399 | 0.95198 | 2.4637 | -116.555 | 107.2548 | 2.3488 | -117.4491 | 107.7878
Line4_2_6 | 0.098134 | 2.1528 | 2.3704 | 0.098135 | 2.1528 | 2.3704 | 0.022663 | 0.49718 | 0.54743 | 0.022663 | 0.49718 | 0.54743 | -0.024116 | 0.10663 | 0.22078 | 0.023599 | -0.078201 | -0.15438 | 0.014597 | 0.30718 | 0.32084 | -0.013865 | -0.21477 | -0.22534 | -145.6432 | 172.1207 | 51.8523 | 34.3569 | -7.8793 | -128.1477 |  | 1.2439 | 0.65401 | 0.71145 | 1.2077 | 0.45972 | 0.49897 | 3.1713 | -117.023 | 107.3191 | 3.9214 | -117.8866 | 107.4382
Line5_6_7 | 0.098135 | 2.1528 | 2.3704 | 0.098135 | 2.1528 | 2.3704 | 0.022663 | 0.49718 | 0.54743 | 0.022663 | 0.49718 | 0.54743 | -0.023599 | 0.078201 | 0.15438 | 0.023082 | -0.049769 | -0.087971 | 0.013865 | 0.21477 | 0.22534 | -0.013133 | -0.12236 | -0.12984 | -145.6431 | 172.1207 | 51.8523 | 34.357 | -7.8793 | -128.1477 |  | 1.2077 | 0.45972 | 0.49897 | 1.1718 | 0.26569 | 0.2865 | 3.9214 | -117.8866 | 107.4382 | 4.7177 | -120.0129 | 107.7339
Line6_7_8 | 0 | 2.9833 | 3.277 | 0 | 2.9833 | 3.277 | 0 | 0.68897 | 0.75679 | 0 | 0.68897 | 0.75679 | -1.96e-09 | 0.050424 | 0.12584 | -2.8256e-10 | 6.7268e-14 | 3.3724e-14 | -1.0845e-07 | 0.17597 | 0.17656 | 7.1095e-08 | -4.1705e-15 | -1.2971e-14 | 0 | 165.9765 | 53.2128 | 0 | -14.0235 | -126.7872 |  | 1.1718 | 0.26569 | 0.2865 | 1.1179 | 0 | 0 | 4.7177 | -120.0129 | 107.7339 | 5.4966 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4187e-11 | -1.1116e-21 | -6.619e-22 | -9.4187e-11 | -1.4013e-19 | -6.4903e-18 | -3.5331e-08 | -3.195e-21 | 1.1394e-21 | 4.3189e-10 | 1.8959e-17 | -3.0914e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1179 | 0 | 0 | 1.1179 | 0 | 0 | 5.4966 | 0 | 0 | 5.4966 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4187e-11 | -1.1116e-21 | -6.619e-22 | -9.4186e-11 | -1.4012e-19 | -6.4903e-18 | -3.5331e-08 | -3.195e-21 | 1.1394e-21 | 4.3189e-10 | 1.8959e-17 | -3.0914e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1179 | 0 | 0 | 1.1179 | 0 | 0 | 5.4966 | 0 | 0 | 5.4966 | 0 | 0
Line9_3_11 | 0.084914 | 0.34606 | 0.33692 | 0.084914 | 0.34606 | 0.33692 | 0.01961 | 0.079919 | 0.077807 | 0.01961 | 0.079919 | 0.077807 | 0.015341 | 0.014105 | -0.063615 | -0.015415 | -0.013609 | 0.064869 | 0.019934 | -0.06812 | -0.037215 | -0.01994 | 0.070031 | 0.038664 | -50.0815 | -38.9917 | -102.5808 | 129.9185 | 141.0083 | 77.4192 |  | 1.2827 | 0.87045 | 0.94722 | 1.2852 | 0.89267 | 0.97057 | 2.3379 | -117.2932 | 107.747 | 2.2127 | -117.9949 | 108.2154

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1104 | 0.088359 | 0.086431 | 0.1104 | 0.088359 | 0.086431 | 0.025496 | 0.020406 | 0.01996 | 0.025496 | 0.020406 | 0.01996 | -0.011074 | -0.0057937 | -0.0064029 | 0.011195 | 0.0058779 | 0.0064708 | -0.02568 | -0.021535 | -0.020888 | 0.025914 | 0.021696 | 0.02104 | 113.4824 | -14.9101 | -133.0111 | -66.5176 | 165.0899 | 46.9889 |  | 1.0969 | 1.0929 | 1.0945 | 1.1072 | 1.1015 | 1.1028 | 0.15557 | -119.9684 | 119.9466 | 0.11697 | -120.0691 | 119.894
Line10_11_12 | 0.099723 | 0.10358 | 0.10116 | 0.099723 | 0.10358 | 0.10116 | 0.02303 | 0.023921 | 0.023362 | 0.02303 | 0.023921 | 0.023362 | -0.00052992 | -0.0011559 | -0.0016942 | 0.00062832 | 0.0012615 | 0.0017991 | -0.025662 | -0.02655 | -0.025936 | 0.025863 | 0.026763 | 0.02614 | 90.9111 | -27.898 | -146.7255 | -89.0889 | 152.102 | 33.2745 |  | 1.1145 | 1.111 | 1.1125 | 1.1233 | 1.12 | 1.1216 | -0.27188 | -120.3907 | 119.5371 | -0.48057 | -120.5968 | 119.3374
Line11_12_13 | 0.099723 | 0.10358 | 0.10116 | 0.099723 | 0.10358 | 0.10116 | 0.02303 | 0.023921 | 0.023362 | 0.02303 | 0.023921 | 0.023362 | -0.00062833 | -0.0012615 | -0.0017991 | 0.00072673 | 0.0013672 | 0.001904 | -0.025863 | -0.026763 | -0.02614 | 0.026064 | 0.026975 | 0.026345 | 90.9111 | -27.898 | -146.7254 | -89.0889 | 152.102 | 33.2746 |  | 1.1233 | 1.12 | 1.1216 | 1.1322 | 1.1291 | 1.1306 | -0.48057 | -120.5968 | 119.3374 | -0.68599 | -120.7995 | 119.1408
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3593e-10 | 9.0431e-10 | 1.4719e-09 | -7.6543e-10 | -9.3088e-10 | -1.3159e-09 | -1.6114e-10 | 6.7609e-10 | 1.7068e-11 | 5.5243e-11 | -5.1139e-10 | -7.6651e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1322 | 1.1291 | 1.1306 | 1.1322 | 1.1291 | 1.1306 | -0.68599 | -120.7995 | 119.1408 | -0.68599 | -120.7995 | 119.1408
Line13_13_14 | 0.099723 | 0.10358 | 0.10116 | 0.099723 | 0.10358 | 0.10116 | 0.02303 | 0.023921 | 0.023362 | 0.02303 | 0.023921 | 0.023362 | -0.00072673 | -0.0013672 | -0.001904 | 0.00082513 | 0.0014729 | 0.0020089 | -0.026064 | -0.026975 | -0.026345 | 0.026265 | 0.027188 | 0.026549 | 90.9111 | -27.898 | -146.7254 | -89.0889 | 152.102 | 33.2746 |  | 1.1322 | 1.1291 | 1.1306 | 1.141 | 1.1382 | 1.1396 | -0.68599 | -120.7995 | 119.1408 | -0.88824 | -120.999 | 118.9473
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2396e-10 | 6.0287e-10 | 9.8128e-10 | -5.5345e-10 | -6.2944e-10 | -8.2522e-10 | -1.0743e-10 | 4.5073e-10 | 1.1379e-11 | 1.5278e-12 | -2.8602e-10 | -7.0962e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1322 | 1.1291 | 1.1306 | 1.1322 | 1.1291 | 1.1306 | -0.68599 | -120.7995 | 119.1408 | -0.68599 | -120.7995 | 119.1408
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1198e-10 | 3.0144e-10 | 4.9064e-10 | -3.4147e-10 | -3.28e-10 | -3.3458e-10 | -5.3715e-11 | 2.2536e-10 | 5.6893e-12 | -5.2187e-11 | -6.0661e-11 | -6.5272e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1322 | 1.1291 | 1.1306 | 1.1322 | 1.1291 | 1.1306 | -0.68599 | -120.7995 | 119.1408 | -0.68599 | -120.7995 | 119.1408
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7526e-11 | 1.7766e-10 | 4.0905e-10 | -2.3635e-10 | -2.2051e-10 | -2.2738e-10 | -1.2184e-10 | 2.0225e-10 | -3.2463e-11 | -8.4018e-12 | -1.7435e-11 | -2.3164e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1082 | 1.1044 | 1.1061 | 1.1082 | 1.1044 | 1.1061 | -0.11283 | -120.2349 | 119.6883 | -0.11283 | -120.2349 | 119.6883
Line17_5_19 | 0.11895 | 0.1236 | 0.12095 | 0.11895 | 0.1236 | 0.12095 | 0.02747 | 0.028545 | 0.027932 | 0.02747 | 0.028545 | 0.027932 | -0.00076662 | -0.0014204 | -0.0020947 | 0.00090689 | 0.0015708 | 0.0022445 | -0.030412 | -0.031472 | -0.030802 | 0.030698 | 0.031775 | 0.031094 | 91.3467 | -27.6351 | -146.4061 | -88.6533 | 152.3649 | 33.5939 |  | 1.1074 | 1.1037 | 1.1053 | 1.118 | 1.1145 | 1.1161 | -0.097345 | -120.2192 | 119.7035 | -0.34548 | -120.4652 | 119.4652
Line1_1_3 | 0.099723 | 0.10358 | 0.10116 | 0.099723 | 0.10358 | 0.10116 | 0.02303 | 0.023921 | 0.023362 | 0.02303 | 0.023921 | 0.023362 | -0.00033311 | -0.00094446 | -0.0014844 | 0.00043152 | 0.0010502 | 0.0015893 | -0.025259 | -0.026125 | -0.025527 | 0.02546 | 0.026338 | 0.025732 | 90.9111 | -27.898 | -146.7255 | -89.0889 | 152.102 | 33.2745 |  | 1.0969 | 1.0929 | 1.0945 | 1.1057 | 1.1019 | 1.1035 | 0.15557 | -119.9684 | 119.9466 | -0.059858 | -120.1813 | 119.7402
Line2_1_4 | 0.12711 | 0.13209 | 0.12936 | 0.12711 | 0.13209 | 0.12936 | 0.029355 | 0.030505 | 0.029875 | 0.029355 | 0.030505 | 0.029875 | -0.00077444 | -0.0014245 | -0.002157 | 0.00093474 | 0.0015962 | 0.0023284 | -0.03219 | -0.033308 | -0.032628 | 0.032517 | 0.033654 | 0.032962 | 91.5337 | -27.5195 | -146.2711 | -88.4663 | 152.4805 | 33.7289 |  | 1.0969 | 1.0929 | 1.0945 | 1.1082 | 1.1044 | 1.1061 | 0.15557 | -119.9684 | 119.9466 | -0.11283 | -120.2349 | 119.6883
Line3_1_5 | 0.11895 | 0.1236 | 0.12095 | 0.11895 | 0.1236 | 0.12095 | 0.02747 | 0.028545 | 0.027932 | 0.02747 | 0.028545 | 0.027932 | -0.00062635 | -0.00127 | -0.0019449 | 0.00076662 | 0.0014204 | 0.0020947 | -0.030125 | -0.03117 | -0.03051 | 0.030412 | 0.031472 | 0.030802 | 91.3467 | -27.6351 | -146.4061 | -88.6533 | 152.3649 | 33.5939 |  | 1.0969 | 1.0929 | 1.0945 | 1.1074 | 1.1037 | 1.1053 | 0.15557 | -119.9684 | 119.9466 | -0.097345 | -120.2192 | 119.7035
Line4_2_6 | 0.1104 | 0.088359 | 0.086431 | 0.1104 | 0.088359 | 0.086431 | 0.025496 | 0.020406 | 0.01996 | 0.025496 | 0.020406 | 0.01996 | -0.011195 | -0.0058779 | -0.0064708 | 0.011317 | 0.0059621 | 0.0065386 | -0.025914 | -0.021696 | -0.02104 | 0.026148 | 0.021856 | 0.021193 | 113.4824 | -14.9101 | -133.0111 | -66.5176 | 165.0899 | 46.9889 |  | 1.1072 | 1.1015 | 1.1028 | 1.1175 | 1.1102 | 1.1111 | 0.11697 | -120.0691 | 119.894 | 0.07909 | -120.1683 | 119.8422
Line5_6_7 | 0.1104 | 0.088359 | 0.086431 | 0.1104 | 0.088359 | 0.086431 | 0.025496 | 0.020406 | 0.01996 | 0.025496 | 0.020406 | 0.01996 | -0.011317 | -0.0059621 | -0.0065386 | 0.011439 | 0.0060463 | 0.0066065 | -0.026148 | -0.021856 | -0.021193 | 0.026382 | 0.022017 | 0.021345 | 113.4824 | -14.9101 | -133.0111 | -66.5176 | 165.0899 | 46.9889 |  | 1.1175 | 1.1102 | 1.1111 | 1.1279 | 1.1189 | 1.1194 | 0.07909 | -120.1683 | 119.8422 | 0.041902 | -120.2659 | 119.7912
Line6_7_8 | 0 | 0.036449 | 0.036455 | 0 | 0.036449 | 0.036455 | 0 | 0.0084175 | 0.0084189 | 0 | 0.0084175 | 0.0084189 | 3.5837e-10 | 0.0066509 | 0.0066608 | -5.5246e-10 | -0.0066426 | -0.0066448 | -8.7063e-10 | 0.0066688 | 0.0066672 | 6.0027e-10 | -0.0066426 | -0.0066448 | 0 | -165.343 | 74.7636 | 0 | 14.657 | -105.2364 |  | 1.1279 | 1.1189 | 1.1194 | 1.1273 | 1.116 | 1.1162 | 0.041902 | -120.2659 | 119.7912 | 0.032601 | -120.343 | 119.7636
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1647e-10 | 1.1867e-10 | 6.2555e-10 | -3.1952e-10 | -2.702e-10 | -2.7097e-10 | -2.989e-10 | 3.4754e-10 | -1.1296e-11 | 2.4696e-12 | -2.5724e-11 | -1.773e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1273 | 1.116 | 1.1162 | 1.1273 | 1.116 | 1.1162 | 0.032601 | -120.343 | 119.7636 | 0.032601 | -120.343 | 119.7636
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1647e-10 | 1.1867e-10 | 6.2555e-10 | -3.1952e-10 | -2.702e-10 | -2.7097e-10 | -2.989e-10 | 3.4754e-10 | -1.1296e-11 | 2.4696e-12 | -2.5724e-11 | -1.773e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1273 | 1.116 | 1.1162 | 1.1273 | 1.116 | 1.1162 | 0.032601 | -120.343 | 119.7636 | 0.032601 | -120.343 | 119.7636
Line9_3_11 | 0.099723 | 0.10358 | 0.10116 | 0.099723 | 0.10358 | 0.10116 | 0.02303 | 0.023921 | 0.023362 | 0.02303 | 0.023921 | 0.023362 | -0.00043152 | -0.0010502 | -0.0015893 | 0.00052992 | 0.0011559 | 0.0016942 | -0.02546 | -0.026338 | -0.025732 | 0.025662 | 0.02655 | 0.025936 | 90.9111 | -27.898 | -146.7255 | -89.0889 | 152.102 | 33.2745 |  | 1.1057 | 1.1019 | 1.1035 | 1.1145 | 1.111 | 1.1125 | -0.059858 | -120.1813 | 119.7402 | -0.27188 | -120.3907 | 119.5371

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11108 | 0.087924 | 0.085866 | 0.11108 | 0.087924 | 0.085866 | 0.025653 | 0.020305 | 0.01983 | 0.025653 | 0.020305 | 0.01983 | -0.011584 | -0.0057679 | -0.0064417 | 0.011707 | 0.0058515 | 0.0065082 | -0.027115 | -0.022523 | -0.02181 | 0.027352 | 0.022682 | 0.02196 | 113.2923 | -15.6063 | -133.6045 | -66.7077 | 164.3937 | 46.3955 |  | 1.1494 | 1.145 | 1.1468 | 1.1598 | 1.1536 | 1.1551 | 0.15943 | -119.9705 | 119.9407 | 0.12028 | -120.072 | 119.8878
Line10_11_12 | 0.10075 | 0.10485 | 0.10231 | 0.10075 | 0.10485 | 0.10231 | 0.023267 | 0.024214 | 0.023627 | 0.023267 | 0.024214 | 0.023627 | -0.00057481 | -0.0012645 | -0.0018644 | 0.00067522 | 0.0013727 | 0.0019718 | -0.027153 | -0.028141 | -0.027463 | 0.027358 | 0.028359 | 0.027672 | 90.9607 | -27.8041 | -146.5691 | -89.0393 | 152.1959 | 33.4309 |  | 1.1672 | 1.1633 | 1.1651 | 1.1762 | 1.1725 | 1.1742 | -0.25204 | -120.377 | 119.5473 | -0.4531 | -120.5754 | 119.3552
Line11_12_13 | 0.10075 | 0.10485 | 0.10231 | 0.10075 | 0.10485 | 0.10231 | 0.023267 | 0.024214 | 0.023627 | 0.023267 | 0.024214 | 0.023627 | -0.00067522 | -0.0013727 | -0.0019718 | 0.00077562 | 0.0014809 | 0.0020792 | -0.027358 | -0.028359 | -0.027672 | 0.027564 | 0.028576 | 0.027881 | 90.9607 | -27.8041 | -146.5691 | -89.0393 | 152.1959 | 33.4309 |  | 1.1762 | 1.1725 | 1.1742 | 1.1851 | 1.1817 | 1.1833 | -0.4531 | -120.5754 | 119.3552 | -0.65112 | -120.7708 | 119.1661
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6215e-10 | 9.6894e-10 | 1.6293e-09 | -8.1162e-10 | -1.0005e-09 | -1.4483e-09 | -2.0692e-10 | 7.6417e-10 | 3.5685e-12 | 8.3627e-11 | -5.7356e-10 | -7.184e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1851 | 1.1817 | 1.1833 | 1.1851 | 1.1817 | 1.1833 | -0.65112 | -120.7708 | 119.1661 | -0.65112 | -120.7708 | 119.1661
Line13_13_14 | 0.10075 | 0.10485 | 0.10231 | 0.10075 | 0.10485 | 0.10231 | 0.023267 | 0.024214 | 0.023627 | 0.023267 | 0.024214 | 0.023627 | -0.00077562 | -0.0014809 | -0.0020792 | 0.00087602 | 0.0015891 | 0.0021866 | -0.027564 | -0.028576 | -0.027881 | 0.027769 | 0.028794 | 0.02809 | 90.9607 | -27.8041 | -146.569 | -89.0393 | 152.1959 | 33.431 |  | 1.1851 | 1.1817 | 1.1833 | 1.1941 | 1.1909 | 1.1925 | -0.65112 | -120.7708 | 119.1661 | -0.84618 | -120.9631 | 118.9799
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4144e-10 | 6.4596e-10 | 1.0862e-09 | -5.909e-10 | -6.7751e-10 | -9.0521e-10 | -1.3795e-10 | 5.0944e-10 | 2.379e-12 | 1.4654e-11 | -3.1884e-10 | -7.0651e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1851 | 1.1817 | 1.1833 | 1.1851 | 1.1817 | 1.1833 | -0.65112 | -120.7708 | 119.1661 | -0.65112 | -120.7708 | 119.1661
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2072e-10 | 3.2298e-10 | 5.4311e-10 | -3.7018e-10 | -3.5453e-10 | -3.6209e-10 | -6.8973e-11 | 2.5472e-10 | 1.1896e-12 | -5.4319e-11 | -6.4115e-11 | -6.9461e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1851 | 1.1817 | 1.1833 | 1.1851 | 1.1817 | 1.1833 | -0.65112 | -120.7708 | 119.1661 | -0.65112 | -120.7708 | 119.1661
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8849e-11 | 1.9035e-10 | 4.5752e-10 | -2.5847e-10 | -2.4018e-10 | -2.4806e-10 | -1.4256e-10 | 2.3112e-10 | -3.8761e-11 | -7.894e-12 | -1.8298e-11 | -2.4887e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1607 | 1.1566 | 1.1584 | 1.1607 | 1.1566 | 1.1584 | -0.096611 | -120.2247 | 119.6948 | -0.096611 | -120.2247 | 119.6948
Line17_5_19 | 0.11939 | 0.1243 | 0.12153 | 0.11939 | 0.1243 | 0.12153 | 0.027573 | 0.028707 | 0.028066 | 0.027573 | 0.028707 | 0.028066 | -0.00082264 | -0.0015405 | -0.0022852 | 0.00096391 | 0.0016924 | 0.0024367 | -0.031975 | -0.033146 | -0.03241 | 0.032263 | 0.033452 | 0.032704 | 91.3913 | -27.5495 | -146.258 | -88.6087 | 152.4505 | 33.742 |  | 1.16 | 1.1559 | 1.1577 | 1.1706 | 1.1668 | 1.1685 | -0.082453 | -120.2103 | 119.7087 | -0.31996 | -120.4457 | 119.481
Line1_1_3 | 0.10075 | 0.10485 | 0.10231 | 0.10075 | 0.10485 | 0.10231 | 0.023267 | 0.024214 | 0.023627 | 0.023267 | 0.024214 | 0.023627 | -0.00037401 | -0.0010481 | -0.0016496 | 0.00047441 | 0.0011563 | 0.001757 | -0.026742 | -0.027706 | -0.027045 | 0.026947 | 0.027924 | 0.027254 | 90.9607 | -27.8041 | -146.5691 | -89.0393 | 152.1959 | 33.4309 |  | 1.1494 | 1.145 | 1.1468 | 1.1583 | 1.1542 | 1.1559 | 0.15943 | -119.9705 | 119.9407 | -0.047886 | -120.1753 | 119.7425
Line2_1_4 | 0.12724 | 0.13248 | 0.12963 | 0.12724 | 0.13248 | 0.12963 | 0.029384 | 0.030594 | 0.029936 | 0.029384 | 0.030594 | 0.029936 | -0.00083406 | -0.0015476 | -0.0023539 | 0.00099462 | 0.0017201 | 0.0025261 | -0.033765 | -0.034996 | -0.03425 | 0.034093 | 0.035344 | 0.034585 | 91.5745 | -27.4385 | -146.1278 | -88.4255 | 152.5615 | 33.8722 |  | 1.1494 | 1.145 | 1.1468 | 1.1607 | 1.1566 | 1.1584 | 0.15943 | -119.9705 | 119.9407 | -0.096611 | -120.2247 | 119.6948
Line3_1_5 | 0.11939 | 0.1243 | 0.12153 | 0.11939 | 0.1243 | 0.12153 | 0.027573 | 0.028707 | 0.028066 | 0.027573 | 0.028707 | 0.028066 | -0.00068137 | -0.0013885 | -0.0021338 | 0.00082264 | 0.0015405 | 0.0022852 | -0.031686 | -0.03284 | -0.032115 | 0.031975 | 0.033146 | 0.03241 | 91.3913 | -27.5495 | -146.258 | -88.6087 | 152.4505 | 33.742 |  | 1.1494 | 1.145 | 1.1468 | 1.16 | 1.1559 | 1.1577 | 0.15943 | -119.9705 | 119.9407 | -0.082453 | -120.2103 | 119.7087
Line4_2_6 | 0.11108 | 0.087924 | 0.085866 | 0.11108 | 0.087924 | 0.085866 | 0.025653 | 0.020305 | 0.01983 | 0.025653 | 0.020305 | 0.01983 | -0.011707 | -0.0058515 | -0.0065082 | 0.01183 | 0.0059352 | 0.0065748 | -0.027352 | -0.022682 | -0.02196 | 0.027588 | 0.022842 | 0.022111 | 113.2923 | -15.6063 | -133.6045 | -66.7077 | 164.3937 | 46.3955 |  | 1.1598 | 1.1536 | 1.1551 | 1.1702 | 1.1623 | 1.1633 | 0.12028 | -120.072 | 119.8878 | 0.08183 | -120.1719 | 119.8356
Line5_6_7 | 0.11108 | 0.087924 | 0.085866 | 0.11108 | 0.087924 | 0.085866 | 0.025653 | 0.020305 | 0.01983 | 0.025653 | 0.020305 | 0.01983 | -0.01183 | -0.0059352 | -0.0065748 | 0.011954 | 0.0060189 | 0.0066414 | -0.027588 | -0.022842 | -0.022111 | 0.027825 | 0.023001 | 0.022262 | 113.2923 | -15.6063 | -133.6045 | -66.7077 | 164.3937 | 46.3955 |  | 1.1702 | 1.1623 | 1.1633 | 1.1805 | 1.1709 | 1.1715 | 0.08183 | -120.1719 | 119.8356 | 0.044052 | -120.2703 | 119.7842
Line6_7_8 | 0 | 0.038143 | 0.038152 | 0 | 0.038143 | 0.038152 | 0 | 0.0088087 | 0.0088108 | 0 | 0.0088087 | 0.0088108 | 3.5762e-10 | 0.0072835 | 0.0072954 | -5.778e-10 | -0.0072744 | -0.0072778 | -9.8039e-10 | 0.0073032 | 0.0073024 | 6.7551e-10 | -0.0072744 | -0.0072778 | 0 | -165.3475 | 74.7566 | 0 | 14.6525 | -105.2434 |  | 1.1805 | 1.1709 | 1.1715 | 1.18 | 1.1679 | 1.1682 | 0.044052 | -120.2703 | 119.7842 | 0.034759 | -120.3475 | 119.7566
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1594e-10 | 1.2121e-10 | 6.9152e-10 | -3.4592e-10 | -2.9077e-10 | -2.9197e-10 | -3.3631e-10 | 3.9184e-10 | -1.4055e-11 | 2.8872e-12 | -2.8567e-11 | -2.0018e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.18 | 1.1679 | 1.1682 | 1.18 | 1.1679 | 1.1682 | 0.034759 | -120.3475 | 119.7566 | 0.034759 | -120.3475 | 119.7566
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1594e-10 | 1.2121e-10 | 6.9152e-10 | -3.4592e-10 | -2.9077e-10 | -2.9197e-10 | -3.3631e-10 | 3.9184e-10 | -1.4055e-11 | 2.8873e-12 | -2.8567e-11 | -2.0018e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.18 | 1.1679 | 1.1682 | 1.18 | 1.1679 | 1.1682 | 0.034759 | -120.3475 | 119.7566 | 0.034759 | -120.3475 | 119.7566
Line9_3_11 | 0.10075 | 0.10485 | 0.10231 | 0.10075 | 0.10485 | 0.10231 | 0.023267 | 0.024214 | 0.023627 | 0.023267 | 0.024214 | 0.023627 | -0.00047441 | -0.0011563 | -0.001757 | 0.00057481 | 0.0012645 | 0.0018644 | -0.026947 | -0.027924 | -0.027254 | 0.027153 | 0.028141 | 0.027463 | 90.9607 | -27.8041 | -146.5691 | -89.0393 | 152.1959 | 33.4309 |  | 1.1583 | 1.1542 | 1.1559 | 1.1672 | 1.1633 | 1.1651 | -0.047886 | -120.1753 | 119.7425 | -0.25204 | -120.377 | 119.5473

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.012567 | 1.4256 | 1.4852 | 0.012567 | 1.4256 | 1.4852 | 0.0029022 | 0.32923 | 0.343 | 0.0029023 | 0.32923 | 0.343 | -0.00049119 | 0.1553 | 0.17078 | 0.00049721 | -0.11659 | -0.12816 | 0.0040277 | 0.16536 | 0.17377 | -0.0040183 | -0.12399 | -0.13043 | -96.4312 | -145.1497 | 39.4611 | 83.5689 | 34.8503 | -140.5389 |  | 1.3981 | 0.68905 | 0.71033 | 1.3951 | 0.51696 | 0.53312 | 0.52186 | -98.3522 | 84.9593 | 0.62249 | -98.3868 | 84.9639
Line10_11_12 | 0.01305 | 0.011689 | 0.01456 | 0.01305 | 0.01169 | 0.01456 | 0.0030137 | 0.0026996 | 0.0033624 | 0.0030138 | 0.0026996 | 0.0033624 | -3.3111e-05 | 0.001745 | -0.0023931 | 3.4805e-05 | -0.0017441 | 0.0023956 | 0.00421 | -0.00064221 | 3.0573e-05 | -0.0042084 | 0.00064369 | -2.8415e-05 | -89.8823 | -78.2524 | -94.2036 | 90.1177 | 101.7475 | 85.7964 |  | 1.397 | 0.68878 | 0.71178 | 1.3964 | 0.68865 | 0.71251 | 0.56832 | -98.4576 | 85.0644 | 0.59157 | -98.5103 | 85.1169
Line11_12_13 | 0.01305 | 0.01169 | 0.01456 | 0.01305 | 0.01169 | 0.01456 | 0.0030138 | 0.0026996 | 0.0033624 | 0.0030138 | 0.0026996 | 0.0033625 | -3.4808e-05 | 0.0017441 | -0.0023956 | 3.6502e-05 | -0.0017432 | 0.0023981 | 0.0042084 | -0.00064369 | 2.8414e-05 | -0.0042068 | 0.00064518 | -2.6256e-05 | -89.8823 | -78.2526 | -94.2036 | 90.1177 | 101.7473 | 85.7965 |  | 1.3964 | 0.68865 | 0.71251 | 1.3959 | 0.68852 | 0.71323 | 0.59157 | -98.5103 | 85.1169 | 0.61484 | -98.563 | 85.1692
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3026e-09 | -7.829e-08 | 7.983e-08 | -4.4842e-09 | 5.2688e-08 | -5.3046e-08 | -1.5847e-07 | 1.1551e-08 | -5.2227e-09 | 1.057e-07 | -6.8243e-09 | 2.0628e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3959 | 0.68852 | 0.71323 | 1.3959 | 0.68852 | 0.71323 | 0.61484 | -98.563 | 85.1692 | 0.61484 | -98.563 | 85.1692
Line13_13_14 | 0.013051 | 0.01169 | 0.01456 | 0.013051 | 0.01169 | 0.014561 | 0.0030139 | 0.0026997 | 0.0033626 | 0.0030139 | 0.0026998 | 0.0033626 | -3.6507e-05 | 0.0017433 | -0.0023982 | 3.8202e-05 | -0.0017424 | 0.0024007 | 0.0042069 | -0.00064519 | 2.626e-05 | -0.0042053 | 0.00064668 | -2.4103e-05 | -89.8824 | -78.2532 | -94.2035 | 90.1177 | 101.7466 | 85.7966 |  | 1.3959 | 0.68852 | 0.71323 | 1.3953 | 0.68839 | 0.71396 | 0.61484 | -98.563 | 85.1692 | 0.63814 | -98.6158 | 85.2214
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2017e-09 | -5.2194e-08 | 5.322e-08 | -3.3833e-09 | 2.6591e-08 | -2.6436e-08 | -1.0565e-07 | 7.7008e-09 | -3.4818e-09 | 5.2875e-08 | -2.9739e-09 | 3.2189e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3959 | 0.68852 | 0.71323 | 1.3959 | 0.68852 | 0.71323 | 0.61484 | -98.563 | 85.1692 | 0.61484 | -98.563 | 85.1692
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1009e-09 | -2.6097e-08 | 2.661e-08 | -2.2825e-09 | 4.9421e-10 | 1.7408e-10 | -5.2823e-08 | 3.8504e-09 | -1.7409e-09 | 5.2177e-11 | 8.7654e-10 | -1.419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3959 | 0.68852 | 0.71323 | 1.3959 | 0.68852 | 0.71323 | 0.61484 | -98.563 | 85.1692 | 0.61484 | -98.563 | 85.1692
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2307e-09 | -2.6234e-08 | 2.663e-08 | -2.2935e-09 | 4.9108e-10 | 1.7532e-10 | -5.308e-08 | 3.7016e-09 | -1.7198e-09 | 4.6331e-11 | 8.8319e-10 | -1.4203e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3975 | 0.68891 | 0.71107 | 1.3975 | 0.68891 | 0.71107 | 0.54531 | -98.4051 | 85.0119 | 0.54531 | -98.4051 | 85.0119
Line17_5_19 | 0.013099 | 0.011733 | 0.014617 | 0.013099 | 0.011733 | 0.014618 | 0.0030251 | 0.0027095 | 0.0033757 | 0.0030251 | 0.0027096 | 0.0033758 | -4.7454e-05 | 0.0017545 | -0.0024002 | 4.9161e-05 | -0.0017536 | 0.0024028 | 0.0042274 | -0.00063711 | 2.4475e-05 | -0.0042258 | 0.00063861 | -2.23e-05 | -90.0979 | -78.4477 | -94.4039 | 89.9021 | 101.5522 | 85.5962 |  | 1.3975 | 0.68891 | 0.71106 | 1.397 | 0.68878 | 0.71179 | 0.54526 | -98.405 | 85.0119 | 0.56867 | -98.4579 | 85.0645
Line1_1_3 | 0.013049 | 0.011689 | 0.014559 | 0.01305 | 0.011689 | 0.014559 | 0.0030136 | 0.0026995 | 0.0033623 | 0.0030137 | 0.0026995 | 0.0033623 | -2.9719e-05 | 0.0017468 | -0.0023881 | 3.1413e-05 | -0.0017459 | 0.0023906 | 0.0042132 | -0.00063924 | 3.489e-05 | -0.0042116 | 0.00064072 | -3.2733e-05 | -89.8823 | -78.2521 | -94.2037 | 90.1177 | 101.7478 | 85.7964 |  | 1.3981 | 0.68905 | 0.71033 | 1.3975 | 0.68891 | 0.71106 | 0.52186 | -98.3522 | 84.9593 | 0.54508 | -98.4049 | 85.0119
Line2_1_4 | 0.013115 | 0.011747 | 0.014636 | 0.013115 | 0.011747 | 0.014636 | 0.0030288 | 0.0027128 | 0.0033801 | 0.0030289 | 0.0027128 | 0.0033801 | -5.1138e-05 | 0.0017583 | -0.0024009 | 5.285e-05 | -0.0017574 | 0.0024034 | 0.0042342 | -0.00063439 | 2.3872e-05 | -0.0042326 | 0.00063589 | -2.1691e-05 | -90.1701 | -78.5127 | -94.4711 | 89.8299 | 101.4872 | 85.529 |  | 1.3981 | 0.68905 | 0.71033 | 1.3975 | 0.68891 | 0.71107 | 0.52186 | -98.3522 | 84.9593 | 0.54531 | -98.4051 | 85.0119
Line3_1_5 | 0.013099 | 0.011732 | 0.014617 | 0.013099 | 0.011733 | 0.014617 | 0.0030251 | 0.0027095 | 0.0033757 | 0.0030251 | 0.0027095 | 0.0033757 | -4.5745e-05 | 0.0017554 | -0.0023977 | 4.7452e-05 | -0.0017545 | 0.0024002 | 0.004229 | -0.00063562 | 2.6651e-05 | -0.0042274 | 0.00063712 | -2.4476e-05 | -90.0979 | -78.4475 | -94.4039 | 89.9021 | 101.5523 | 85.5962 |  | 1.3981 | 0.68905 | 0.71033 | 1.3975 | 0.68891 | 0.71106 | 0.52186 | -98.3522 | 84.9593 | 0.54526 | -98.405 | 85.0119
Line4_2_6 | 0.012567 | 1.4256 | 1.4852 | 0.012567 | 1.4256 | 1.4852 | 0.0029023 | 0.32923 | 0.343 | 0.0029023 | 0.32923 | 0.343 | -0.00049721 | 0.11659 | 0.12816 | 0.00050322 | -0.077878 | -0.085548 | 0.0040183 | 0.12399 | 0.13043 | -0.004009 | -0.082624 | -0.08709 | -96.4311 | -145.1497 | 39.4611 | 83.569 | 34.8503 | -140.5389 |  | 1.3951 | 0.51696 | 0.53312 | 1.3921 | 0.34487 | 0.35591 | 0.62249 | -98.3868 | 84.9639 | 0.72356 | -98.4561 | 84.973
Line5_6_7 | 0.012567 | 1.4256 | 1.4852 | 0.012568 | 1.4256 | 1.4852 | 0.0029023 | 0.32923 | 0.343 | 0.0029024 | 0.32923 | 0.343 | -0.00050323 | 0.077878 | 0.085548 | 0.00050924 | -0.039167 | -0.042933 | 0.004009 | 0.082624 | 0.08709 | -0.0039996 | -0.041254 | -0.043748 | -96.4311 | -145.1497 | 39.4611 | 83.569 | 34.8503 | -140.5389 |  | 1.3921 | 0.34487 | 0.35591 | 1.3892 | 0.17278 | 0.1787 | 0.72356 | -98.4561 | 84.973 | 0.82505 | -98.6632 | 85.0003
Line6_7_8 | 0 | 1.4279 | 1.5018 | 0 | 1.4279 | 1.5018 | 0 | 0.32976 | 0.34683 | 0 | 0.32976 | 0.34683 | 6.3518e-09 | 0.038768 | 0.043603 | -6.661e-09 | -2.0127e-14 | 2.5743e-14 | -1.6146e-07 | 0.041753 | 0.044049 | 1.0761e-07 | -1.124e-14 | 4.5992e-15 | 0 | -145.7866 | 39.7084 | 0 | 34.2134 | -140.2917 |  | 1.3892 | 0.17278 | 0.1787 | 1.3866 | 0 | 0 | 0.82505 | -98.6632 | 85.0003 | 0.9011 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2203e-09 | -2.644e-21 | -2.1121e-21 | -2.2203e-09 | 6.795e-18 | -1.1938e-17 | -5.3766e-08 | 1.2358e-21 | 1.6707e-21 | 7.5959e-11 | 2.1978e-17 | -2.0618e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3866 | 0 | 0 | 1.3866 | 0 | 0 | 0.9011 | 0 | 0 | 0.9011 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2203e-09 | -2.644e-21 | -2.1121e-21 | -2.2203e-09 | 6.795e-18 | -1.1938e-17 | -5.3766e-08 | 1.2358e-21 | 1.6707e-21 | 7.5959e-11 | 2.1978e-17 | -2.0618e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3866 | 0 | 0 | 1.3866 | 0 | 0 | 0.9011 | 0 | 0 | 0.9011 | 0 | 0
Line9_3_11 | 0.01305 | 0.011689 | 0.014559 | 0.01305 | 0.011689 | 0.01456 | 0.0030137 | 0.0026995 | 0.0033623 | 0.0030137 | 0.0026996 | 0.0033624 | -3.1415e-05 | 0.0017459 | -0.0023906 | 3.3109e-05 | -0.001745 | 0.0023931 | 0.0042116 | -0.00064072 | 3.2731e-05 | -0.00421 | 0.00064221 | -3.0574e-05 | -89.8823 | -78.2522 | -94.2037 | 90.1177 | 101.7476 | 85.7964 |  | 1.3975 | 0.68891 | 0.71106 | 1.397 | 0.68878 | 0.71178 | 0.54508 | -98.4049 | 85.0119 | 0.56832 | -98.4576 | 85.0644

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.011906 | 1.3506 | 1.4071 | 0.011906 | 1.3506 | 1.4071 | 0.0027495 | 0.3119 | 0.32495 | 0.0027495 | 0.3119 | 0.32495 | -0.00044085 | 0.13938 | 0.15328 | 0.00044625 | -0.10464 | -0.11503 | 0.0036149 | 0.14841 | 0.15596 | -0.0036065 | -0.11128 | -0.11706 | -96.4312 | -145.1497 | 39.4611 | 83.5689 | 34.8503 | -140.5389 |  | 1.3245 | 0.65278 | 0.67295 | 1.3217 | 0.48975 | 0.50507 | 0.52186 | -98.3522 | 84.9593 | 0.62249 | -98.3868 | 84.9639
Line10_11_12 | 0.012363 | 0.011074 | 0.013793 | 0.012363 | 0.011074 | 0.013793 | 0.0028551 | 0.0025575 | 0.0031854 | 0.0028551 | 0.0025575 | 0.0031855 | -2.9718e-05 | 0.0015661 | -0.0021478 | 3.1238e-05 | -0.0015653 | 0.0021501 | 0.0037785 | -0.00057639 | 2.7439e-05 | -0.003777 | 0.00057772 | -2.5503e-05 | -89.8823 | -78.2524 | -94.2036 | 90.1177 | 101.7475 | 85.7964 |  | 1.3235 | 0.65253 | 0.67432 | 1.3229 | 0.6524 | 0.67501 | 0.56832 | -98.4576 | 85.0644 | 0.59157 | -98.5103 | 85.1169
Line11_12_13 | 0.012363 | 0.011074 | 0.013793 | 0.012363 | 0.011075 | 0.013794 | 0.0028551 | 0.0025575 | 0.0031855 | 0.0028552 | 0.0025575 | 0.0031855 | -3.124e-05 | 0.0015653 | -0.0021501 | 3.2761e-05 | -0.0015645 | 0.0021523 | 0.003777 | -0.00057772 | 2.5502e-05 | -0.0037756 | 0.00057905 | -2.3565e-05 | -89.8823 | -78.2526 | -94.2036 | 90.1177 | 101.7473 | 85.7965 |  | 1.3229 | 0.6524 | 0.67501 | 1.3224 | 0.65228 | 0.6757 | 0.59157 | -98.5103 | 85.1169 | 0.61484 | -98.563 | 85.1692
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9641e-09 | -7.0266e-08 | 7.1648e-08 | -4.0246e-09 | 4.7288e-08 | -4.7609e-08 | -1.4223e-07 | 1.0367e-08 | -4.6874e-09 | 9.4864e-08 | -6.1249e-09 | 1.8514e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3224 | 0.65228 | 0.6757 | 1.3224 | 0.65228 | 0.6757 | 0.61484 | -98.563 | 85.1692 | 0.61484 | -98.563 | 85.1692
Line13_13_14 | 0.012364 | 0.011075 | 0.013794 | 0.012364 | 0.011075 | 0.013794 | 0.0028553 | 0.0025577 | 0.0031856 | 0.0028553 | 0.0025577 | 0.0031856 | -3.2766e-05 | 0.0015646 | -0.0021524 | 3.4286e-05 | -0.0015638 | 0.0021546 | 0.0037757 | -0.00057906 | 2.3569e-05 | -0.0037743 | 0.0005804 | -2.1632e-05 | -89.8824 | -78.2532 | -94.2035 | 90.1177 | 101.7466 | 85.7966 |  | 1.3224 | 0.65228 | 0.6757 | 1.3219 | 0.65216 | 0.67638 | 0.61484 | -98.563 | 85.1692 | 0.63814 | -98.6158 | 85.2214
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.976e-09 | -4.6844e-08 | 4.7766e-08 | -3.0366e-09 | 2.3866e-08 | -2.3727e-08 | -9.4817e-08 | 6.9116e-09 | -3.1249e-09 | 4.7455e-08 | -2.6691e-09 | 2.889e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3224 | 0.65228 | 0.6757 | 1.3224 | 0.65228 | 0.6757 | 0.61484 | -98.563 | 85.1692 | 0.61484 | -98.563 | 85.1692
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8802e-10 | -2.3422e-08 | 2.3883e-08 | -2.0485e-09 | 4.4356e-10 | 1.5624e-10 | -4.7409e-08 | 3.4558e-09 | -1.5625e-09 | 4.683e-11 | 7.867e-10 | -1.2736e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3224 | 0.65228 | 0.6757 | 1.3224 | 0.65228 | 0.6757 | 0.61484 | -98.563 | 85.1692 | 0.61484 | -98.563 | 85.1692
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1046e-09 | -2.3545e-08 | 2.3901e-08 | -2.0584e-09 | 4.4075e-10 | 1.5735e-10 | -4.7639e-08 | 3.3222e-09 | -1.5436e-09 | 4.1583e-11 | 7.9267e-10 | -1.2747e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.324 | 0.65265 | 0.67364 | 1.324 | 0.65265 | 0.67364 | 0.54531 | -98.4051 | 85.0119 | 0.54531 | -98.4051 | 85.0119
Line17_5_19 | 0.01241 | 0.011115 | 0.013848 | 0.01241 | 0.011115 | 0.013848 | 0.0028659 | 0.0025669 | 0.0031981 | 0.0028659 | 0.002567 | 0.0031981 | -4.2591e-05 | 0.0015747 | -0.0021542 | 4.4123e-05 | -0.0015739 | 0.0021565 | 0.0037941 | -0.00057182 | 2.1966e-05 | -0.0037927 | 0.00057316 | -2.0014e-05 | -90.0979 | -78.4477 | -94.4039 | 89.9021 | 101.5522 | 85.5962 |  | 1.324 | 0.65265 | 0.67364 | 1.3235 | 0.65252 | 0.67433 | 0.54526 | -98.405 | 85.0119 | 0.56867 | -98.4579 | 85.0645
Line1_1_3 | 0.012363 | 0.011074 | 0.013793 | 0.012363 | 0.011074 | 0.013793 | 0.002855 | 0.0025574 | 0.0031853 | 0.0028551 | 0.0025574 | 0.0031854 | -2.6673e-05 | 0.0015677 | -0.0021433 | 2.8193e-05 | -0.0015669 | 0.0021456 | 0.0037814 | -0.00057372 | 3.1314e-05 | -0.0037799 | 0.00057505 | -2.9378e-05 | -89.8823 | -78.2521 | -94.2037 | 90.1177 | 101.7478 | 85.7964 |  | 1.3245 | 0.65278 | 0.67295 | 1.324 | 0.65265 | 0.67363 | 0.52186 | -98.3522 | 84.9593 | 0.54508 | -98.4049 | 85.0119
Line2_1_4 | 0.012425 | 0.011128 | 0.013866 | 0.012425 | 0.011128 | 0.013866 | 0.0028694 | 0.00257 | 0.0032022 | 0.0028694 | 0.00257 | 0.0032022 | -4.5897e-05 | 0.0015781 | -0.0021548 | 4.7433e-05 | -0.0015772 | 0.0021571 | 0.0038002 | -0.00056937 | 2.1425e-05 | -0.0037988 | 0.00057071 | -1.9468e-05 | -90.1701 | -78.5127 | -94.4711 | 89.8299 | 101.4872 | 85.529 |  | 1.3245 | 0.65278 | 0.67295 | 1.324 | 0.65265 | 0.67364 | 0.52186 | -98.3522 | 84.9593 | 0.54531 | -98.4051 | 85.0119
Line3_1_5 | 0.01241 | 0.011115 | 0.013848 | 0.01241 | 0.011115 | 0.013848 | 0.0028659 | 0.0025669 | 0.003198 | 0.0028659 | 0.0025669 | 0.0031981 | -4.1056e-05 | 0.0015755 | -0.002152 | 4.2588e-05 | -0.0015747 | 0.0021542 | 0.0037956 | -0.00057047 | 2.3919e-05 | -0.0037941 | 0.00057182 | -2.1967e-05 | -90.0979 | -78.4475 | -94.4039 | 89.9021 | 101.5523 | 85.5962 |  | 1.3245 | 0.65278 | 0.67295 | 1.324 | 0.65265 | 0.67364 | 0.52186 | -98.3522 | 84.9593 | 0.54526 | -98.405 | 85.0119
Line4_2_6 | 0.011906 | 1.3506 | 1.4071 | 0.011906 | 1.3506 | 1.4071 | 0.0027495 | 0.3119 | 0.32495 | 0.0027496 | 0.3119 | 0.32495 | -0.00044625 | 0.10464 | 0.11503 | 0.00045165 | -0.069896 | -0.07678 | 0.0036065 | 0.11128 | 0.11706 | -0.0035981 | -0.074155 | -0.078164 | -96.4311 | -145.1497 | 39.4611 | 83.569 | 34.8503 | -140.5389 |  | 1.3217 | 0.48975 | 0.50507 | 1.3189 | 0.32672 | 0.33718 | 0.62249 | -98.3868 | 84.9639 | 0.72356 | -98.4561 | 84.973
Line5_6_7 | 0.011906 | 1.3506 | 1.4071 | 0.011906 | 1.3506 | 1.4071 | 0.0027496 | 0.3119 | 0.32495 | 0.0027496 | 0.3119 | 0.32495 | -0.00045165 | 0.069896 | 0.07678 | 0.00045705 | -0.035153 | -0.038532 | 0.0035981 | 0.074155 | 0.078164 | -0.0035897 | -0.037026 | -0.039265 | -96.4311 | -145.1497 | 39.4611 | 83.569 | 34.8503 | -140.5389 |  | 1.3189 | 0.32672 | 0.33718 | 1.3161 | 0.16369 | 0.1693 | 0.72356 | -98.4561 | 84.973 | 0.82505 | -98.6632 | 85.0003
Line6_7_8 | 0 | 1.3527 | 1.4228 | 0 | 1.3527 | 1.4228 | 0 | 0.3124 | 0.32858 | 0 | 0.3124 | 0.32858 | 5.7008e-09 | 0.034795 | 0.039134 | -5.9783e-09 | -1.8025e-14 | 2.3029e-14 | -1.4491e-07 | 0.037474 | 0.039535 | 9.658e-08 | -1.0225e-14 | 4.3478e-15 | 0 | -145.7866 | 39.7084 | 0 | 34.2134 | -140.2917 |  | 1.3161 | 0.16369 | 0.1693 | 1.3136 | 0 | 0 | 0.82505 | -98.6632 | 85.0003 | 0.9011 | 0 | 0
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9928e-09 | -2.3842e-21 | -1.9074e-21 | -1.9928e-09 | 6.0986e-18 | -1.0714e-17 | -4.8256e-08 | 1.095e-21 | 1.4786e-21 | 6.8174e-11 | 1.9725e-17 | -1.8505e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3136 | 0 | 0 | 1.3136 | 0 | 0 | 0.9011 | 0 | 0 | 0.9011 | 0 | 0
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9928e-09 | -2.3842e-21 | -1.9074e-21 | -1.9928e-09 | 6.0986e-18 | -1.0714e-17 | -4.8256e-08 | 1.095e-21 | 1.4786e-21 | 6.8174e-11 | 1.9725e-17 | -1.8505e-18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3136 | 0 | 0 | 1.3136 | 0 | 0 | 0.9011 | 0 | 0 | 0.9011 | 0 | 0
Line9_3_11 | 0.012363 | 0.011074 | 0.013793 | 0.012363 | 0.011074 | 0.013793 | 0.0028551 | 0.0025574 | 0.0031854 | 0.0028551 | 0.0025575 | 0.0031854 | -2.8195e-05 | 0.0015669 | -0.0021456 | 2.9716e-05 | -0.0015661 | 0.0021478 | 0.0037799 | -0.00057505 | 2.9377e-05 | -0.0037785 | 0.00057639 | -2.744e-05 | -89.8823 | -78.2522 | -94.2037 | 90.1177 | 101.7476 | 85.7964 |  | 1.324 | 0.65265 | 0.67363 | 1.3235 | 0.65253 | 0.67432 | 0.54508 | -98.4049 | 85.0119 | 0.56832 | -98.4576 | 85.0644

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0021512 | 0.027742 | 0.029178 | 0.0021512 | 0.027742 | 0.029178 | 0.00049679 | 0.0064067 | 0.0067385 | 0.0004968 | 0.0064067 | 0.0067385 | 0.00024312 | 0.0042878 | 0.0042902 | -0.00024293 | -0.0042754 | -0.0042728 | 0.00044165 | 0.0036823 | 0.0047767 | -0.00044139 | -0.0036658 | -0.0047622 | -58.9326 | -158.4676 | 67.2873 | 121.0674 | 21.5324 | -112.7127 |  | 1.0148 | 0.88218 | 0.95281 | 1.0141 | 0.87904 | 0.94949 | 2.2354 | -117.8123 | 115.359 | 2.2408 | -117.8567 | 115.3875
Line10_11_12 | 0.002171 | 0.0021791 | 0.0022073 | 0.002171 | 0.0021791 | 0.0022073 | 0.00050136 | 0.00050323 | 0.00050975 | 0.00050137 | 0.00050324 | 0.00050975 | 0.00025116 | 0.00021445 | -0.00048327 | -0.00025111 | -0.0002144 | 0.00048332 | 0.00044232 | -0.00038876 | 4.93e-05 | -0.00044228 | 0.00038882 | -4.9253e-05 | -58.1724 | -56.71 | -58.8037 | 121.8276 | 123.29 | 121.1963 |  | 1.0145 | 0.88227 | 0.95298 | 1.0144 | 0.88231 | 0.95306 | 2.2391 | -117.8284 | 115.3715 | 2.2409 | -117.8364 | 115.3777
Line11_12_13 | 0.002171 | 0.0021791 | 0.0022073 | 0.002171 | 0.0021791 | 0.0022073 | 0.00050137 | 0.00050324 | 0.00050975 | 0.00050137 | 0.00050325 | 0.00050976 | 0.00025111 | 0.0002144 | -0.00048332 | -0.00025107 | -0.00021436 | 0.00048338 | 0.00044228 | -0.00038882 | 4.9252e-05 | -0.00044224 | 0.00038887 | -4.9204e-05 | -58.1725 | -56.7101 | -58.8037 | 121.8275 | 123.2899 | 121.1963 |  | 1.0144 | 0.88231 | 0.95306 | 1.0143 | 0.88235 | 0.95314 | 2.2409 | -117.8364 | 115.3777 | 2.2428 | -117.8444 | 115.384
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.8755e-09 | -9.087e-09 | 1.8103e-08 | 5.6752e-09 | 6.2747e-09 | -1.2091e-08 | -1.7186e-08 | 1.4194e-08 | -1.3009e-09 | 1.1596e-08 | -9.3471e-09 | 6.0004e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0143 | 0.88235 | 0.95314 | 1.0143 | 0.88235 | 0.95314 | 2.2428 | -117.8444 | 115.384 | 2.2428 | -117.8444 | 115.384
Line13_13_14 | 0.0021711 | 0.0021792 | 0.0022074 | 0.0021711 | 0.0021792 | 0.0022074 | 0.00050139 | 0.00050327 | 0.00050978 | 0.0005014 | 0.00050327 | 0.00050979 | 0.00025108 | 0.00021437 | -0.0004834 | -0.00025104 | -0.00021433 | 0.00048345 | 0.00044226 | -0.00038888 | 4.9206e-05 | -0.00044222 | 0.00038894 | -4.9158e-05 | -58.1726 | -56.7103 | -58.8038 | 121.8274 | 123.2897 | 121.1962 |  | 1.0143 | 0.88235 | 0.95314 | 1.0142 | 0.88239 | 0.95323 | 2.2428 | -117.8444 | 115.384 | 2.2446 | -117.8525 | 115.3903
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.917e-09 | -6.058e-09 | 1.2069e-08 | 2.7167e-09 | 3.2457e-09 | -6.0562e-09 | -1.1458e-08 | 9.4627e-09 | -8.6723e-10 | 5.867e-09 | -4.6157e-09 | 1.6642e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0143 | 0.88235 | 0.95314 | 1.0143 | 0.88235 | 0.95314 | 2.2428 | -117.8444 | 115.384 | 2.2428 | -117.8444 | 115.384
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9585e-09 | -3.029e-09 | 6.0344e-09 | -2.4182e-10 | 2.167e-10 | -2.1754e-11 | -5.7288e-09 | 4.7313e-09 | -4.3362e-10 | 1.3826e-10 | 1.156e-10 | -2.6719e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0143 | 0.88235 | 0.95314 | 1.0143 | 0.88235 | 0.95314 | 2.2428 | -117.8444 | 115.384 | 2.2428 | -117.8444 | 115.384
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9507e-09 | -3.0589e-09 | 6.0568e-09 | -2.433e-10 | 2.1702e-10 | -2.0958e-11 | -5.7627e-09 | 4.7363e-09 | -4.1551e-10 | 1.3798e-10 | 1.1688e-10 | -2.6821e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0147 | 0.88222 | 0.95289 | 1.0147 | 0.88222 | 0.95289 | 2.2373 | -117.8204 | 115.3652 | 2.2373 | -117.8204 | 115.3652
Line17_5_19 | 0.0021792 | 0.0021874 | 0.0022158 | 0.0021792 | 0.0021874 | 0.0022158 | 0.00050327 | 0.00050515 | 0.00051171 | 0.00050328 | 0.00050516 | 0.00051171 | 0.00025056 | 0.00021669 | -0.00048525 | -0.00025052 | -0.00021665 | 0.00048531 | 0.00044496 | -0.00038943 | 4.7805e-05 | -0.00044491 | 0.00038948 | -4.7757e-05 | -58.3783 | -56.9133 | -59.0084 | 121.6217 | 123.0867 | 120.9917 |  | 1.0147 | 0.88222 | 0.95289 | 1.0145 | 0.88227 | 0.95298 | 2.2373 | -117.8204 | 115.3652 | 2.2392 | -117.8284 | 115.3715
Line1_1_3 | 0.0021709 | 0.002179 | 0.0022072 | 0.0021709 | 0.002179 | 0.0022072 | 0.00050135 | 0.00050322 | 0.00050974 | 0.00050136 | 0.00050323 | 0.00050974 | 0.00025124 | 0.00021453 | -0.00048316 | -0.0002512 | -0.00021449 | 0.00048322 | 0.0004424 | -0.00038866 | 4.9396e-05 | -0.00044236 | 0.00038871 | -4.9349e-05 | -58.1724 | -56.7099 | -58.8036 | 121.8276 | 123.2901 | 121.1964 |  | 1.0148 | 0.88218 | 0.95281 | 1.0147 | 0.88222 | 0.95289 | 2.2354 | -117.8123 | 115.359 | 2.2373 | -117.8203 | 115.3652
Line2_1_4 | 0.0021819 | 0.0021901 | 0.0022185 | 0.0021819 | 0.0021901 | 0.0022186 | 0.00050389 | 0.00050577 | 0.00051235 | 0.0005039 | 0.00050578 | 0.00051235 | 0.00025038 | 0.00021746 | -0.00048587 | -0.00025034 | -0.00021742 | 0.00048592 | 0.00044585 | -0.0003896 | 4.7333e-05 | -0.00044581 | 0.00038966 | -4.7285e-05 | -58.4472 | -56.9813 | -59.0769 | 121.5528 | 123.0187 | 120.9231 |  | 1.0148 | 0.88218 | 0.95281 | 1.0147 | 0.88222 | 0.95289 | 2.2354 | -117.8123 | 115.359 | 2.2373 | -117.8204 | 115.3652
Line3_1_5 | 0.0021792 | 0.0021873 | 0.0022157 | 0.0021792 | 0.0021874 | 0.0022158 | 0.00050326 | 0.00050514 | 0.0005117 | 0.00050327 | 0.00050515 | 0.00051171 | 0.0002506 | 0.00021673 | -0.0004852 | -0.00025056 | -0.00021669 | 0.00048525 | 0.000445 | -0.00038937 | 4.7854e-05 | -0.00044496 | 0.00038943 | -4.7806e-05 | -58.3782 | -56.9133 | -59.0083 | 121.6218 | 123.0867 | 120.9917 |  | 1.0148 | 0.88218 | 0.95281 | 1.0147 | 0.88222 | 0.95289 | 2.2354 | -117.8123 | 115.359 | 2.2373 | -117.8204 | 115.3652
Line4_2_6 | 0.0021512 | 0.027742 | 0.029178 | 0.0021512 | 0.027742 | 0.029178 | 0.0004968 | 0.0064067 | 0.0067385 | 0.00049681 | 0.0064067 | 0.0067385 | 0.00024293 | 0.0042754 | 0.0042728 | -0.00024273 | -0.004263 | -0.0042555 | 0.00044139 | 0.0036658 | 0.0047622 | -0.00044114 | -0.0036494 | -0.0047477 | -58.9326 | -158.4676 | 67.2873 | 121.0674 | 21.5325 | -112.7128 |  | 1.0141 | 0.87904 | 0.94949 | 1.0135 | 0.87591 | 0.94617 | 2.2408 | -117.8567 | 115.3875 | 2.2462 | -117.9013 | 115.4163
Line5_6_7 | 0.0021512 | 0.027742 | 0.029178 | 0.0021513 | 0.027742 | 0.029178 | 0.00049681 | 0.0064067 | 0.0067385 | 0.00049681 | 0.0064067 | 0.0067385 | 0.00024273 | 0.004263 | 0.0042555 | -0.00024254 | -0.0042505 | -0.0042382 | 0.00044114 | 0.0036494 | 0.0047477 | -0.00044089 | -0.003633 | -0.0047332 | -58.9326 | -158.4675 | 67.2872 | 121.0674 | 21.5325 | -112.7128 |  | 1.0135 | 0.87591 | 0.94617 | 1.0128 | 0.87277 | 0.94285 | 2.2462 | -117.9013 | 115.4163 | 2.2516 | -117.9463 | 115.4452
Line6_7_8 | 0 | 0.0284 | 0.030682 | 0 | 0.0284 | 0.030682 | 0 | 0.0065587 | 0.0070857 | 0 | 0.0065587 | 0.0070857 | -8.8152e-09 | 0.0040451 | 0.004726 | 5.6372e-09 | -0.0040328 | -0.0047069 | -1.7713e-08 | 0.0040503 | 0.0047221 | 1.1957e-08 | -0.0040328 | -0.0047069 | 0 | -162.9832 | 70.4689 | 0 | 17.0169 | -109.5312 |  | 1.0128 | 0.87277 | 0.94285 | 1.0123 | 0.86957 | 0.93944 | 2.2516 | -117.9463 | 115.4452 | 2.2551 | -117.983 | 115.4688
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9356e-09 | -3.1656e-09 | 6.0545e-09 | -2.3404e-10 | 2.5456e-10 | 2.6154e-11 | -5.909e-09 | 4.7417e-09 | -3.3415e-10 | 1.3875e-10 | 1.0661e-10 | -2.5853e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0123 | 0.86957 | 0.93944 | 1.0123 | 0.86957 | 0.93944 | 2.2551 | -117.983 | 115.4688 | 2.2551 | -117.983 | 115.4688
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9356e-09 | -3.1656e-09 | 6.0545e-09 | -2.3404e-10 | 2.5456e-10 | 2.6154e-11 | -5.909e-09 | 4.7417e-09 | -3.3415e-10 | 1.3875e-10 | 1.0661e-10 | -2.5853e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0123 | 0.86957 | 0.93944 | 1.0123 | 0.86957 | 0.93944 | 2.2551 | -117.983 | 115.4688 | 2.2551 | -117.983 | 115.4688
Line9_3_11 | 0.0021709 | 0.002179 | 0.0022072 | 0.002171 | 0.0021791 | 0.0022073 | 0.00050136 | 0.00050323 | 0.00050974 | 0.00050136 | 0.00050323 | 0.00050975 | 0.0002512 | 0.00021449 | -0.00048322 | -0.00025116 | -0.00021445 | 0.00048327 | 0.00044236 | -0.00038871 | 4.9348e-05 | -0.00044232 | 0.00038876 | -4.9301e-05 | -58.1724 | -56.71 | -58.8037 | 121.8276 | 123.29 | 121.1963 |  | 1.0147 | 0.88222 | 0.95289 | 1.0145 | 0.88227 | 0.95298 | 2.2373 | -117.8203 | 115.3652 | 2.2391 | -117.8284 | 115.3715

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.002038 | 0.026282 | 0.027643 | 0.002038 | 0.026282 | 0.027643 | 0.00047065 | 0.0060695 | 0.0063838 | 0.00047065 | 0.0060695 | 0.0063838 | 0.0002182 | 0.0038483 | 0.0038504 | -0.00021803 | -0.0038372 | -0.0038349 | 0.00039638 | 0.0033049 | 0.0042871 | -0.00039615 | -0.0032901 | -0.0042741 | -58.9326 | -158.4676 | 67.2873 | 121.0674 | 21.5324 | -112.7127 |  | 0.96139 | 0.83575 | 0.90266 | 0.96077 | 0.83278 | 0.89952 | 2.2354 | -117.8123 | 115.359 | 2.2408 | -117.8567 | 115.3875
Line10_11_12 | 0.0020567 | 0.0020644 | 0.0020911 | 0.0020567 | 0.0020644 | 0.0020911 | 0.00047497 | 0.00047675 | 0.00048292 | 0.00047498 | 0.00047675 | 0.00048293 | 0.00022541 | 0.00019247 | -0.00043374 | -0.00022538 | -0.00019243 | 0.00043379 | 0.00039699 | -0.00034892 | 4.4247e-05 | -0.00039695 | 0.00034896 | -4.4204e-05 | -58.1724 | -56.71 | -58.8037 | 121.8276 | 123.29 | 121.1963 |  | 0.96115 | 0.83583 | 0.90282 | 0.96103 | 0.83587 | 0.9029 | 2.2391 | -117.8284 | 115.3715 | 2.2409 | -117.8364 | 115.3777
Line11_12_13 | 0.0020567 | 0.0020644 | 0.0020911 | 0.0020568 | 0.0020644 | 0.0020912 | 0.00047498 | 0.00047675 | 0.00048293 | 0.00047499 | 0.00047676 | 0.00048293 | 0.00022538 | 0.00019243 | -0.00043379 | -0.00022534 | -0.00019239 | 0.00043383 | 0.00039695 | -0.00034896 | 4.4204e-05 | -0.00039691 | 0.00034901 | -4.4161e-05 | -58.1725 | -56.7101 | -58.8037 | 121.8275 | 123.2899 | 121.1963 |  | 0.96103 | 0.83587 | 0.9029 | 0.96091 | 0.83591 | 0.90298 | 2.2409 | -117.8364 | 115.3777 | 2.2428 | -117.8444 | 115.384
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9659e-09 | -8.1557e-09 | 1.6248e-08 | 5.0935e-09 | 5.6316e-09 | -1.0851e-08 | -1.5425e-08 | 1.2739e-08 | -1.1675e-09 | 1.0407e-08 | -8.3891e-09 | 5.3854e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96091 | 0.83591 | 0.90298 | 0.96091 | 0.83591 | 0.90298 | 2.2428 | -117.8444 | 115.384 | 2.2428 | -117.8444 | 115.384
Line13_13_14 | 0.0020568 | 0.0020645 | 0.0020912 | 0.0020569 | 0.0020645 | 0.0020913 | 0.000475 | 0.00047678 | 0.00048295 | 0.00047501 | 0.00047678 | 0.00048296 | 0.00022535 | 0.0001924 | -0.00043385 | -0.00022531 | -0.00019236 | 0.0004339 | 0.00039693 | -0.00034903 | 4.4162e-05 | -0.00039689 | 0.00034907 | -4.4119e-05 | -58.1726 | -56.7103 | -58.8038 | 121.8274 | 123.2897 | 121.1962 |  | 0.96091 | 0.83591 | 0.90298 | 0.96079 | 0.83595 | 0.90306 | 2.2428 | -117.8444 | 115.384 | 2.2446 | -117.8525 | 115.3903
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.3106e-09 | -5.4371e-09 | 1.0832e-08 | 2.4382e-09 | 2.913e-09 | -5.4354e-09 | -1.0283e-08 | 8.4928e-09 | -7.7835e-10 | 5.2657e-09 | -4.1427e-09 | 1.4937e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96091 | 0.83591 | 0.90298 | 0.96091 | 0.83591 | 0.90298 | 2.2428 | -117.8444 | 115.384 | 2.2428 | -117.8444 | 115.384
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6553e-09 | -2.7186e-09 | 5.4159e-09 | -2.1704e-10 | 1.9449e-10 | -1.9524e-11 | -5.1416e-09 | 4.2464e-09 | -3.8917e-10 | 1.2409e-10 | 1.0375e-10 | -2.3981e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96091 | 0.83591 | 0.90298 | 0.96091 | 0.83591 | 0.90298 | 2.2428 | -117.8444 | 115.384 | 2.2428 | -117.8444 | 115.384
Line16_4_18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6483e-09 | -2.7453e-09 | 5.4361e-09 | -2.1836e-10 | 1.9478e-10 | -1.881e-11 | -5.172e-09 | 4.2509e-09 | -3.7292e-10 | 1.2384e-10 | 1.049e-10 | -2.4072e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.96127 | 0.83579 | 0.90274 | 0.96127 | 0.83579 | 0.90274 | 2.2373 | -117.8204 | 115.3652 | 2.2373 | -117.8204 | 115.3652
Line17_5_19 | 0.0020645 | 0.0020722 | 0.0020991 | 0.0020645 | 0.0020723 | 0.0020992 | 0.00047678 | 0.00047856 | 0.00048478 | 0.00047679 | 0.00047857 | 0.00048478 | 0.00022488 | 0.00019448 | -0.00043552 | -0.00022484 | -0.00019444 | 0.00043557 | 0.00039935 | -0.00034951 | 4.2906e-05 | -0.00039931 | 0.00034956 | -4.2862e-05 | -58.3783 | -56.9133 | -59.0084 | 121.6217 | 123.0867 | 120.9917 |  | 0.96127 | 0.83579 | 0.90274 | 0.96115 | 0.83583 | 0.90282 | 2.2373 | -117.8204 | 115.3652 | 2.2392 | -117.8284 | 115.3715
Line1_1_3 | 0.0020566 | 0.0020643 | 0.0020911 | 0.0020567 | 0.0020644 | 0.0020911 | 0.00047496 | 0.00047674 | 0.00048291 | 0.00047497 | 0.00047674 | 0.00048291 | 0.00022549 | 0.00019254 | -0.00043364 | -0.00022545 | -0.0001925 | 0.00043369 | 0.00039706 | -0.00034882 | 4.4334e-05 | -0.00039702 | 0.00034887 | -4.4291e-05 | -58.1724 | -56.7099 | -58.8036 | 121.8276 | 123.2901 | 121.1964 |  | 0.96139 | 0.83575 | 0.90266 | 0.96127 | 0.83579 | 0.90274 | 2.2354 | -117.8123 | 115.359 | 2.2373 | -117.8203 | 115.3652
Line2_1_4 | 0.0020671 | 0.0020748 | 0.0021018 | 0.0020671 | 0.0020748 | 0.0021018 | 0.00047737 | 0.00047915 | 0.00048538 | 0.00047737 | 0.00047916 | 0.00048539 | 0.00022472 | 0.00019518 | -0.00043607 | -0.00022468 | -0.00019514 | 0.00043612 | 0.00040016 | -0.00034967 | 4.2482e-05 | -0.00040012 | 0.00034972 | -4.2438e-05 | -58.4472 | -56.9813 | -59.0769 | 121.5528 | 123.0187 | 120.9231 |  | 0.96139 | 0.83575 | 0.90266 | 0.96127 | 0.83579 | 0.90274 | 2.2354 | -117.8123 | 115.359 | 2.2373 | -117.8204 | 115.3652
Line3_1_5 | 0.0020645 | 0.0020722 | 0.0020991 | 0.0020645 | 0.0020722 | 0.0020991 | 0.00047678 | 0.00047856 | 0.00048477 | 0.00047678 | 0.00047856 | 0.00048478 | 0.00022492 | 0.00019452 | -0.00043547 | -0.00022488 | -0.00019448 | 0.00043552 | 0.00039939 | -0.00034947 | 4.2949e-05 | -0.00039935 | 0.00034951 | -4.2906e-05 | -58.3782 | -56.9133 | -59.0083 | 121.6218 | 123.0867 | 120.9917 |  | 0.96139 | 0.83575 | 0.90266 | 0.96127 | 0.83579 | 0.90274 | 2.2354 | -117.8123 | 115.359 | 2.2373 | -117.8204 | 115.3652
Line4_2_6 | 0.002038 | 0.026282 | 0.027643 | 0.002038 | 0.026282 | 0.027643 | 0.00047065 | 0.0060695 | 0.0063838 | 0.00047066 | 0.0060695 | 0.0063838 | 0.00021803 | 0.0038372 | 0.0038349 | -0.00021785 | -0.003826 | -0.0038194 | 0.00039615 | 0.0032901 | 0.0042741 | -0.00039593 | -0.0032754 | -0.0042611 | -58.9326 | -158.4676 | 67.2873 | 121.0674 | 21.5325 | -112.7128 |  | 0.96077 | 0.83278 | 0.89952 | 0.96015 | 0.82981 | 0.89637 | 2.2408 | -117.8567 | 115.3875 | 2.2462 | -117.9013 | 115.4163
Line5_6_7 | 0.002038 | 0.026282 | 0.027643 | 0.002038 | 0.026282 | 0.027643 | 0.00047066 | 0.0060695 | 0.0063838 | 0.00047066 | 0.0060695 | 0.0063838 | 0.00021785 | 0.003826 | 0.0038194 | -0.00021768 | -0.0038149 | -0.0038038 | 0.00039593 | 0.0032754 | 0.0042611 | -0.0003957 | -0.0032607 | -0.0042481 | -58.9326 | -158.4675 | 67.2872 | 121.0674 | 21.5325 | -112.7128 |  | 0.96015 | 0.82981 | 0.89637 | 0.95954 | 0.82683 | 0.89323 | 2.2462 | -117.9013 | 115.4163 | 2.2516 | -117.9463 | 115.4452
Line6_7_8 | 0 | 0.026905 | 0.029067 | 0 | 0.026905 | 0.029067 | 0 | 0.0062135 | 0.0067128 | 0 | 0.0062135 | 0.0067128 | -7.9117e-09 | 0.0036305 | 0.0042416 | 5.0594e-09 | -0.0036195 | -0.0042245 | -1.5898e-08 | 0.0036351 | 0.0042381 | 1.0731e-08 | -0.0036195 | -0.0042245 | 0 | -162.9832 | 70.4689 | 0 | 17.0169 | -109.5312 |  | 0.95954 | 0.82683 | 0.89323 | 0.95904 | 0.82381 | 0.88999 | 2.2516 | -117.9463 | 115.4452 | 2.2551 | -117.983 | 115.4688
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6347e-09 | -2.8411e-09 | 5.434e-09 | -2.1005e-10 | 2.2847e-10 | 2.3473e-11 | -5.3033e-09 | 4.2557e-09 | -2.999e-10 | 1.2453e-10 | 9.5683e-11 | -2.3203e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95904 | 0.82381 | 0.88999 | 0.95904 | 0.82381 | 0.88999 | 2.2551 | -117.983 | 115.4688 | 2.2551 | -117.983 | 115.4688
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6347e-09 | -2.8411e-09 | 5.434e-09 | -2.1005e-10 | 2.2847e-10 | 2.3473e-11 | -5.3033e-09 | 4.2557e-09 | -2.999e-10 | 1.2453e-10 | 9.5683e-11 | -2.3203e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.95904 | 0.82381 | 0.88999 | 0.95904 | 0.82381 | 0.88999 | 2.2551 | -117.983 | 115.4688 | 2.2551 | -117.983 | 115.4688
Line9_3_11 | 0.0020567 | 0.0020644 | 0.0020911 | 0.0020567 | 0.0020644 | 0.0020911 | 0.00047497 | 0.00047674 | 0.00048291 | 0.00047497 | 0.00047675 | 0.00048292 | 0.00022545 | 0.0001925 | -0.00043369 | -0.00022542 | -0.00019247 | 0.00043374 | 0.00039702 | -0.00034887 | 4.4291e-05 | -0.00039699 | 0.00034892 | -4.4248e-05 | -58.1724 | -56.71 | -58.8037 | 121.8276 | 123.29 | 121.1963 |  | 0.96127 | 0.83579 | 0.90274 | 0.96115 | 0.83583 | 0.90282 | 2.2373 | -117.8203 | 115.3652 | 2.2391 | -117.8284 | 115.3715