## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.32497 | 0.32497 | 0 | 0 | 0.22515 | 0.22515 | -0.081585 | 0.084753 | -0.15129 | 0.15762 | 112.3024 | -67.6976 | 0.76342 | 0.79487 | -6.0346 | -5.9644
Line10_11_12 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.078736 | 0.08124 | -0.14384 | 0.14885 | 112.8171 | -67.1829 | 0.81932 | 0.84727 | -5.8785 | -5.8082
Line11_12_13 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.08124 | 0.083744 | -0.14885 | 0.15386 | 112.8171 | -67.1829 | 0.84727 | 0.87523 | -5.8082 | -5.7423
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87523 | 0.87523 | -5.7423 | -5.7423
Line13_13_14 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.083744 | 0.086247 | -0.15386 | 0.15886 | 112.8171 | -67.1829 | 0.87523 | 0.90318 | -5.7423 | -5.6806
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87523 | 0.87523 | -5.7423 | -5.7423
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87523 | 0.87523 | -5.7423 | -5.7423
Line16_4_18 | 4.2793 | 4.2793 | 0 | 8.0393 | 2.9648 | 2.9648 | 0.54938 | -1e-07 | 1.0988 | -1e-07 | -69.5382 | 110.4618 | 0.41434 | 0 | -6.1032 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76342 | 0.76342 | -6.0346 | -6.0346
Line1_1_3 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.073729 | 0.076233 | -0.13383 | 0.13883 | 112.8171 | -67.1829 | 0.76342 | 0.79137 | -6.0346 | -5.9538
Line2_1_4 | 3.6053 | 3.6053 | 0 | 0 | 2.4978 | 2.4978 | 0.8552 | -0.46526 | 1.7043 | -0.92447 | -69.388 | 110.612 | 0.76342 | 0.41434 | -6.0346 | -6.1032
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76342 | 0.76342 | -6.0346 | -6.0346
Line4_2_6 | 0.32497 | 0.32497 | 0 | 0 | 0.22515 | 0.22515 | -0.084753 | 0.087921 | -0.15762 | 0.16396 | 112.3024 | -67.6976 | 0.79487 | 0.82632 | -5.9644 | -5.8996
Line5_6_7 | 0.32497 | 0.32497 | 0 | 0 | 0.22515 | 0.22515 | -0.087921 | 0.09109 | -0.16396 | 0.1703 | 112.3024 | -67.6976 | 0.82632 | 0.85778 | -5.8996 | -5.8396
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85778 | 0.85778 | -5.8396 | -5.8396
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85778 | 0.85778 | -5.8396 | -5.8396
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85778 | 0.85778 | -5.8396 | -5.8396
Line9_3_11 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.076233 | 0.078736 | -0.13883 | 0.14384 | 112.8171 | -67.1829 | 0.79137 | 0.81932 | -5.9538 | -5.8785

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.3348 | 0.3348 | 0 | 0 | 0.23196 | 0.23196 | -0.087546 | 0.090909 | -0.16063 | 0.16736 | 112.3588 | -67.6412 | 0.78869 | 0.82109 | -6.232 | -6.152
Line10_11_12 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.084782 | 0.087462 | -0.15341 | 0.15877 | 112.8681 | -67.1319 | 0.84651 | 0.87543 | -6.0587 | -5.9806
Line11_12_13 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.087462 | 0.090142 | -0.15877 | 0.16413 | 112.8681 | -67.1319 | 0.87543 | 0.90434 | -5.9806 | -5.9076
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90434 | 0.90434 | -5.9076 | -5.9076
Line13_13_14 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.090142 | 0.092822 | -0.16413 | 0.16949 | 112.8681 | -67.1319 | 0.90434 | 0.93326 | -5.9076 | -5.8391
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90434 | 0.90434 | -5.9076 | -5.9076
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90434 | 0.90434 | -5.9076 | -5.9076
Line16_4_18 | 4.4124 | 4.4124 | 0 | 8.3118 | 3.057 | 3.057 | 0.58408 | -1e-07 | 1.1682 | -1e-07 | -69.7214 | 110.2786 | 0.42723 | 0 | -6.2864 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78869 | 0.78869 | -6.232 | -6.232
Line1_1_3 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.079423 | 0.082103 | -0.14269 | 0.14805 | 112.8681 | -67.1319 | 0.78869 | 0.8176 | -6.232 | -6.1423
Line2_1_4 | 3.7331 | 3.7331 | 0 | 0 | 2.5864 | 2.5864 | 0.9143 | -0.49621 | 1.8235 | -0.9873 | -69.6025 | 110.3975 | 0.78869 | 0.42723 | -6.232 | -6.2864
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78869 | 0.78869 | -6.232 | -6.232
Line4_2_6 | 0.3348 | 0.3348 | 0 | 0 | 0.23196 | 0.23196 | -0.090909 | 0.094272 | -0.16736 | 0.17408 | 112.3588 | -67.6412 | 0.82109 | 0.85348 | -6.152 | -6.0781
Line5_6_7 | 0.3348 | 0.3348 | 0 | 0 | 0.23196 | 0.23196 | -0.094272 | 0.097635 | -0.17408 | 0.18081 | 112.3588 | -67.6412 | 0.85348 | 0.88588 | -6.0781 | -6.0096
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88588 | 0.88588 | -6.0096 | -6.0096
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88588 | 0.88588 | -6.0096 | -6.0096
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88588 | 0.88588 | -6.0096 | -6.0096
Line9_3_11 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.082103 | 0.084782 | -0.14805 | 0.15341 | 112.8681 | -67.1319 | 0.8176 | 0.84651 | -6.1423 | -6.0587

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.12039 | 0.12039 | 0 | 0 | 0.083411 | 0.083411 | -0.006237 | 0.0066719 | -0.09019 | 0.09106 | 93.9805 | -86.0195 | 1.0839 | 1.0946 | 0.024519 | -0.21006
Line10_11_12 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0060352 | 0.0063806 | -0.081782 | 0.082473 | 93.8274 | -86.1726 | 1.103 | 1.1127 | -0.3931 | -0.5965
Line11_12_13 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0063806 | 0.0067261 | -0.082473 | 0.083164 | 93.8274 | -86.1726 | 1.1127 | 1.1223 | -0.5965 | -0.79641
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1223 | 1.1223 | -0.79641 | -0.79641
Line13_13_14 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0067261 | 0.0070715 | -0.083164 | 0.083855 | 93.8274 | -86.1726 | 1.1223 | 1.1319 | -0.79641 | -0.99292
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1223 | 1.1223 | -0.79641 | -0.79641
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1223 | 1.1223 | -0.79641 | -0.79641
Line16_4_18 | 0.035619 | 0.035619 | 0 | 0.066915 | 0.024677 | 0.024677 | 0.019068 | -0.01903 | 0.019106 | -0.01903 | -45.1981 | 134.8019 | 1.0939 | 1.0906 | -0.14093 | -0.19806
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0839 | 1.0839 | 0.024519 | 0.024519
Line1_1_3 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0053443 | 0.0056897 | -0.080401 | 0.081091 | 93.8274 | -86.1726 | 1.0839 | 1.0934 | 0.024519 | -0.18612
Line2_1_4 | 0.10837 | 0.10837 | 0 | 0 | 0.07508 | 0.07508 | -0.012793 | 0.013146 | -0.080364 | 0.081069 | 99.0698 | -80.9302 | 1.0839 | 1.0939 | 0.024519 | -0.14093
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0839 | 1.0839 | 0.024519 | 0.024519
Line4_2_6 | 0.12039 | 0.12039 | 0 | 0 | 0.083411 | 0.083411 | -0.0066719 | 0.0071067 | -0.09106 | 0.09193 | 93.9805 | -86.0195 | 1.0946 | 1.1054 | -0.21006 | -0.44005
Line5_6_7 | 0.12039 | 0.12039 | 0 | 0 | 0.083411 | 0.083411 | -0.0071067 | 0.0075416 | -0.09193 | 0.0928 | 93.9805 | -86.0195 | 1.1054 | 1.1162 | -0.44005 | -0.6656
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1162 | 1.1162 | -0.6656 | -0.6656
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1162 | 1.1162 | -0.6656 | -0.6656
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1162 | 1.1162 | -0.6656 | -0.6656
Line9_3_11 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0056897 | 0.0060352 | -0.081091 | 0.081782 | 93.8274 | -86.1726 | 1.0934 | 1.103 | -0.18612 | -0.3931

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.1213 | 0.1213 | 0 | 0 | 0.084041 | 0.084041 | -0.0067259 | 0.0071674 | -0.095199 | 0.096082 | 94.0592 | -85.9408 | 1.1356 | 1.1465 | 0.017899 | -0.20695
Line10_11_12 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0065032 | 0.0068567 | -0.086627 | 0.087334 | 93.9091 | -86.0909 | 1.155 | 1.1648 | -0.3841 | -0.58006
Line11_12_13 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0068567 | 0.0072103 | -0.087334 | 0.088041 | 93.9091 | -86.0909 | 1.1648 | 1.1745 | -0.58006 | -0.77278
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1745 | 1.1745 | -0.77278 | -0.77278
Line13_13_14 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0072103 | 0.0075638 | -0.088041 | 0.088748 | 93.9091 | -86.0909 | 1.1745 | 1.1843 | -0.77278 | -0.96232
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1745 | 1.1745 | -0.77278 | -0.77278
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1745 | 1.1745 | -0.77278 | -0.77278
Line16_4_18 | 0.037299 | 0.037299 | 0 | 0.070262 | 0.025842 | 0.025842 | 0.02091 | -0.020868 | 0.020952 | -0.020868 | -45.2026 | 134.7974 | 1.1455 | 1.1421 | -0.14543 | -0.20255
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1356 | 1.1356 | 0.017899 | 0.017899
Line1_1_3 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0057961 | 0.0061496 | -0.085213 | 0.08592 | 93.9091 | -86.0909 | 1.1356 | 1.1453 | 0.017899 | -0.1848
Line2_1_4 | 0.10744 | 0.10744 | 0 | 0 | 0.074435 | 0.074435 | -0.01216 | 0.012506 | -0.083649 | 0.084342 | 98.2891 | -81.7109 | 1.1356 | 1.1455 | 0.017899 | -0.14543
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1356 | 1.1356 | 0.017899 | 0.017899
Line4_2_6 | 0.1213 | 0.1213 | 0 | 0 | 0.084041 | 0.084041 | -0.0071674 | 0.0076088 | -0.096082 | 0.096965 | 94.0592 | -85.9408 | 1.1465 | 1.1573 | -0.20695 | -0.42758
Line5_6_7 | 0.1213 | 0.1213 | 0 | 0 | 0.084041 | 0.084041 | -0.0076088 | 0.0080502 | -0.096965 | 0.097848 | 94.0592 | -85.9408 | 1.1573 | 1.1682 | -0.42758 | -0.6441
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1682 | 1.1682 | -0.6441 | -0.6441
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1682 | 1.1682 | -0.6441 | -0.6441
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1682 | 1.1682 | -0.6441 | -0.6441
Line9_3_11 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0061496 | 0.0065032 | -0.08592 | 0.086627 | 93.9091 | -86.0909 | 1.1453 | 1.155 | -0.1848 | -0.3841

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.0049477 | 0.0049477 | 0 | 0 | 0.0034279 | 0.0034279 | -0.0019748 | 0.0019762 | -0.0013385 | 0.0013399 | 134.3184 | -45.6816 | 0.69595 | 0.69653 | -11.5528 | -11.5426
Line10_11_12 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019731 | 0.0019745 | -0.0013332 | 0.0013347 | 134.4202 | -45.5798 | 0.69711 | 0.69769 | -11.5323 | -11.5221
Line11_12_13 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019745 | 0.0019759 | -0.0013347 | 0.0013361 | 134.4202 | -45.5798 | 0.69769 | 0.69827 | -11.5221 | -11.5119
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69827 | 0.69827 | -11.5119 | -11.5119
Line13_13_14 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019758 | 0.0019772 | -0.0013361 | 0.0013376 | 134.42 | -45.58 | 0.69827 | 0.69885 | -11.5119 | -11.5018
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69827 | 0.69827 | -11.5119 | -11.5119
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69827 | 0.69827 | -11.5119 | -11.5119
Line16_4_18 | 2.9036 | 2.9036 | 0 | 4.7948 | 2.0117 | 2.0117 | 0.48561 | -1e-07 | 0.50584 | -1e-07 | -57.7375 | 122.2625 | 0.34857 | 0 | -11.5684 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69595 | 0.69595 | -11.5528 | -11.5528
Line1_1_3 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019703 | 0.0019717 | -0.0013303 | 0.0013318 | 134.4203 | -45.5797 | 0.69595 | 0.69653 | -11.5528 | -11.5425
Line2_1_4 | 2.8936 | 2.8936 | 0 | 0 | 2.0048 | 2.0048 | 0.96651 | -0.48422 | 1.0062 | -0.50385 | -57.7063 | 122.2937 | 0.69595 | 0.34857 | -11.5528 | -11.5684
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69595 | 0.69595 | -11.5528 | -11.5528
Line4_2_6 | 0.0049477 | 0.0049477 | 0 | 0 | 0.0034279 | 0.0034279 | -0.0019762 | 0.0019776 | -0.0013399 | 0.0013414 | 134.3184 | -45.6816 | 0.69653 | 0.69711 | -11.5426 | -11.5324
Line5_6_7 | 0.0049477 | 0.0049477 | 0 | 0 | 0.0034279 | 0.0034279 | -0.0019776 | 0.001979 | -0.0013414 | 0.0013429 | 134.3183 | -45.6817 | 0.69711 | 0.6977 | -11.5324 | -11.5223
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6977 | 0.6977 | -11.5223 | -11.5223
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6977 | 0.6977 | -11.5223 | -11.5223
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6977 | 0.6977 | -11.5223 | -11.5223
Line9_3_11 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019717 | 0.0019731 | -0.0013318 | 0.0013332 | 134.4203 | -45.5797 | 0.69653 | 0.69711 | -11.5425 | -11.5323

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.0046873 | 0.0046873 | 0 | 0 | 0.0032475 | 0.0032475 | -0.0017724 | 0.0017737 | -0.0012013 | 0.0012026 | 134.3184 | -45.6816 | 0.65932 | 0.65987 | -11.5528 | -11.5426
Line10_11_12 | 0.0046709 | 0.0046709 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017708 | 0.0017721 | -0.0011966 | 0.0011979 | 134.4202 | -45.5798 | 0.66042 | 0.66097 | -11.5323 | -11.5221
Line11_12_13 | 0.0046709 | 0.0046709 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017721 | 0.0017733 | -0.0011979 | 0.0011992 | 134.4202 | -45.5798 | 0.66097 | 0.66152 | -11.5221 | -11.5119
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66152 | 0.66152 | -11.5119 | -11.5119
Line13_13_14 | 0.0046709 | 0.0046709 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017733 | 0.0017746 | -0.0011992 | 0.0012005 | 134.42 | -45.58 | 0.66152 | 0.66207 | -11.5119 | -11.5018
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66152 | 0.66152 | -11.5119 | -11.5119
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66152 | 0.66152 | -11.5119 | -11.5119
Line16_4_18 | 2.7508 | 2.7508 | 0 | 4.5424 | 1.9058 | 1.9058 | 0.43584 | -1e-07 | 0.454 | -1e-07 | -57.7375 | 122.2625 | 0.33023 | 0 | -11.5684 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65932 | 0.65932 | -11.5528 | -11.5528
Line1_1_3 | 0.004671 | 0.004671 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017683 | 0.0017696 | -0.001194 | 0.0011953 | 134.4203 | -45.5797 | 0.65932 | 0.65987 | -11.5528 | -11.5425
Line2_1_4 | 2.7413 | 2.7413 | 0 | 0 | 1.8992 | 1.8992 | 0.86745 | -0.43459 | 0.9031 | -0.45221 | -57.7063 | 122.2937 | 0.65932 | 0.33023 | -11.5528 | -11.5684
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65932 | 0.65932 | -11.5528 | -11.5528
Line4_2_6 | 0.0046873 | 0.0046873 | 0 | 0 | 0.0032475 | 0.0032475 | -0.0017736 | 0.0017749 | -0.0012026 | 0.0012039 | 134.3184 | -45.6816 | 0.65987 | 0.66042 | -11.5426 | -11.5324
Line5_6_7 | 0.0046873 | 0.0046873 | 0 | 0 | 0.0032475 | 0.0032475 | -0.0017749 | 0.0017762 | -0.0012039 | 0.0012053 | 134.3183 | -45.6817 | 0.66042 | 0.66097 | -11.5324 | -11.5223
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66097 | 0.66097 | -11.5223 | -11.5223
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66097 | 0.66097 | -11.5223 | -11.5223
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66097 | 0.66097 | -11.5223 | -11.5223
Line9_3_11 | 0.004671 | 0.004671 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017696 | 0.0017708 | -0.0011953 | 0.0011966 | 134.4203 | -45.5797 | 0.65987 | 0.66042 | -11.5425 | -11.5323

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 5.2325e-05 | 5.2325e-05 | 0 | 0 | 3.6252e-05 | 3.6252e-05 | -2.8824e-05 | 2.8824e-05 | -1.8685e-05 | 1.8685e-05 | 146.9224 | -33.0776 | 0.94756 | 0.94756 | -0.1244 | -0.12431
Line10_11_12 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8757e-05 | 2.8757e-05 | -1.8569e-05 | 1.8569e-05 | 147.0242 | -32.9758 | 0.94757 | 0.94757 | -0.12422 | -0.12414
Line11_12_13 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8757e-05 | 2.8757e-05 | -1.8569e-05 | 1.8569e-05 | 147.0241 | -32.9759 | 0.94757 | 0.94758 | -0.12414 | -0.12405
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94758 | 0.94758 | -0.12405 | -0.12405
Line13_13_14 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8757e-05 | 2.8757e-05 | -1.857e-05 | 1.857e-05 | 147.0239 | -32.9761 | 0.94758 | 0.94759 | -0.12405 | -0.12396
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94758 | 0.94758 | -0.12405 | -0.12405
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94758 | 0.94758 | -0.12405 | -0.12405
Line16_4_18 | 0.030707 | 0.030707 | 0 | 0.050707 | 0.021274 | 0.021274 | 0.014198 | -0.014144 | 0.0142 | -0.014144 | -45.1336 | 134.8664 | 0.94388 | 0.9402 | -0.12903 | -0.1336
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.1244 | -0.1244
Line1_1_3 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8756e-05 | 2.8757e-05 | -1.8569e-05 | 1.8569e-05 | 147.0243 | -32.9757 | 0.94756 | 0.94756 | -0.1244 | -0.12431
Line2_1_4 | 0.030601 | 0.030601 | 0 | 0 | 0.021201 | 0.021201 | 0.014211 | -0.014157 | 0.0142 | -0.014144 | -45.1023 | 134.8977 | 0.94756 | 0.94388 | -0.1244 | -0.12903
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.1244 | -0.1244
Line4_2_6 | 5.2325e-05 | 5.2325e-05 | 0 | 0 | 3.6252e-05 | 3.6252e-05 | -2.8824e-05 | 2.8824e-05 | -1.8685e-05 | 1.8685e-05 | 146.9223 | -33.0777 | 0.94756 | 0.94757 | -0.12431 | -0.12422
Line5_6_7 | 5.2325e-05 | 5.2325e-05 | 0 | 0 | 3.6252e-05 | 3.6252e-05 | -2.8824e-05 | 2.8824e-05 | -1.8685e-05 | 1.8686e-05 | 146.9222 | -33.0778 | 0.94757 | 0.94757 | -0.12422 | -0.12414
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94757 | 0.94757 | -0.12414 | -0.12414
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94757 | 0.94757 | -0.12414 | -0.12414
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94757 | 0.94757 | -0.12414 | -0.12414
Line9_3_11 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8756e-05 | 2.8757e-05 | -1.8569e-05 | 1.8569e-05 | 147.0242 | -32.9758 | 0.94756 | 0.94757 | -0.12431 | -0.12422

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 4.9571e-05 | 4.9571e-05 | 0 | 0 | 3.4344e-05 | 3.4344e-05 | -2.587e-05 | 2.587e-05 | -1.677e-05 | 1.677e-05 | 146.9224 | -33.0776 | 0.89769 | 0.89769 | -0.1244 | -0.12431
Line10_11_12 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.5809e-05 | -1.6666e-05 | 1.6666e-05 | 147.0242 | -32.9758 | 0.8977 | 0.8977 | -0.12422 | -0.12414
Line11_12_13 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.581e-05 | -1.6666e-05 | 1.6666e-05 | 147.0241 | -32.9759 | 0.8977 | 0.89771 | -0.12414 | -0.12405
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89771 | 0.89771 | -0.12405 | -0.12405
Line13_13_14 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.581e-05 | -1.6666e-05 | 1.6666e-05 | 147.0239 | -32.9761 | 0.89771 | 0.89771 | -0.12405 | -0.12396
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89771 | 0.89771 | -0.12405 | -0.12405
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89771 | 0.89771 | -0.12405 | -0.12405
Line16_4_18 | 0.029091 | 0.029091 | 0 | 0.048038 | 0.020155 | 0.020155 | 0.012743 | -0.012694 | 0.012745 | -0.012694 | -45.1336 | 134.8664 | 0.89421 | 0.89071 | -0.12903 | -0.1336
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.1244 | -0.1244
Line1_1_3 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.5809e-05 | -1.6666e-05 | 1.6666e-05 | 147.0243 | -32.9757 | 0.89769 | 0.89769 | -0.1244 | -0.12431
Line2_1_4 | 0.028991 | 0.028991 | 0 | 0 | 0.020085 | 0.020085 | 0.012754 | -0.012706 | 0.012745 | -0.012694 | -45.1023 | 134.8977 | 0.89769 | 0.89421 | -0.1244 | -0.12903
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.1244 | -0.1244
Line4_2_6 | 4.9571e-05 | 4.9571e-05 | 0 | 0 | 3.4344e-05 | 3.4344e-05 | -2.587e-05 | 2.587e-05 | -1.677e-05 | 1.677e-05 | 146.9223 | -33.0777 | 0.89769 | 0.8977 | -0.12431 | -0.12422
Line5_6_7 | 4.9571e-05 | 4.9571e-05 | 0 | 0 | 3.4344e-05 | 3.4344e-05 | -2.587e-05 | 2.587e-05 | -1.677e-05 | 1.677e-05 | 146.9222 | -33.0778 | 0.8977 | 0.8977 | -0.12422 | -0.12414
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8977 | 0.8977 | -0.12414 | -0.12414
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8977 | 0.8977 | -0.12414 | -0.12414
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8977 | 0.8977 | -0.12414 | -0.12414
Line9_3_11 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.5809e-05 | -1.6666e-05 | 1.6666e-05 | 147.0242 | -32.9758 | 0.89769 | 0.8977 | -0.12431 | -0.12422

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.12004 | 0.27826 | 0.2879 | 0.12004 | 0.27826 | 0.2879 | 0.027723 | 0.06426 | 0.066487 | 0.027723 | 0.06426 | 0.066487 | -0.0066356 | -0.043731 | 0.0053609 | 0.0067797 | 0.044505 | -0.004532 | -0.02942 | -0.038454 | -0.05306 | 0.029708 | 0.040002 | 0.054718 | 103.3755 | 5.6755 | -149.9183 | -76.6245 | -174.3245 | 30.0817 | 1.0879 | 0.9062 | 0.80211 | 1.0992 | 0.93122 | 0.8258 | 0.66504 | -132.9982 | 125.851 | 0.51995 | -132.3743 | 124.8165
Line10_11_12 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0054328 | -0.040559 | 0.0029652 | 0.0055444 | 0.041166 | -0.0022943 | -0.026465 | -0.035746 | -0.050471 | 0.026688 | 0.03696 | 0.051813 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.1076 | 0.95025 | 0.84519 | 1.1175 | 0.9724 | 0.86702 | 0.38687 | -131.8661 | 124.0632 | 0.25148 | -131.3386 | 123.2363
Line11_12_13 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0055444 | -0.041166 | 0.0022943 | 0.0056559 | 0.041773 | -0.0016234 | -0.026688 | -0.03696 | -0.051813 | 0.026911 | 0.038174 | 0.053154 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.1175 | 0.9724 | 0.86702 | 1.1274 | 0.99463 | 0.88902 | 0.25148 | -131.3386 | 123.2363 | 0.11846 | -130.8346 | 122.4502
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5966e-10 | -4.0105e-10 | -1.5649e-09 | -9.5966e-10 | 4.0105e-10 | 1.5649e-09 | -2.6922e-11 | 2.1594e-09 | -4.3897e-10 | 2.6922e-11 | -2.1594e-09 | 4.3897e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1274 | 0.99463 | 0.88902 | 1.1274 | 0.99463 | 0.88902 | 0.11846 | -130.8346 | 122.4502 | 0.11846 | -130.8346 | 122.4502
Line13_13_14 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0056559 | -0.041773 | 0.0016234 | 0.0057675 | 0.04238 | -0.00095251 | -0.026911 | -0.038174 | -0.053154 | 0.027134 | 0.039388 | 0.054496 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.1274 | 0.99463 | 0.88902 | 1.1373 | 1.0169 | 0.91117 | 0.11846 | -130.8346 | 122.4502 | -0.012245 | -130.3527 | 121.7021
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3977e-10 | -2.6737e-10 | -1.0433e-09 | -6.3977e-10 | 2.6737e-10 | 1.0433e-09 | -1.7948e-11 | 1.4396e-09 | -2.9264e-10 | 1.7948e-11 | -1.4396e-09 | 2.9264e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1274 | 0.99463 | 0.88902 | 1.1274 | 0.99463 | 0.88902 | 0.11846 | -130.8346 | 122.4502 | 0.11846 | -130.8346 | 122.4502
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1989e-10 | -1.3368e-10 | -5.2163e-10 | -3.1989e-10 | 1.3368e-10 | 5.2163e-10 | -8.974e-12 | 7.1981e-10 | -1.4632e-10 | 8.9739e-12 | -7.1981e-10 | 1.4632e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1274 | 0.99463 | 0.88902 | 1.1274 | 0.99463 | 0.88902 | 0.11846 | -130.8346 | 122.4502 | 0.11846 | -130.8346 | 122.4502
Line16_4_18 | 0 | 3.6866 | 3.6866 | 0 | 3.6866 | 3.6866 | 0 | 0.85139 | 0.85139 | 0 | 0.85139 | 0.85139 | 2.2277e-10 | 0.58108 | -0.30926 | -2.2277e-10 | -0.44517 | 0.44517 | -6.0249e-11 | 0.12002 | 0.42364 | 6.0249e-11 | 0.15181 | -0.15181 | 0 | -160.3584 | 19.6416 | 0 | 19.6416 | -160.3584 | 1.1049 | 0.69692 | 0.61606 | 1.1049 | 0.55244 | 0.55244 | 0.81154 | -148.6887 | 145.7714 | 0.81154 | -179.1885 | -179.1885
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5131e-10 | -3.884e-10 | -7.1297e-10 | -1.5131e-10 | 3.884e-10 | 7.1297e-10 | -4.8613e-11 | 7.8472e-10 | -3.1481e-10 | 4.8613e-11 | -7.8472e-10 | 3.1481e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0879 | 0.9062 | 0.80211 | 1.0879 | 0.9062 | 0.80211 | 0.66504 | -132.9982 | 125.851 | 0.66504 | -132.9982 | 125.851
Line1_1_3 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0052097 | -0.039345 | 0.0043071 | 0.0053213 | 0.039952 | -0.0036361 | -0.026019 | -0.033319 | -0.047787 | 0.026242 | 0.034532 | 0.049129 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.0879 | 0.9062 | 0.80211 | 1.0977 | 0.92818 | 0.82355 | 0.66504 | -132.9982 | 125.851 | 0.5247 | -132.4187 | 124.9337
Line2_1_4 | 0.17814 | 3.1133 | 3.1623 | 0.17814 | 3.1133 | 3.1623 | 0.041139 | 0.71898 | 0.7303 | 0.041139 | 0.71898 | 0.7303 | -0.026301 | 0.59177 | -0.16845 | 0.026618 | -0.49484 | 0.26845 | -0.03621 | 0.27262 | 0.56104 | 0.036845 | -0.078773 | -0.36104 | 126.6571 | -157.7336 | 19.1385 | -53.3429 | 22.2664 | -160.8615 | 1.0879 | 0.9062 | 0.80211 | 1.1049 | 0.69692 | 0.61606 | 0.66504 | -132.9982 | 125.851 | 0.81154 | -148.6887 | 145.7714
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0262e-10 | -7.7681e-10 | -1.4259e-09 | -3.0262e-10 | 7.7681e-10 | 1.4259e-09 | -9.7225e-11 | 1.5694e-09 | -6.2962e-10 | 9.7225e-11 | -1.5694e-09 | 6.2962e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0879 | 0.9062 | 0.80211 | 1.0879 | 0.9062 | 0.80211 | 0.66504 | -132.9982 | 125.851 | 0.66504 | -132.9982 | 125.851
Line4_2_6 | 0.12004 | 0.27826 | 0.2879 | 0.12004 | 0.27826 | 0.2879 | 0.027723 | 0.06426 | 0.066487 | 0.027723 | 0.06426 | 0.066487 | -0.0067797 | -0.044505 | 0.004532 | 0.0069238 | 0.045279 | -0.0037032 | -0.029708 | -0.040002 | -0.054718 | 0.029996 | 0.041551 | 0.056376 | 103.3755 | 5.6755 | -149.9183 | -76.6245 | -174.3245 | 30.0817 | 1.0992 | 0.93122 | 0.8258 | 1.1104 | 0.95634 | 0.84974 | 0.51995 | -132.3743 | 124.8165 | 0.37782 | -131.7831 | 123.8399
Line5_6_7 | 0.12004 | 0.27826 | 0.2879 | 0.12004 | 0.27826 | 0.2879 | 0.027723 | 0.06426 | 0.066487 | 0.027723 | 0.06426 | 0.066487 | -0.0069238 | -0.045279 | 0.0037032 | 0.0070679 | 0.046053 | -0.0028743 | -0.029996 | -0.041551 | -0.056376 | 0.030284 | 0.0431 | 0.058033 | 103.3755 | 5.6754 | -149.9183 | -76.6245 | -174.3246 | 30.0817 | 1.1104 | 0.95634 | 0.84974 | 1.1217 | 0.98156 | 0.87392 | 0.37782 | -131.7831 | 123.8399 | 0.23855 | -131.2223 | 122.9172
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8544e-10 | -5.2221e-10 | -1.6796e-09 | -8.8544e-10 | 5.2221e-10 | 1.6796e-09 | -5.3942e-11 | 2.2064e-09 | -5.137e-10 | 5.3942e-11 | -2.2064e-09 | 5.137e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1217 | 0.98156 | 0.87392 | 1.1217 | 0.98156 | 0.87392 | 0.23855 | -131.2223 | 122.9172 | 0.23855 | -131.2223 | 122.9172
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9515e-10 | -1.7407e-10 | -5.5987e-10 | -2.9515e-10 | 1.7407e-10 | 5.5987e-10 | -1.7981e-11 | 7.3545e-10 | -1.7123e-10 | 1.7981e-11 | -7.3545e-10 | 1.7123e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1217 | 0.98156 | 0.87392 | 1.1217 | 0.98156 | 0.87392 | 0.23855 | -131.2223 | 122.9172 | 0.23855 | -131.2223 | 122.9172
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9515e-10 | -1.7407e-10 | -5.5987e-10 | -2.9515e-10 | 1.7407e-10 | 5.5987e-10 | -1.7981e-11 | 7.3545e-10 | -1.7123e-10 | 1.7981e-11 | -7.3545e-10 | 1.7123e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1217 | 0.98156 | 0.87392 | 1.1217 | 0.98156 | 0.87392 | 0.23855 | -131.2223 | 122.9172 | 0.23855 | -131.2223 | 122.9172
Line9_3_11 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0053213 | -0.039952 | 0.0036361 | 0.0054328 | 0.040559 | -0.0029652 | -0.026242 | -0.034532 | -0.049129 | 0.026465 | 0.035746 | 0.050471 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.0977 | 0.92818 | 0.82355 | 1.1076 | 0.95025 | 0.84519 | 0.5247 | -132.4187 | 124.9337 | 0.38687 | -131.8661 | 124.0632

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.12125 | 0.28676 | 0.29545 | 0.12125 | 0.28676 | 0.29545 | 0.028001 | 0.066224 | 0.068232 | 0.028001 | 0.066224 | 0.068232 | -0.0072796 | -0.047408 | 0.0062354 | 0.0074266 | 0.04823 | -0.0053624 | -0.031079 | -0.040686 | -0.056392 | 0.031373 | 0.04233 | 0.058138 | 103.86 | 5.8931 | -150.127 | -76.14 | -174.1069 | 29.873 | 1.14 | 0.94335 | 0.8315 | 1.1514 | 0.969 | 0.85567 | 0.67744 | -133.4704 | 126.1827 | 0.54223 | -132.8342 | 125.1429
Line10_11_12 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0059982 | -0.044121 | 0.0036669 | 0.0061128 | 0.044772 | -0.0029546 | -0.028047 | -0.038002 | -0.053845 | 0.028276 | 0.039303 | 0.05527 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.16 | 0.98872 | 0.87564 | 1.1701 | 1.0115 | 0.89801 | 0.41665 | -132.313 | 124.377 | 0.28961 | -131.7733 | 123.5412
Line11_12_13 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0061128 | -0.044772 | 0.0029546 | 0.0062274 | 0.045422 | -0.0022423 | -0.028276 | -0.039303 | -0.05527 | 0.028506 | 0.040604 | 0.056694 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.1701 | 1.0115 | 0.89801 | 1.1801 | 1.0345 | 0.92056 | 0.28961 | -131.7733 | 123.5412 | 0.16473 | -131.2575 | 122.7461
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0401e-09 | -5.0503e-10 | -1.8042e-09 | -1.0401e-09 | 5.0503e-10 | 1.8042e-09 | -4.1056e-11 | 2.4435e-09 | -5.3366e-10 | 4.1055e-11 | -2.4435e-09 | 5.3366e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1801 | 1.0345 | 0.92056 | 1.1801 | 1.0345 | 0.92056 | 0.16473 | -131.2575 | 122.7461 | 0.16473 | -131.2575 | 122.7461
Line13_13_14 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0062274 | -0.045422 | 0.0022423 | 0.006342 | 0.046072 | -0.00153 | -0.028506 | -0.040604 | -0.056694 | 0.028735 | 0.041904 | 0.058119 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.1801 | 1.0345 | 0.92056 | 1.1902 | 1.0574 | 0.94328 | 0.16473 | -131.2575 | 122.7461 | 0.041965 | -130.7641 | 121.9892
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9337e-10 | -3.3669e-10 | -1.2028e-09 | -6.9337e-10 | 3.3669e-10 | 1.2028e-09 | -2.737e-11 | 1.629e-09 | -3.5577e-10 | 2.737e-11 | -1.629e-09 | 3.5577e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1801 | 1.0345 | 0.92056 | 1.1801 | 1.0345 | 0.92056 | 0.16473 | -131.2575 | 122.7461 | 0.16473 | -131.2575 | 122.7461
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4669e-10 | -1.6834e-10 | -6.0141e-10 | -3.4669e-10 | 1.6834e-10 | 6.0141e-10 | -1.3685e-11 | 8.1451e-10 | -1.7789e-10 | 1.3685e-11 | -8.1451e-10 | 1.7789e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1801 | 1.0345 | 0.92056 | 1.1801 | 1.0345 | 0.92056 | 0.16473 | -131.2575 | 122.7461 | 0.16473 | -131.2575 | 122.7461
Line16_4_18 | 0 | 3.8016 | 3.8016 | 0 | 3.8016 | 3.8016 | 0 | 0.87794 | 0.87794 | 0 | 0.87794 | 0.87794 | 2.4252e-10 | 0.6258 | -0.33676 | -2.4252e-10 | -0.48128 | 0.48128 | -6.6499e-11 | 0.12673 | 0.45136 | 6.6499e-11 | 0.16231 | -0.16231 | 0 | -160.5465 | 19.4535 | 0 | 19.4535 | -160.5465 | 1.1571 | 0.72727 | 0.64143 | 1.1571 | 0.57853 | 0.57853 | 0.81646 | -149.0986 | 146.1801 | 0.81646 | -179.1835 | -179.1835
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.674e-10 | -4.3718e-10 | -7.991e-10 | -1.674e-10 | 4.3718e-10 | 7.991e-10 | -5.4362e-11 | 8.8631e-10 | -3.6119e-10 | 5.4362e-11 | -8.8631e-10 | 3.6119e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 0.94335 | 0.8315 | 1.14 | 0.94335 | 0.8315 | 0.67744 | -133.4704 | 126.1827 | 0.67744 | -133.4704 | 126.1827
Line1_1_3 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0057689 | -0.042821 | 0.0050915 | 0.0058836 | 0.043471 | -0.0043792 | -0.027589 | -0.035401 | -0.050996 | 0.027818 | 0.036701 | 0.052421 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.14 | 0.94335 | 0.8315 | 1.15 | 0.96598 | 0.85346 | 0.67744 | -133.4704 | 126.1827 | 0.54591 | -132.8781 | 125.2565
Line2_1_4 | 0.17875 | 3.2235 | 3.2732 | 0.17875 | 3.2235 | 3.2732 | 0.04128 | 0.74444 | 0.7559 | 0.04128 | 0.74444 | 0.7559 | -0.027594 | 0.63877 | -0.18623 | 0.027913 | -0.53486 | 0.29337 | -0.038119 | 0.29181 | 0.60031 | 0.038758 | -0.083991 | -0.38604 | 126.5778 | -158.0231 | 18.9477 | -53.4222 | 21.9769 | -161.0523 | 1.14 | 0.94335 | 0.8315 | 1.1571 | 0.72727 | 0.64143 | 0.67744 | -133.4704 | 126.1827 | 0.81646 | -149.0986 | 146.1801
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3479e-10 | -8.7436e-10 | -1.5982e-09 | -3.3479e-10 | 8.7436e-10 | 1.5982e-09 | -1.0872e-10 | 1.7726e-09 | -7.2239e-10 | 1.0872e-10 | -1.7726e-09 | 7.2239e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 0.94335 | 0.8315 | 1.14 | 0.94335 | 0.8315 | 0.67744 | -133.4704 | 126.1827 | 0.67744 | -133.4704 | 126.1827
Line4_2_6 | 0.12125 | 0.28676 | 0.29545 | 0.12125 | 0.28676 | 0.29545 | 0.028001 | 0.066224 | 0.068232 | 0.028001 | 0.066224 | 0.068232 | -0.0074266 | -0.04823 | 0.0053624 | 0.0075736 | 0.049052 | -0.0044895 | -0.031373 | -0.04233 | -0.058138 | 0.031667 | 0.043975 | 0.059883 | 103.86 | 5.8931 | -150.127 | -76.14 | -174.1069 | 29.873 | 1.1514 | 0.969 | 0.85567 | 1.1628 | 0.99477 | 0.8801 | 0.54223 | -132.8342 | 125.1429 | 0.40967 | -132.2309 | 124.1605
Line5_6_7 | 0.12125 | 0.28676 | 0.29545 | 0.12125 | 0.28676 | 0.29545 | 0.028001 | 0.066224 | 0.068232 | 0.028001 | 0.066224 | 0.068232 | -0.0075736 | -0.049052 | 0.0044895 | 0.0077206 | 0.049874 | -0.0036166 | -0.031667 | -0.043975 | -0.059883 | 0.031961 | 0.045619 | 0.061629 | 103.86 | 5.8931 | -150.127 | -76.14 | -174.1069 | 29.873 | 1.1628 | 0.99477 | 0.8801 | 1.1743 | 1.0206 | 0.90478 | 0.40967 | -132.2309 | 124.1605 | 0.2797 | -131.6582 | 123.2314
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5941e-10 | -6.3614e-10 | -1.9255e-09 | -9.5941e-10 | 6.3614e-10 | 1.9255e-09 | -6.9362e-11 | 2.4956e-09 | -6.1712e-10 | 6.9362e-11 | -2.4956e-09 | 6.1712e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1743 | 1.0206 | 0.90478 | 1.1743 | 1.0206 | 0.90478 | 0.2797 | -131.6582 | 123.2314 | 0.2797 | -131.6582 | 123.2314
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.198e-10 | -2.1205e-10 | -6.4184e-10 | -3.198e-10 | 2.1205e-10 | 6.4184e-10 | -2.3121e-11 | 8.3185e-10 | -2.0571e-10 | 2.312e-11 | -8.3185e-10 | 2.0571e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1743 | 1.0206 | 0.90478 | 1.1743 | 1.0206 | 0.90478 | 0.2797 | -131.6582 | 123.2314 | 0.2797 | -131.6582 | 123.2314
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.198e-10 | -2.1205e-10 | -6.4184e-10 | -3.198e-10 | 2.1205e-10 | 6.4184e-10 | -2.3121e-11 | 8.3185e-10 | -2.0571e-10 | 2.3121e-11 | -8.3185e-10 | 2.0571e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1743 | 1.0206 | 0.90478 | 1.1743 | 1.0206 | 0.90478 | 0.2797 | -131.6582 | 123.2314 | 0.2797 | -131.6582 | 123.2314
Line9_3_11 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0058836 | -0.043471 | 0.0043792 | 0.0059982 | 0.044121 | -0.0036669 | -0.027818 | -0.036701 | -0.052421 | 0.028047 | 0.038002 | 0.053845 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.15 | 0.96598 | 0.85346 | 1.16 | 0.98872 | 0.87564 | 0.54591 | -132.8781 | 125.2565 | 0.41665 | -132.313 | 124.377

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11916 | 0.12006 | 0.12197 | 0.11916 | 0.12006 | 0.12197 | 0.027519 | 0.027727 | 0.028168 | 0.027519 | 0.027727 | 0.028168 | -0.0017278 | -0.0025535 | -0.0019426 | 0.0018698 | 0.0026977 | 0.0020913 | -0.029835 | -0.029959 | -0.030392 | 0.030119 | 0.030247 | 0.03069 | 93.44 | -25.2506 | -146.2691 | -86.56 | 154.7494 | 33.7309 | 1.086 | 1.0844 | 1.0812 | 1.0966 | 1.0952 | 1.092 | 0.12554 | -120.1223 | 120.0737 | -0.11242 | -120.3471 | 119.8325
Line10_11_12 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.00168 | -0.0024342 | -0.0019093 | 0.0017928 | 0.0025486 | 0.0020275 | -0.027055 | -0.027149 | -0.027575 | 0.027281 | 0.027378 | 0.027811 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.1049 | 1.1037 | 1.1006 | 1.1144 | 1.1133 | 1.1103 | -0.29874 | -120.5223 | 119.6447 | -0.50548 | -120.7171 | 119.4358
Line11_12_13 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.0017928 | -0.0025486 | -0.0020275 | 0.0019057 | 0.002663 | 0.0021458 | -0.027281 | -0.027378 | -0.027811 | 0.027506 | 0.027607 | 0.028048 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.1144 | 1.1133 | 1.1103 | 1.1239 | 1.123 | 1.12 | -0.50548 | -120.7171 | 119.4358 | -0.70873 | -120.9085 | 119.2306
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1428e-10 | 9.0327e-10 | 8.6406e-10 | -9.1428e-10 | -9.0327e-10 | -8.6406e-10 | 1.6056e-10 | 2.0566e-10 | 1.7371e-10 | -1.6056e-10 | -2.0566e-10 | -1.7371e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1239 | 1.123 | 1.12 | 1.1239 | 1.123 | 1.12 | -0.70873 | -120.9085 | 119.2306 | -0.70873 | -120.9085 | 119.2306
Line13_13_14 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.0019057 | -0.002663 | -0.0021458 | 0.0020185 | 0.0027774 | 0.0022641 | -0.027506 | -0.027607 | -0.028048 | 0.027732 | 0.027836 | 0.028285 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.1239 | 1.123 | 1.12 | 1.1334 | 1.1327 | 1.1298 | -0.70873 | -120.9085 | 119.2306 | -0.90857 | -121.0967 | 119.0289
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0952e-10 | 6.0218e-10 | 5.7604e-10 | -6.0952e-10 | -6.0218e-10 | -5.7604e-10 | 1.0704e-10 | 1.3711e-10 | 1.1581e-10 | -1.0704e-10 | -1.3711e-10 | -1.1581e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1239 | 1.123 | 1.12 | 1.1239 | 1.123 | 1.12 | -0.70873 | -120.9085 | 119.2306 | -0.70873 | -120.9085 | 119.2306
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0476e-10 | 3.0109e-10 | 2.8802e-10 | -3.0476e-10 | -3.0109e-10 | -2.8802e-10 | 5.3521e-11 | 6.8554e-11 | 5.7904e-11 | -5.3521e-11 | -6.8554e-11 | -5.7904e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1239 | 1.123 | 1.12 | 1.1239 | 1.123 | 1.12 | -0.70873 | -120.9085 | 119.2306 | -0.70873 | -120.9085 | 119.2306
Line16_4_18 | 0 | 0.06123 | 0.06123 | 0 | 0.06123 | 0.06123 | 0 | 0.01414 | 0.01414 | 0 | 0.01414 | 0.01414 | 1.9703e-10 | 0.014944 | 0.0038761 | -1.9703e-10 | -0.014907 | -0.0038386 | -1.0652e-12 | 0.0039945 | 0.014901 | 1.0651e-12 | -0.0039195 | -0.014826 | 0 | -135.4076 | 44.5924 | 0 | 44.5924 | -135.4076 | 1.0989 | 1.094 | 1.0888 | 1.0989 | 1.09 | 1.0831 | 0.014424 | -120.4428 | 120.0116 | 0.014424 | -120.6761 | 120.0768
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4339e-10 | 1.3695e-10 | 1.2351e-10 | -1.4339e-10 | -1.3695e-10 | -1.2351e-10 | -9.1614e-12 | 8.9118e-12 | -5.3514e-12 | 9.1614e-12 | -8.9118e-12 | 5.3514e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.086 | 1.0844 | 1.0812 | 1.086 | 1.0844 | 1.0812 | 0.12554 | -120.1223 | 120.0737 | 0.12554 | -120.1223 | 120.0737
Line1_1_3 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.0014543 | -0.0022055 | -0.0016727 | 0.0015671 | 0.0023199 | 0.001791 | -0.026604 | -0.026692 | -0.027102 | 0.026829 | 0.026921 | 0.027338 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.086 | 1.0844 | 1.0812 | 1.0955 | 1.0941 | 1.0909 | 0.12554 | -120.1223 | 120.0737 | -0.08843 | -120.324 | 119.8573
Line2_1_4 | 0.13494 | 0.1167 | 0.080388 | 0.13494 | 0.1167 | 0.080388 | 0.031163 | 0.026951 | 0.018565 | 0.031163 | 0.026951 | 0.018565 | -0.0099948 | 0.0031674 | -0.0061539 | 0.010177 | -0.0030312 | 0.0062186 | -0.032333 | -0.029054 | -0.019105 | 0.032698 | 0.029326 | 0.019234 | 107.3028 | -36.344 | -132.0717 | -72.6972 | 143.656 | 47.9283 | 1.086 | 1.0844 | 1.0812 | 1.0989 | 1.094 | 1.0888 | 0.12554 | -120.1223 | 120.0737 | 0.014424 | -120.4428 | 120.0116
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8677e-10 | 2.7389e-10 | 2.4702e-10 | -2.8677e-10 | -2.7389e-10 | -2.4702e-10 | -1.8323e-11 | 1.7824e-11 | -1.0703e-11 | 1.8323e-11 | -1.7824e-11 | 1.0703e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.086 | 1.0844 | 1.0812 | 1.086 | 1.0844 | 1.0812 | 0.12554 | -120.1223 | 120.0737 | 0.12554 | -120.1223 | 120.0737
Line4_2_6 | 0.11916 | 0.12006 | 0.12197 | 0.11916 | 0.12006 | 0.12197 | 0.027519 | 0.027727 | 0.028168 | 0.027519 | 0.027727 | 0.028168 | -0.0018698 | -0.0026977 | -0.0020913 | 0.0020118 | 0.0028418 | 0.0022401 | -0.030119 | -0.030247 | -0.03069 | 0.030403 | 0.030536 | 0.030987 | 93.44 | -25.2506 | -146.2691 | -86.56 | 154.7494 | 33.7309 | 1.0966 | 1.0952 | 1.092 | 1.1072 | 1.1061 | 1.103 | -0.11242 | -120.3471 | 119.8325 | -0.34582 | -120.5675 | 119.596
Line5_6_7 | 0.11916 | 0.12006 | 0.12197 | 0.11916 | 0.12006 | 0.12197 | 0.027519 | 0.027727 | 0.028168 | 0.027519 | 0.027727 | 0.028168 | -0.0020118 | -0.0028418 | -0.0022401 | 0.0021538 | 0.0029859 | 0.0023889 | -0.030403 | -0.030536 | -0.030987 | 0.030687 | 0.030824 | 0.031285 | 93.44 | -25.2506 | -146.2691 | -86.56 | 154.7494 | 33.7309 | 1.1072 | 1.1061 | 1.103 | 1.1179 | 1.1169 | 1.1139 | -0.34582 | -120.5675 | 119.596 | -0.57478 | -120.7836 | 119.3643
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3549e-10 | 8.2335e-10 | 7.8344e-10 | -8.3549e-10 | -8.2335e-10 | -7.8344e-10 | 1.2952e-10 | 1.7642e-10 | 1.4275e-10 | -1.2952e-10 | -1.7642e-10 | -1.4275e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.1169 | 1.1139 | 1.1179 | 1.1169 | 1.1139 | -0.57478 | -120.7836 | 119.3643 | -0.57478 | -120.7836 | 119.3643
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.785e-10 | 2.7445e-10 | 2.6115e-10 | -2.785e-10 | -2.7445e-10 | -2.6115e-10 | 4.3175e-11 | 5.8808e-11 | 4.7582e-11 | -4.3175e-11 | -5.8808e-11 | -4.7582e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.1169 | 1.1139 | 1.1179 | 1.1169 | 1.1139 | -0.57478 | -120.7836 | 119.3643 | -0.57478 | -120.7836 | 119.3643
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.785e-10 | 2.7445e-10 | 2.6115e-10 | -2.785e-10 | -2.7445e-10 | -2.6115e-10 | 4.3175e-11 | 5.8808e-11 | 4.7582e-11 | -4.3175e-11 | -5.8808e-11 | -4.7582e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.1169 | 1.1139 | 1.1179 | 1.1169 | 1.1139 | -0.57478 | -120.7836 | 119.3643 | -0.57478 | -120.7836 | 119.3643
Line9_3_11 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.0015671 | -0.0023199 | -0.001791 | 0.00168 | 0.0024342 | 0.0019093 | -0.026829 | -0.026921 | -0.027338 | 0.027055 | 0.027149 | 0.027575 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.0955 | 1.0941 | 1.0909 | 1.1049 | 1.1037 | 1.1006 | -0.08843 | -120.324 | 119.8573 | -0.29874 | -120.5223 | 119.6447

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11999 | 0.12096 | 0.12297 | 0.11999 | 0.12096 | 0.12297 | 0.027711 | 0.027934 | 0.028398 | 0.027711 | 0.027934 | 0.028398 | -0.0018547 | -0.0027674 | -0.0020891 | 0.0019987 | 0.0029137 | 0.0022403 | -0.03148 | -0.031619 | -0.032096 | 0.031768 | 0.031912 | 0.032399 | 93.4956 | -25.1341 | -146.2064 | -86.5044 | 154.8659 | 33.7936 | 1.138 | 1.1362 | 1.1326 | 1.1486 | 1.1471 | 1.1436 | 0.12371 | -120.136 | 120.0696 | -0.10453 | -120.351 | 119.838
Line10_11_12 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0018008 | -0.0026377 | -0.0020514 | 0.0019162 | 0.0027547 | 0.0021726 | -0.028646 | -0.028754 | -0.029224 | 0.028877 | 0.028988 | 0.029466 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.1571 | 1.1557 | 1.1523 | 1.1667 | 1.1655 | 1.1621 | -0.28496 | -120.5202 | 119.656 | -0.48427 | -120.7074 | 119.4545
Line11_12_13 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0019162 | -0.0027547 | -0.0021726 | 0.0020316 | 0.0028718 | 0.0022938 | -0.028877 | -0.028988 | -0.029466 | 0.029108 | 0.029222 | 0.029708 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.1667 | 1.1655 | 1.1621 | 1.1763 | 1.1753 | 1.172 | -0.48427 | -120.7074 | 119.4545 | -0.68033 | -120.8916 | 119.2563
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8776e-10 | 9.7474e-10 | 9.2953e-10 | -9.8776e-10 | -9.7474e-10 | -9.2953e-10 | 1.6899e-10 | 2.2128e-10 | 1.8406e-10 | -1.69e-10 | -2.2128e-10 | -1.8406e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1763 | 1.1753 | 1.172 | 1.1763 | 1.1753 | 1.172 | -0.68033 | -120.8916 | 119.2563 | -0.68033 | -120.8916 | 119.2563
Line13_13_14 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0020316 | -0.0028718 | -0.0022938 | 0.002147 | 0.0029888 | 0.002415 | -0.029108 | -0.029222 | -0.029708 | 0.029338 | 0.029456 | 0.029951 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.1763 | 1.1753 | 1.172 | 1.1859 | 1.1851 | 1.1819 | -0.68033 | -120.8916 | 119.2563 | -0.87321 | -121.0727 | 119.0615
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.585e-10 | 6.4983e-10 | 6.1968e-10 | -6.585e-10 | -6.4983e-10 | -6.1968e-10 | 1.1266e-10 | 1.4752e-10 | 1.2271e-10 | -1.1266e-10 | -1.4752e-10 | -1.2271e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1763 | 1.1753 | 1.172 | 1.1763 | 1.1753 | 1.172 | -0.68033 | -120.8916 | 119.2563 | -0.68033 | -120.8916 | 119.2563
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2925e-10 | 3.2491e-10 | 3.0984e-10 | -3.2925e-10 | -3.2491e-10 | -3.0984e-10 | 5.6332e-11 | 7.3759e-11 | 6.1353e-11 | -5.6332e-11 | -7.3759e-11 | -6.1353e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1763 | 1.1753 | 1.172 | 1.1763 | 1.1753 | 1.172 | -0.68033 | -120.8916 | 119.2563 | -0.68033 | -120.8916 | 119.2563
Line16_4_18 | 0 | 0.064112 | 0.064112 | 0 | 0.064112 | 0.064112 | 0 | 0.014806 | 0.014806 | 0 | 0.014806 | 0.014806 | 2.1466e-10 | 0.016387 | 0.0042473 | -2.1466e-10 | -0.016346 | -0.0042062 | -1.1899e-12 | 0.0043792 | 0.016337 | 1.1899e-12 | -0.0042969 | -0.016255 | 0 | -135.4167 | 44.5833 | 0 | 44.5833 | -135.4167 | 1.1509 | 1.1456 | 1.1401 | 1.1509 | 1.1415 | 1.134 | 0.014686 | -120.4547 | 120.0101 | 0.014686 | -120.688 | 120.0753
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.584e-10 | 1.5097e-10 | 1.3552e-10 | -1.584e-10 | -1.5097e-10 | -1.3552e-10 | -9.9101e-12 | 1.0879e-11 | -5.547e-12 | 9.9101e-12 | -1.0879e-11 | 5.547e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.138 | 1.1362 | 1.1326 | 1.138 | 1.1362 | 1.1326 | 0.12371 | -120.136 | 120.0696 | 0.12371 | -120.136 | 120.0696
Line1_1_3 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0015701 | -0.0024036 | -0.001809 | 0.0016855 | 0.0025207 | 0.0019302 | -0.028185 | -0.028286 | -0.028739 | 0.028415 | 0.02852 | 0.028981 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.138 | 1.1362 | 1.1326 | 1.1475 | 1.146 | 1.1425 | 0.12371 | -120.136 | 120.0696 | -0.082328 | -120.3297 | 119.861
Line2_1_4 | 0.1352 | 0.11679 | 0.077932 | 0.1352 | 0.11679 | 0.077932 | 0.031223 | 0.026972 | 0.017998 | 0.031223 | 0.026972 | 0.017998 | -0.010349 | 0.0041229 | -0.006144 | 0.010532 | -0.0039865 | 0.0062047 | -0.03399 | -0.030368 | -0.019437 | 0.034355 | 0.03064 | 0.019558 | 107.0584 | -37.8676 | -132.3885 | -72.9416 | 142.1324 | 47.6115 | 1.138 | 1.1362 | 1.1326 | 1.1509 | 1.1456 | 1.1401 | 0.12371 | -120.136 | 120.0696 | 0.014686 | -120.4547 | 120.0101
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.168e-10 | 3.0194e-10 | 2.7104e-10 | -3.168e-10 | -3.0194e-10 | -2.7104e-10 | -1.982e-11 | 2.1759e-11 | -1.1094e-11 | 1.982e-11 | -2.1759e-11 | 1.1094e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.138 | 1.1362 | 1.1326 | 1.138 | 1.1362 | 1.1326 | 0.12371 | -120.136 | 120.0696 | 0.12371 | -120.136 | 120.0696
Line4_2_6 | 0.11999 | 0.12096 | 0.12297 | 0.11999 | 0.12096 | 0.12297 | 0.027711 | 0.027934 | 0.028398 | 0.027711 | 0.027934 | 0.028398 | -0.0019987 | -0.0029137 | -0.0022403 | 0.0021427 | 0.00306 | 0.0023915 | -0.031768 | -0.031912 | -0.032399 | 0.032055 | 0.032204 | 0.032701 | 93.4956 | -25.1341 | -146.2064 | -86.5044 | 154.8659 | 33.7936 | 1.1486 | 1.1471 | 1.1436 | 1.1594 | 1.1581 | 1.1546 | -0.10453 | -120.351 | 119.838 | -0.32855 | -120.5619 | 119.6109
Line5_6_7 | 0.11999 | 0.12096 | 0.12297 | 0.11999 | 0.12096 | 0.12297 | 0.027711 | 0.027934 | 0.028398 | 0.027711 | 0.027934 | 0.028398 | -0.0021427 | -0.00306 | -0.0023915 | 0.0022867 | 0.0032063 | 0.0025427 | -0.032055 | -0.032204 | -0.032701 | 0.032343 | 0.032497 | 0.033003 | 93.4956 | -25.1341 | -146.2064 | -86.5044 | 154.8659 | 33.7936 | 1.1594 | 1.1581 | 1.1546 | 1.1701 | 1.169 | 1.1656 | -0.32855 | -120.5619 | 119.6109 | -0.54848 | -120.7689 | 119.388
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0263e-10 | 8.883e-10 | 8.4233e-10 | -9.0263e-10 | -8.883e-10 | -8.4233e-10 | 1.3553e-10 | 1.8983e-10 | 1.5064e-10 | -1.3553e-10 | -1.8983e-10 | -1.5064e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1701 | 1.169 | 1.1656 | 1.1701 | 1.169 | 1.1656 | -0.54848 | -120.7689 | 119.388 | -0.54848 | -120.7689 | 119.388
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0088e-10 | 2.961e-10 | 2.8078e-10 | -3.0088e-10 | -2.961e-10 | -2.8078e-10 | 4.5176e-11 | 6.3275e-11 | 5.0214e-11 | -4.5176e-11 | -6.3275e-11 | -5.0214e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1701 | 1.169 | 1.1656 | 1.1701 | 1.169 | 1.1656 | -0.54848 | -120.7689 | 119.388 | -0.54848 | -120.7689 | 119.388
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0088e-10 | 2.961e-10 | 2.8078e-10 | -3.0088e-10 | -2.961e-10 | -2.8078e-10 | 4.5176e-11 | 6.3275e-11 | 5.0214e-11 | -4.5176e-11 | -6.3275e-11 | -5.0214e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1701 | 1.169 | 1.1656 | 1.1701 | 1.169 | 1.1656 | -0.54848 | -120.7689 | 119.388 | -0.54848 | -120.7689 | 119.388
Line9_3_11 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0016855 | -0.0025207 | -0.0019302 | 0.0018008 | 0.0026377 | 0.0020514 | -0.028415 | -0.02852 | -0.028981 | 0.028646 | 0.028754 | 0.029224 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.1475 | 1.146 | 1.1425 | 1.1571 | 1.1557 | 1.1523 | -0.082328 | -120.3297 | 119.861 | -0.28496 | -120.5202 | 119.656

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00073134 | 0.0043194 | 0.0036537 | 0.00073134 | 0.0043194 | 0.0036537 | 0.0001689 | 0.00099752 | 0.00084379 | 0.0001689 | 0.00099752 | 0.00084379 | -0.00015686 | -0.00082368 | -8.0449e-05 | 0.00015687 | 0.00082404 | 8.0705e-05 | 3.3794e-05 | -0.00014813 | -0.00057528 | -3.3783e-05 | 0.00014851 | 0.00057555 | -167.8235 | 34.5522 | -141.0778 | 12.1765 | -145.4478 | 38.9222 | 0.95002 | 0.83898 | 0.68841 | 0.95006 | 0.8394 | 0.68877 | 0.018327 | -135.2526 | 120.9615 | 0.022833 | -135.2318 | 120.9401
Line10_11_12 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.00015579 | -0.00082213 | -8.1681e-05 | 0.0001558 | 0.00082249 | 8.1936e-05 | 3.422e-05 | -0.00014656 | -0.00057406 | -3.4209e-05 | 0.00014693 | 0.00057433 | -167.5846 | 34.6813 | -140.983 | 12.4154 | -145.3187 | 39.017 | 0.95011 | 0.83981 | 0.68912 | 0.95015 | 0.84023 | 0.68948 | 0.027308 | -135.211 | 120.919 | 0.031798 | -135.1903 | 120.8977
Line11_12_13 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.0001558 | -0.00082249 | -8.1935e-05 | 0.00015581 | 0.00082284 | 8.219e-05 | 3.4209e-05 | -0.00014693 | -0.00057432 | -3.4198e-05 | 0.0001473 | 0.00057459 | -167.5846 | 34.6812 | -140.9831 | 12.4154 | -145.3188 | 39.0169 | 0.95015 | 0.84023 | 0.68948 | 0.9502 | 0.84065 | 0.68983 | 0.031798 | -135.1903 | 120.8977 | 0.036287 | -135.1696 | 120.8765
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0919e-12 | -7.0508e-10 | -1.9734e-09 | -2.0919e-12 | 7.0508e-10 | 1.9734e-09 | -6.2887e-12 | 2.2988e-09 | -1.1028e-10 | 6.2887e-12 | -2.2988e-09 | 1.1028e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9502 | 0.84065 | 0.68983 | 0.9502 | 0.84065 | 0.68983 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line13_13_14 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.00015581 | -0.00082284 | -8.2187e-05 | 0.00015582 | 0.0008232 | 8.2442e-05 | 3.4198e-05 | -0.0001473 | -0.00057459 | -3.4188e-05 | 0.00014767 | 0.00057486 | -167.5846 | 34.681 | -140.9833 | 12.4154 | -145.319 | 39.0167 | 0.9502 | 0.84065 | 0.68983 | 0.95025 | 0.84107 | 0.69019 | 0.036287 | -135.1696 | 120.8765 | 0.040776 | -135.1488 | 120.8553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3946e-12 | -4.7005e-10 | -1.3156e-09 | -1.3946e-12 | 4.7005e-10 | 1.3156e-09 | -4.1924e-12 | 1.5325e-09 | -7.3518e-11 | 4.1924e-12 | -1.5325e-09 | 7.3518e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9502 | 0.84065 | 0.68983 | 0.9502 | 0.84065 | 0.68983 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9728e-13 | -2.3503e-10 | -6.5778e-10 | -6.9729e-13 | 2.3503e-10 | 6.5778e-10 | -2.0962e-12 | 7.6626e-10 | -3.6759e-11 | 2.0962e-12 | -7.6626e-10 | 3.6759e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9502 | 0.84065 | 0.68983 | 0.9502 | 0.84065 | 0.68983 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line16_4_18 | 0 | 2.5141 | 2.5141 | 0 | 2.5141 | 2.5141 | 0 | 0.58062 | 0.58062 | 0 | 0.58062 | 0.58062 | 5.6281e-13 | 0.35474 | -0.11202 | -5.6281e-13 | -0.23338 | 0.23338 | -1.4359e-12 | -0.020622 | 0.27346 | 1.436e-12 | 0.14704 | -0.14704 | 0 | -147.7624 | 32.2376 | 0 | 32.2376 | -147.7624 | 0.95016 | 0.61201 | 0.50896 | 0.95016 | 0.47508 | 0.47508 | 0.024856 | -151.0894 | 144.5135 | 0.024856 | -179.9751 | -179.9751
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2304e-14 | -2.3859e-10 | -6.5996e-10 | -6.2322e-14 | 2.3859e-10 | 6.5996e-10 | -1.0585e-12 | 7.6882e-10 | -4.0238e-11 | 1.0585e-12 | -7.6882e-10 | 4.0238e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95002 | 0.83898 | 0.68841 | 0.95002 | 0.83898 | 0.68841 | 0.018327 | -135.2526 | 120.9615 | 0.018327 | -135.2526 | 120.9615
Line1_1_3 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.00015577 | -0.00082142 | -8.1172e-05 | 0.00015578 | 0.00082178 | 8.1427e-05 | 3.4241e-05 | -0.00014581 | -0.00057353 | -3.423e-05 | 0.00014619 | 0.00057379 | -167.5846 | 34.6814 | -140.9829 | 12.4154 | -145.3186 | 39.0171 | 0.95002 | 0.83898 | 0.68841 | 0.95006 | 0.8394 | 0.68877 | 0.018327 | -135.2526 | 120.9615 | 0.022818 | -135.2318 | 120.9402
Line2_1_4 | 0.0014981 | 2.5058 | 2.5069 | 0.0014981 | 2.5058 | 2.5069 | 0.00034597 | 0.57869 | 0.57895 | 0.00034597 | 0.57869 | 0.57895 | -0.00032449 | 0.4741 | 0.0091695 | 0.00032454 | -0.35354 | 0.1115 | -5.2275e-05 | 0.10463 | 0.39845 | 5.232e-05 | 0.020954 | -0.27276 | 170.8668 | -147.6976 | 32.2798 | -9.1332 | 32.3024 | -147.7202 | 0.95002 | 0.83898 | 0.68841 | 0.95016 | 0.61201 | 0.50896 | 0.018327 | -135.2526 | 120.9615 | 0.024856 | -151.0894 | 144.5135
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2466e-13 | -4.7718e-10 | -1.3199e-09 | -1.2466e-13 | 4.7718e-10 | 1.3199e-09 | -2.117e-12 | 1.5376e-09 | -8.0477e-11 | 2.1169e-12 | -1.5376e-09 | 8.0477e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95002 | 0.83898 | 0.68841 | 0.95002 | 0.83898 | 0.68841 | 0.018327 | -135.2526 | 120.9615 | 0.018327 | -135.2526 | 120.9615
Line4_2_6 | 0.00073134 | 0.0043194 | 0.0036537 | 0.00073134 | 0.0043194 | 0.0036537 | 0.0001689 | 0.00099752 | 0.00084379 | 0.0001689 | 0.00099752 | 0.00084379 | -0.00015687 | -0.00082404 | -8.0704e-05 | 0.00015688 | 0.0008244 | 8.0961e-05 | 3.3783e-05 | -0.00014851 | -0.00057555 | -3.3772e-05 | 0.00014888 | 0.00057581 | -167.8235 | 34.5522 | -141.0778 | 12.1765 | -145.4478 | 38.9222 | 0.95006 | 0.8394 | 0.68877 | 0.95011 | 0.83982 | 0.68912 | 0.022833 | -135.2318 | 120.9401 | 0.027339 | -135.211 | 120.9187
Line5_6_7 | 0.00073134 | 0.0043194 | 0.0036537 | 0.00073134 | 0.0043194 | 0.0036537 | 0.0001689 | 0.00099752 | 0.00084379 | 0.0001689 | 0.00099752 | 0.00084379 | -0.00015688 | -0.0008244 | -8.096e-05 | 0.00015689 | 0.00082476 | 8.1216e-05 | 3.3772e-05 | -0.00014888 | -0.00057581 | -3.3762e-05 | 0.00014925 | 0.00057608 | -167.8235 | 34.5521 | -141.0779 | 12.1765 | -145.4479 | 38.9221 | 0.95011 | 0.83982 | 0.68912 | 0.95016 | 0.84024 | 0.68948 | 0.027339 | -135.211 | 120.9187 | 0.031844 | -135.1903 | 120.8974
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6338e-12 | -7.0771e-10 | -1.975e-09 | -1.6338e-12 | 7.0771e-10 | 1.975e-09 | -5.5183e-12 | 2.3007e-09 | -1.1285e-10 | 5.5183e-12 | -2.3007e-09 | 1.1285e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95016 | 0.84024 | 0.68948 | 0.95016 | 0.84024 | 0.68948 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4457e-13 | -2.359e-10 | -6.5833e-10 | -5.446e-13 | 2.359e-10 | 6.5833e-10 | -1.8395e-12 | 7.669e-10 | -3.7615e-11 | 1.8395e-12 | -7.669e-10 | 3.7615e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95016 | 0.84024 | 0.68948 | 0.95016 | 0.84024 | 0.68948 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4459e-13 | -2.359e-10 | -6.5833e-10 | -5.446e-13 | 2.359e-10 | 6.5833e-10 | -1.8395e-12 | 7.669e-10 | -3.7615e-11 | 1.8394e-12 | -7.669e-10 | 3.7615e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95016 | 0.84024 | 0.68948 | 0.95016 | 0.84024 | 0.68948 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line9_3_11 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.00015578 | -0.00082178 | -8.1427e-05 | 0.00015579 | 0.00082213 | 8.1681e-05 | 3.423e-05 | -0.00014619 | -0.00057379 | -3.422e-05 | 0.00014656 | 0.00057406 | -167.5846 | 34.6813 | -140.9829 | 12.4154 | -145.3187 | 39.0171 | 0.95006 | 0.8394 | 0.68877 | 0.95011 | 0.83981 | 0.68912 | 0.022818 | -135.2318 | 120.9402 | 0.027308 | -135.211 | 120.919

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00016001 | 0.00094502 | 0.00079938 | 0.00016001 | 0.00094502 | 0.00079938 | -0.00014078 | -0.00073926 | -7.2203e-05 | 0.00014079 | 0.00073958 | 7.2433e-05 | 3.033e-05 | -0.00013295 | -0.00051632 | -3.032e-05 | 0.00013329 | 0.00051656 | -167.8235 | 34.5522 | -141.0778 | 12.1765 | -145.4478 | 38.9222 | 0.90002 | 0.79482 | 0.65218 | 0.90006 | 0.79522 | 0.65252 | 0.018327 | -135.2526 | 120.9615 | 0.022833 | -135.2318 | 120.9401
Line10_11_12 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013983 | -0.00073787 | -7.3309e-05 | 0.00013984 | 0.00073819 | 7.3538e-05 | 3.0712e-05 | -0.00013154 | -0.00051522 | -3.0703e-05 | 0.00013187 | 0.00051546 | -167.5846 | 34.6813 | -140.983 | 12.4154 | -145.3187 | 39.017 | 0.9001 | 0.79561 | 0.65285 | 0.90015 | 0.79601 | 0.65319 | 0.027308 | -135.211 | 120.919 | 0.031798 | -135.1903 | 120.8977
Line11_12_13 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013984 | -0.00073819 | -7.3537e-05 | 0.00013984 | 0.00073851 | 7.3766e-05 | 3.0703e-05 | -0.00013187 | -0.00051546 | -3.0693e-05 | 0.0001322 | 0.0005157 | -167.5846 | 34.6812 | -140.9831 | 12.4154 | -145.3188 | 39.0169 | 0.90015 | 0.79601 | 0.65319 | 0.90019 | 0.7964 | 0.65352 | 0.031798 | -135.1903 | 120.8977 | 0.036287 | -135.1696 | 120.8765
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8775e-12 | -6.3282e-10 | -1.7711e-09 | -1.8775e-12 | 6.3282e-10 | 1.7711e-09 | -5.6441e-12 | 2.0632e-09 | -9.8974e-11 | 5.6441e-12 | -2.0632e-09 | 9.8974e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90019 | 0.7964 | 0.65352 | 0.90019 | 0.7964 | 0.65352 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line13_13_14 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013984 | -0.00073851 | -7.3764e-05 | 0.00013985 | 0.00073883 | 7.3992e-05 | 3.0693e-05 | -0.00013221 | -0.0005157 | -3.0684e-05 | 0.00013254 | 0.00051594 | -167.5846 | 34.681 | -140.9833 | 12.4154 | -145.319 | 39.0167 | 0.90019 | 0.7964 | 0.65352 | 0.90023 | 0.7968 | 0.65386 | 0.036287 | -135.1696 | 120.8765 | 0.040776 | -135.1488 | 120.8553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2516e-12 | -4.2188e-10 | -1.1807e-09 | -1.2516e-12 | 4.2188e-10 | 1.1807e-09 | -3.7627e-12 | 1.3754e-09 | -6.5983e-11 | 3.7627e-12 | -1.3754e-09 | 6.5983e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90019 | 0.7964 | 0.65352 | 0.90019 | 0.7964 | 0.65352 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2582e-13 | -2.1094e-10 | -5.9037e-10 | -6.2581e-13 | 2.1094e-10 | 5.9037e-10 | -1.8814e-12 | 6.8772e-10 | -3.2991e-11 | 1.8814e-12 | -6.8772e-10 | 3.2991e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90019 | 0.7964 | 0.65352 | 0.90019 | 0.7964 | 0.65352 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line16_4_18 | 0 | 2.3818 | 2.3818 | 0 | 2.3818 | 2.3818 | 0 | 0.55006 | 0.55006 | 0 | 0.55006 | 0.55006 | 5.0511e-13 | 0.31838 | -0.10054 | -5.0517e-13 | -0.20946 | 0.20946 | -1.2887e-12 | -0.018508 | 0.24543 | 1.2888e-12 | 0.13197 | -0.13197 | 0 | -147.7624 | 32.2376 | 0 | 32.2376 | -147.7624 | 0.90015 | 0.5798 | 0.48218 | 0.90015 | 0.45008 | 0.45008 | 0.024856 | -151.0894 | 144.5135 | 0.024856 | -179.9751 | -179.9751
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5935e-14 | -2.1414e-10 | -5.9232e-10 | -5.5935e-14 | 2.1414e-10 | 5.9232e-10 | -9.5004e-13 | 6.9002e-10 | -3.6114e-11 | 9.5001e-13 | -6.9002e-10 | 3.6114e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90002 | 0.79482 | 0.65218 | 0.90002 | 0.79482 | 0.65218 | 0.018327 | -135.2526 | 120.9615 | 0.018327 | -135.2526 | 120.9615
Line1_1_3 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013981 | -0.00073723 | -7.2853e-05 | 0.00013982 | 0.00073755 | 7.3082e-05 | 3.0731e-05 | -0.00013087 | -0.00051475 | -3.0722e-05 | 0.0001312 | 0.00051498 | -167.5846 | 34.6814 | -140.9829 | 12.4154 | -145.3186 | 39.0171 | 0.90002 | 0.79482 | 0.65218 | 0.90006 | 0.79522 | 0.65252 | 0.018327 | -135.2526 | 120.9615 | 0.022818 | -135.2318 | 120.9402
Line2_1_4 | 0.0014192 | 2.3739 | 2.375 | 0.0014192 | 2.3739 | 2.375 | 0.00032776 | 0.54824 | 0.54848 | 0.00032776 | 0.54824 | 0.54848 | -0.00029123 | 0.42551 | 0.0082297 | 0.00029127 | -0.31731 | 0.10007 | -4.6917e-05 | 0.093905 | 0.35761 | 4.6957e-05 | 0.018806 | -0.2448 | 170.8668 | -147.6976 | 32.2798 | -9.1332 | 32.3024 | -147.7202 | 0.90002 | 0.79482 | 0.65218 | 0.90015 | 0.5798 | 0.48218 | 0.018327 | -135.2526 | 120.9615 | 0.024856 | -151.0894 | 144.5135
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1189e-13 | -4.2827e-10 | -1.1846e-09 | -1.1189e-13 | 4.2827e-10 | 1.1846e-09 | -1.9e-12 | 1.38e-09 | -7.2228e-11 | 1.9e-12 | -1.38e-09 | 7.2228e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90002 | 0.79482 | 0.65218 | 0.90002 | 0.79482 | 0.65218 | 0.018327 | -135.2526 | 120.9615 | 0.018327 | -135.2526 | 120.9615
Line4_2_6 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00016001 | 0.00094502 | 0.00079938 | 0.00016001 | 0.00094502 | 0.00079938 | -0.00014079 | -0.00073958 | -7.2433e-05 | 0.0001408 | 0.0007399 | 7.2663e-05 | 3.032e-05 | -0.00013329 | -0.00051656 | -3.0311e-05 | 0.00013362 | 0.0005168 | -167.8235 | 34.5522 | -141.0778 | 12.1765 | -145.4478 | 38.9222 | 0.90006 | 0.79522 | 0.65252 | 0.9001 | 0.79562 | 0.65285 | 0.022833 | -135.2318 | 120.9401 | 0.027339 | -135.211 | 120.9187
Line5_6_7 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00016001 | 0.00094502 | 0.00079938 | 0.00016001 | 0.00094502 | 0.00079938 | -0.0001408 | -0.0007399 | -7.2662e-05 | 0.00014081 | 0.00074023 | 7.2892e-05 | 3.0311e-05 | -0.00013362 | -0.0005168 | -3.0301e-05 | 0.00013396 | 0.00051704 | -167.8235 | 34.5521 | -141.0779 | 12.1765 | -145.4479 | 38.9221 | 0.9001 | 0.79562 | 0.65285 | 0.90015 | 0.79601 | 0.65319 | 0.027339 | -135.211 | 120.9187 | 0.031844 | -135.1903 | 120.8974
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4664e-12 | -6.3518e-10 | -1.7726e-09 | -1.4664e-12 | 6.3518e-10 | 1.7726e-09 | -4.9528e-12 | 2.0649e-09 | -1.0128e-10 | 4.9528e-12 | -2.0649e-09 | 1.0128e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90015 | 0.79601 | 0.65319 | 0.90015 | 0.79601 | 0.65319 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8883e-13 | -2.1173e-10 | -5.9085e-10 | -4.8883e-13 | 2.1173e-10 | 5.9085e-10 | -1.651e-12 | 6.883e-10 | -3.376e-11 | 1.651e-12 | -6.883e-10 | 3.376e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90015 | 0.79601 | 0.65319 | 0.90015 | 0.79601 | 0.65319 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8879e-13 | -2.1173e-10 | -5.9085e-10 | -4.8877e-13 | 2.1173e-10 | 5.9085e-10 | -1.6509e-12 | 6.883e-10 | -3.376e-11 | 1.6509e-12 | -6.883e-10 | 3.376e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90015 | 0.79601 | 0.65319 | 0.90015 | 0.79601 | 0.65319 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line9_3_11 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013982 | -0.00073755 | -7.3081e-05 | 0.00013983 | 0.00073787 | 7.331e-05 | 3.0722e-05 | -0.0001312 | -0.00051498 | -3.0712e-05 | 0.00013154 | 0.00051522 | -167.5846 | 34.6813 | -140.9829 | 12.4154 | -145.3187 | 39.0171 | 0.90006 | 0.79522 | 0.65252 | 0.9001 | 0.79561 | 0.65285 | 0.022818 | -135.2318 | 120.9402 | 0.027308 | -135.211 | 120.919

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | -3.0529e-06 | -1.9323e-05 | -6.1103e-06 | 3.0529e-06 | 1.9324e-05 | 6.1104e-06 | 1.4025e-06 | -4.3332e-06 | -1.553e-05 | -1.4024e-06 | 4.3334e-06 | 1.553e-05 | -155.3261 | 47.0496 | -128.5804 | 24.6739 | -132.9504 | 51.4196 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94815 | 0.94461 | 0.00037951 | -120.3111 | 119.9424 | 0.00048425 | -120.3108 | 119.9422
Line10_11_12 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9273e-05 | -6.119e-06 | 3.0287e-06 | 1.9273e-05 | 6.1191e-06 | 1.4067e-06 | -4.2765e-06 | -1.5477e-05 | -1.4067e-06 | 4.2766e-06 | 1.5477e-05 | -155.0872 | 47.1786 | -128.4856 | 24.9128 | -132.8214 | 51.5144 | 0.95 | 0.94816 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00058802 | -120.3104 | 119.942 | 0.00069228 | -120.3101 | 119.9418
Line11_12_13 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9273e-05 | -6.1191e-06 | 3.0287e-06 | 1.9273e-05 | 6.1192e-06 | 1.4067e-06 | -4.2767e-06 | -1.5477e-05 | -1.4067e-06 | 4.2768e-06 | 1.5477e-05 | -155.0872 | 47.1786 | -128.4857 | 24.9128 | -132.8214 | 51.5143 | 0.95 | 0.94817 | 0.94462 | 0.95 | 0.94818 | 0.94463 | 0.00069228 | -120.3101 | 119.9418 | 0.00079653 | -120.3097 | 119.9416
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4181e-14 | -1.8875e-11 | -5.5767e-11 | -1.4181e-14 | 1.8875e-11 | 5.5767e-11 | -1.3801e-13 | 5.3557e-11 | 1.0068e-11 | 1.3801e-13 | -5.3557e-11 | -1.0068e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94818 | 0.94463 | 0.95 | 0.94818 | 0.94463 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line13_13_14 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9273e-05 | -6.1191e-06 | 3.0287e-06 | 1.9273e-05 | 6.1192e-06 | 1.4067e-06 | -4.2769e-06 | -1.5477e-05 | -1.4067e-06 | 4.2771e-06 | 1.5477e-05 | -155.0872 | 47.1784 | -128.4859 | 24.9128 | -132.8216 | 51.5141 | 0.95 | 0.94818 | 0.94463 | 0.95 | 0.94819 | 0.94464 | 0.00079653 | -120.3097 | 119.9416 | 0.00090079 | -120.3093 | 119.9414
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4531e-15 | -1.2584e-11 | -3.7178e-11 | -9.4531e-15 | 1.2584e-11 | 3.7178e-11 | -9.2007e-14 | 3.5704e-11 | 6.7121e-12 | 9.2008e-14 | -3.5704e-11 | -6.7121e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94818 | 0.94463 | 0.95 | 0.94818 | 0.94463 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7269e-15 | -6.2918e-12 | -1.8589e-11 | -4.7267e-15 | 6.2918e-12 | 1.8589e-11 | -4.6004e-14 | 1.7852e-11 | 3.356e-12 | 4.6003e-14 | -1.7852e-11 | -3.356e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94818 | 0.94463 | 0.95 | 0.94818 | 0.94463 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line16_4_18 | 0 | 0.052642 | 0.052642 | 0 | 0.052642 | 0.052642 | 0 | 0.012157 | 0.012157 | 0 | 0.012157 | 0.012157 | 4.986e-15 | 0.011083 | 0.002879 | -4.9849e-15 | -0.01103 | -0.0028258 | -3.19e-14 | 0.0029191 | 0.011048 | 3.19e-14 | -0.0028636 | -0.010992 | 0 | -135.265 | 44.735 | 0 | 44.735 | -135.265 | 0.95 | 0.94276 | 0.93909 | 0.95 | 0.93738 | 0.93358 | 0.0005523 | -120.5099 | 120.1288 | 0.0005523 | -120.7112 | 120.3181
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5288e-15 | -6.4164e-12 | -1.8706e-11 | 3.5285e-15 | 6.4164e-12 | 1.8706e-11 | -2.1918e-14 | 1.7935e-11 | 3.3076e-12 | 2.1919e-14 | -1.7935e-11 | -3.3076e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94814 | 0.9446 | 0.00037951 | -120.3111 | 119.9424 | 0.00037951 | -120.3111 | 119.9424
Line1_1_3 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9272e-05 | -6.1188e-06 | 3.0287e-06 | 1.9272e-05 | 6.1189e-06 | 1.4067e-06 | -4.2761e-06 | -1.5476e-05 | -1.4067e-06 | 4.2763e-06 | 1.5476e-05 | -155.0872 | 47.1788 | -128.4855 | 24.9128 | -132.8212 | 51.5145 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94815 | 0.94461 | 0.00037951 | -120.3111 | 119.9424 | 0.00048377 | -120.3108 | 119.9422
Line2_1_4 | 3.1368e-05 | 0.052468 | 0.052491 | 3.1368e-05 | 0.052468 | 0.052491 | 7.244e-06 | 0.012117 | 0.012122 | 7.244e-06 | 0.012117 | 0.012122 | -6.87e-06 | 0.011103 | 0.0029318 | 6.87e-06 | -0.01105 | -0.0028789 | 4.038e-07 | 0.002952 | 0.011069 | -4.0378e-07 | -0.0028969 | -0.011014 | -176.6358 | -135.2002 | 44.7772 | 3.3642 | 44.7998 | -135.2228 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94276 | 0.93909 | 0.00037951 | -120.3111 | 119.9424 | 0.0005523 | -120.5099 | 120.1288
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.0582e-15 | -1.2833e-11 | -3.7412e-11 | 7.0582e-15 | 1.2833e-11 | 3.7412e-11 | -4.3836e-14 | 3.587e-11 | 6.6152e-12 | 4.3838e-14 | -3.587e-11 | -6.6152e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94814 | 0.9446 | 0.00037951 | -120.3111 | 119.9424 | 0.00037951 | -120.3111 | 119.9424
Line4_2_6 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | -3.0529e-06 | -1.9324e-05 | -6.1104e-06 | 3.0529e-06 | 1.9324e-05 | 6.1105e-06 | 1.4024e-06 | -4.3334e-06 | -1.553e-05 | -1.4024e-06 | 4.3336e-06 | 1.553e-05 | -155.3261 | 47.0495 | -128.5804 | 24.6739 | -132.9505 | 51.4196 | 0.95 | 0.94815 | 0.94461 | 0.95 | 0.94816 | 0.94462 | 0.00048425 | -120.3108 | 119.9422 | 0.00058898 | -120.3104 | 119.942
Line5_6_7 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | -3.0529e-06 | -1.9324e-05 | -6.1105e-06 | 3.0529e-06 | 1.9324e-05 | 6.1106e-06 | 1.4024e-06 | -4.3336e-06 | -1.553e-05 | -1.4024e-06 | 4.3337e-06 | 1.553e-05 | -155.3261 | 47.0495 | -128.5805 | 24.6739 | -132.9505 | 51.4195 | 0.95 | 0.94816 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00058898 | -120.3104 | 119.942 | 0.00069371 | -120.3101 | 119.9418
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3283e-15 | -1.8967e-11 | -5.5854e-11 | -8.3283e-15 | 1.8967e-11 | 5.5854e-11 | -1.202e-13 | 5.3619e-11 | 1.0033e-11 | 1.202e-13 | -5.3619e-11 | -1.0033e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94817 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7768e-15 | -6.3225e-12 | -1.8618e-11 | -2.7768e-15 | 6.3225e-12 | 1.8618e-11 | -4.0065e-14 | 1.7873e-11 | 3.3442e-12 | 4.0065e-14 | -1.7873e-11 | -3.3442e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94817 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7758e-15 | -6.3225e-12 | -1.8618e-11 | -2.7758e-15 | 6.3225e-12 | 1.8618e-11 | -4.0065e-14 | 1.7873e-11 | 3.3442e-12 | 4.0065e-14 | -1.7873e-11 | -3.3442e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94817 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line9_3_11 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9272e-05 | -6.1189e-06 | 3.0287e-06 | 1.9273e-05 | 6.119e-06 | 1.4067e-06 | -4.2763e-06 | -1.5476e-05 | -1.4067e-06 | 4.2765e-06 | 1.5477e-05 | -155.0872 | 47.1787 | -128.4856 | 24.9128 | -132.8213 | 51.5144 | 0.95 | 0.94815 | 0.94461 | 0.95 | 0.94816 | 0.94462 | 0.00048377 | -120.3108 | 119.9422 | 0.00058802 | -120.3104 | 119.942

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | -2.74e-06 | -1.7343e-05 | -5.4841e-06 | 2.74e-06 | 1.7343e-05 | 5.4842e-06 | 1.2587e-06 | -3.8891e-06 | -1.3938e-05 | -1.2587e-06 | 3.8892e-06 | 1.3938e-05 | -155.3261 | 47.0496 | -128.5804 | 24.6739 | -132.9504 | 51.4196 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89825 | 0.89489 | 0.00037951 | -120.3111 | 119.9424 | 0.00048425 | -120.3108 | 119.9422
Line10_11_12 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7297e-05 | -5.4918e-06 | 2.7183e-06 | 1.7297e-05 | 5.4919e-06 | 1.2625e-06 | -3.8382e-06 | -1.389e-05 | -1.2625e-06 | 3.8383e-06 | 1.389e-05 | -155.0872 | 47.1786 | -128.4856 | 24.9128 | -132.8214 | 51.5144 | 0.9 | 0.89826 | 0.8949 | 0.9 | 0.89826 | 0.89491 | 0.00058802 | -120.3104 | 119.942 | 0.00069228 | -120.3101 | 119.9418
Line11_12_13 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7297e-05 | -5.4919e-06 | 2.7183e-06 | 1.7298e-05 | 5.492e-06 | 1.2625e-06 | -3.8383e-06 | -1.389e-05 | -1.2625e-06 | 3.8385e-06 | 1.389e-05 | -155.0872 | 47.1786 | -128.4857 | 24.9128 | -132.8214 | 51.5143 | 0.9 | 0.89826 | 0.89491 | 0.9 | 0.89827 | 0.89492 | 0.00069228 | -120.3101 | 119.9418 | 0.00079653 | -120.3097 | 119.9416
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2727e-14 | -1.6941e-11 | -5.0052e-11 | -1.2727e-14 | 1.6941e-11 | 5.0052e-11 | -1.2387e-13 | 4.8067e-11 | 9.0362e-12 | 1.2387e-13 | -4.8067e-11 | -9.0362e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89827 | 0.89492 | 0.9 | 0.89827 | 0.89492 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line13_13_14 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7298e-05 | -5.4919e-06 | 2.7183e-06 | 1.7298e-05 | 5.492e-06 | 1.2625e-06 | -3.8385e-06 | -1.3891e-05 | -1.2625e-06 | 3.8387e-06 | 1.3891e-05 | -155.0872 | 47.1784 | -128.4859 | 24.9128 | -132.8216 | 51.5141 | 0.9 | 0.89827 | 0.89492 | 0.9 | 0.89828 | 0.89492 | 0.00079653 | -120.3097 | 119.9416 | 0.00090079 | -120.3093 | 119.9414
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4845e-15 | -1.1294e-11 | -3.3368e-11 | -8.4847e-15 | 1.1294e-11 | 3.3368e-11 | -8.2578e-14 | 3.2045e-11 | 6.0241e-12 | 8.2577e-14 | -3.2045e-11 | -6.0241e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89827 | 0.89492 | 0.9 | 0.89827 | 0.89492 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.242e-15 | -5.6469e-12 | -1.6684e-11 | -4.2422e-15 | 5.6469e-12 | 1.6684e-11 | -4.129e-14 | 1.6022e-11 | 3.0121e-12 | 4.1289e-14 | -1.6022e-11 | -3.0121e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89827 | 0.89492 | 0.9 | 0.89827 | 0.89492 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line16_4_18 | 0 | 0.049871 | 0.049871 | 0 | 0.049871 | 0.049871 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | 4.4738e-15 | 0.0099474 | 0.0025839 | -4.4738e-15 | -0.0098997 | -0.0025362 | -2.8628e-14 | 0.0026199 | 0.0099154 | 2.8628e-14 | -0.0025701 | -0.0098657 | 0 | -135.265 | 44.735 | 0 | 44.735 | -135.265 | 0.9 | 0.89314 | 0.88967 | 0.9 | 0.88804 | 0.88445 | 0.0005523 | -120.5099 | 120.1288 | 0.0005523 | -120.7112 | 120.3181
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1673e-15 | -5.7587e-12 | -1.6789e-11 | 3.1674e-15 | 5.7587e-12 | 1.6789e-11 | -1.9671e-14 | 1.6097e-11 | 2.9686e-12 | 1.9671e-14 | -1.6097e-11 | -2.9686e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89824 | 0.89488 | 0.00037951 | -120.3111 | 119.9424 | 0.00037951 | -120.3111 | 119.9424
Line1_1_3 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7297e-05 | -5.4916e-06 | 2.7183e-06 | 1.7297e-05 | 5.4917e-06 | 1.2625e-06 | -3.8378e-06 | -1.389e-05 | -1.2625e-06 | 3.838e-06 | 1.389e-05 | -155.0872 | 47.1788 | -128.4855 | 24.9128 | -132.8212 | 51.5145 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89825 | 0.89489 | 0.00037951 | -120.3111 | 119.9424 | 0.00048377 | -120.3108 | 119.9422
Line2_1_4 | 2.9717e-05 | 0.049706 | 0.049729 | 2.9717e-05 | 0.049706 | 0.049729 | 6.8628e-06 | 0.011479 | 0.011484 | 6.8628e-06 | 0.011479 | 0.011484 | -6.1658e-06 | 0.0099649 | 0.0026313 | 6.1659e-06 | -0.0099174 | -0.0025838 | 3.6241e-07 | 0.0026494 | 0.0099346 | -3.6239e-07 | -0.0026 | -0.0098851 | -176.6358 | -135.2002 | 44.7772 | 3.3642 | 44.7998 | -135.2228 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89314 | 0.88967 | 0.00037951 | -120.3111 | 119.9424 | 0.0005523 | -120.5099 | 120.1288
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3338e-15 | -1.1517e-11 | -3.3577e-11 | 6.3337e-15 | 1.1517e-11 | 3.3577e-11 | -3.9345e-14 | 3.2194e-11 | 5.9372e-12 | 3.9345e-14 | -3.2194e-11 | -5.9372e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89824 | 0.89488 | 0.00037951 | -120.3111 | 119.9424 | 0.00037951 | -120.3111 | 119.9424
Line4_2_6 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | -2.74e-06 | -1.7343e-05 | -5.4841e-06 | 2.74e-06 | 1.7343e-05 | 5.4842e-06 | 1.2587e-06 | -3.8892e-06 | -1.3938e-05 | -1.2587e-06 | 3.8894e-06 | 1.3939e-05 | -155.3261 | 47.0495 | -128.5804 | 24.6739 | -132.9505 | 51.4196 | 0.9 | 0.89825 | 0.89489 | 0.9 | 0.89826 | 0.8949 | 0.00048425 | -120.3108 | 119.9422 | 0.00058898 | -120.3104 | 119.942
Line5_6_7 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | -2.74e-06 | -1.7343e-05 | -5.4842e-06 | 2.74e-06 | 1.7343e-05 | 5.4843e-06 | 1.2587e-06 | -3.8894e-06 | -1.3939e-05 | -1.2587e-06 | 3.8896e-06 | 1.3939e-05 | -155.3261 | 47.0495 | -128.5805 | 24.6739 | -132.9505 | 51.4195 | 0.9 | 0.89826 | 0.8949 | 0.9 | 0.89826 | 0.89491 | 0.00058898 | -120.3104 | 119.942 | 0.00069371 | -120.3101 | 119.9418
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4754e-15 | -1.7023e-11 | -5.013e-11 | -7.4754e-15 | 1.7023e-11 | 5.013e-11 | -1.0788e-13 | 4.8123e-11 | 9.0043e-12 | 1.0788e-13 | -4.8123e-11 | -9.0043e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89826 | 0.89491 | 0.9 | 0.89826 | 0.89491 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4911e-15 | -5.6745e-12 | -1.671e-11 | -2.4908e-15 | 5.6745e-12 | 1.671e-11 | -3.5959e-14 | 1.6041e-11 | 3.0014e-12 | 3.5959e-14 | -1.6041e-11 | -3.0014e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89826 | 0.89491 | 0.9 | 0.89826 | 0.89491 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4909e-15 | -5.6745e-12 | -1.671e-11 | -2.491e-15 | 5.6745e-12 | 1.671e-11 | -3.5958e-14 | 1.6041e-11 | 3.0014e-12 | 3.5959e-14 | -1.6041e-11 | -3.0014e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89826 | 0.89491 | 0.9 | 0.89826 | 0.89491 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line9_3_11 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7297e-05 | -5.4917e-06 | 2.7183e-06 | 1.7297e-05 | 5.4918e-06 | 1.2625e-06 | -3.838e-06 | -1.389e-05 | -1.2625e-06 | 3.8382e-06 | 1.389e-05 | -155.0872 | 47.1787 | -128.4856 | 24.9128 | -132.8213 | 51.5144 | 0.9 | 0.89825 | 0.89489 | 0.9 | 0.89826 | 0.8949 | 0.00048377 | -120.3108 | 119.9422 | 0.00058802 | -120.3104 | 119.942

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.64322 | 0.28553 | 0.31564 | 0.64322 | 0.28553 | 0.31564 | 0.14855 | 0.065941 | 0.072893 | 0.14855 | 0.065941 | 0.072893 | -0.036622 | -0.068348 | 0.086125 | 0.03953 | 0.069006 | -0.086172 | -0.074043 | 0.047517 | 0.0066016 | 0.079697 | -0.047161 | -0.0055734 | 105.1531 | 87.0617 | 127.255 | -74.8469 | -92.9383 | -52.745 |  | 0.55609 | 1.2624 | 1.185 | 0.59889 | 1.2675 | 1.1846 | -11.1643 | -127.7461 | 131.6383 | -11.2284 | -127.2887 | 130.9557
Line10_11_12 | 0.57888 | 0.25374 | 0.29149 | 0.57888 | 0.25374 | 0.29149 | 0.13369 | 0.058598 | 0.067317 | 0.13369 | 0.058598 | 0.067317 | -0.039626 | -0.059306 | 0.079715 | 0.041996 | 0.059806 | -0.07973 | -0.074766 | 0.044995 | 0.0019171 | 0.079325 | -0.04473 | -0.0010309 | 106.822 | 90.2353 | 128.9873 | -73.178 | -89.7647 | -51.0127 |  | 0.63295 | 1.2704 | 1.1845 | 0.67138 | 1.2745 | 1.1845 | -11.1013 | -126.9516 | 130.365 | -11.0753 | -126.5582 | 129.7281
Line11_12_13 | 0.57888 | 0.25374 | 0.29149 | 0.57888 | 0.25374 | 0.29149 | 0.13369 | 0.058598 | 0.067317 | 0.13369 | 0.058598 | 0.067317 | -0.041996 | -0.059806 | 0.07973 | 0.044366 | 0.060306 | -0.079745 | -0.079325 | 0.04473 | 0.0010309 | 0.083884 | -0.044466 | -0.00014466 | 106.822 | 90.2353 | 128.9873 | -73.178 | -89.7647 | -51.0127 |  | 0.67138 | 1.2745 | 1.1845 | 0.70982 | 1.2787 | 1.1846 | -11.0753 | -126.5582 | 129.7281 | -11.0521 | -126.1673 | 129.0912
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1197e-08 | 5.7175e-08 | -7.5648e-08 | -1.3297e-08 | -3.9217e-08 | 4.979e-08 | 4.5711e-08 | -7.082e-08 | -3.3361e-08 | -3.0998e-08 | 4.6684e-08 | 2.2962e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70982 | 1.2787 | 1.1846 | 0.70982 | 1.2787 | 1.1846 | -11.0521 | -126.1673 | 129.0912 | -11.0521 | -126.1673 | 129.0912
Line13_13_14 | 0.57888 | 0.25374 | 0.29149 | 0.57888 | 0.25374 | 0.29149 | 0.13369 | 0.058598 | 0.067317 | 0.13369 | 0.058598 | 0.067317 | -0.044366 | -0.060306 | 0.079745 | 0.046735 | 0.060806 | -0.07976 | -0.083884 | 0.044466 | 0.00014469 | 0.088442 | -0.044201 | 0.00074151 | 106.822 | 90.2353 | 128.9873 | -73.178 | -89.7647 | -51.0127 |  | 0.70982 | 1.2787 | 1.1846 | 0.74825 | 1.2829 | 1.1849 | -11.0521 | -126.1673 | 129.0912 | -11.0312 | -125.7789 | 128.4546
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4131e-08 | 3.8117e-08 | -5.0432e-08 | -6.231e-09 | -2.0159e-08 | 2.4574e-08 | 3.0474e-08 | -4.7213e-08 | -2.2241e-08 | -1.5761e-08 | 2.3078e-08 | 1.1841e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70982 | 1.2787 | 1.1846 | 0.70982 | 1.2787 | 1.1846 | -11.0521 | -126.1673 | 129.0912 | -11.0521 | -126.1673 | 129.0912
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0657e-09 | 1.9058e-08 | -2.5216e-08 | 8.347e-10 | -1.1005e-09 | -6.4207e-10 | 1.5237e-08 | -2.3607e-08 | -1.112e-08 | -5.2388e-10 | -5.2886e-10 | 7.2064e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70982 | 1.2787 | 1.1846 | 0.70982 | 1.2787 | 1.1846 | -11.0521 | -126.1673 | 129.0912 | -11.0521 | -126.1673 | 129.0912
Line16_4_18 | 3.8653 | 0 | 0 | 3.8653 | 0 | 0 | 0.89265 | 0 | 0 | 0.89265 | 0 | 0 | 0.1245 | 3.1992e-08 | -3.3555e-08 | -1.8434e-14 | -7.7801e-10 | -2.1467e-10 | 0.24901 | -2.9193e-08 | -2.0536e-08 | 7.9136e-14 | -1.5545e-10 | 5.2741e-10 | -75.1238 | 0 | 0 | 104.8762 | 0 | 0 |  | 0.31188 | 1.2459 | 1.1429 | 0 | 1.2229 | 1.0952 | -11.6889 | -124.5851 | 129.2424 | 0 | -121.892 | 127.1854
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4397e-09 | 2.4555e-08 | -2.9254e-08 | 9.6657e-10 | -1.0274e-09 | -6.8037e-10 | 1.5209e-08 | -2.7379e-08 | -1.778e-08 | -4.1454e-10 | -6.5507e-10 | 9.2035e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.55609 | 1.2624 | 1.185 | 0.55609 | 1.2624 | 1.185 | -11.1643 | -127.7461 | 131.6383 | -11.1643 | -127.7461 | 131.6383
Line1_1_3 | 0.57888 | 0.25374 | 0.29149 | 0.57888 | 0.25374 | 0.29149 | 0.13369 | 0.058598 | 0.067317 | 0.13369 | 0.058598 | 0.067317 | -0.034886 | -0.058307 | 0.079685 | 0.037256 | 0.058807 | -0.0797 | -0.065649 | 0.045524 | 0.0036894 | 0.070207 | -0.045259 | -0.0028032 | 106.822 | 90.2353 | 128.9873 | -73.178 | -89.7647 | -51.0127 |  | 0.55609 | 1.2624 | 1.185 | 0.59452 | 1.2664 | 1.1847 | -11.1643 | -127.7461 | 131.6383 | -11.1308 | -127.3476 | 131.0017
Line2_1_4 | 2.9061 | 0.37455 | 0.28961 | 2.9061 | 0.37455 | 0.28961 | 0.67113 | 0.086498 | 0.066882 | 0.67113 | 0.086498 | 0.066882 | 0.17228 | -0.097261 | 0.078995 | -0.09832 | 0.098543 | -0.076383 | 0.33106 | 0.049635 | 0.0064085 | -0.18478 | -0.043617 | -0.0029906 | -73.6718 | 79.2902 | 127.0003 | 106.3282 | -100.7098 | -52.9997 |  | 0.55609 | 1.2624 | 1.185 | 0.31188 | 1.2459 | 1.1429 | -11.1643 | -127.7461 | 131.6383 | -11.6889 | -124.5851 | 129.2424
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0879e-08 | 4.911e-08 | -5.8507e-08 | -4.4731e-09 | -2.5583e-08 | 2.8573e-08 | 3.0418e-08 | -5.4758e-08 | -3.556e-08 | -1.5624e-08 | 2.6724e-08 | 1.87e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.55609 | 1.2624 | 1.185 | 0.55609 | 1.2624 | 1.185 | -11.1643 | -127.7461 | 131.6383 | -11.1643 | -127.7461 | 131.6383
Line4_2_6 | 0.64322 | 0.28553 | 0.31564 | 0.64322 | 0.28553 | 0.31564 | 0.14855 | 0.065941 | 0.072893 | 0.14855 | 0.065941 | 0.072893 | -0.03953 | -0.069006 | 0.086172 | 0.042438 | 0.069663 | -0.086218 | -0.079697 | 0.047161 | 0.0055734 | 0.085351 | -0.046806 | -0.0045453 | 105.1531 | 87.0617 | 127.255 | -74.8469 | -92.9383 | -52.745 |  | 0.59889 | 1.2675 | 1.1846 | 0.64169 | 1.2728 | 1.1845 | -11.2284 | -127.2887 | 130.9557 | -11.284 | -126.835 | 130.2728
Line5_6_7 | 0.64322 | 0.28553 | 0.31564 | 0.64322 | 0.28553 | 0.31564 | 0.14855 | 0.065941 | 0.072893 | 0.14855 | 0.065941 | 0.072893 | -0.042438 | -0.069663 | 0.086218 | 0.045346 | 0.070321 | -0.086265 | -0.085351 | 0.046806 | 0.0045453 | 0.091006 | -0.046451 | -0.0035171 | 105.1531 | 87.0617 | 127.255 | -74.8469 | -92.9383 | -52.745 |  | 0.64169 | 1.2728 | 1.1845 | 0.68449 | 1.2781 | 1.1844 | -11.284 | -126.835 | 130.2728 | -11.3327 | -126.3851 | 129.5897
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0982e-08 | 5.9943e-08 | -7.8282e-08 | -1.3122e-08 | -4.1061e-08 | 5.154e-08 | 4.6062e-08 | -7.3436e-08 | -3.6346e-08 | -3.1226e-08 | 4.841e-08 | 2.4991e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68449 | 1.2781 | 1.1844 | 0.68449 | 1.2781 | 1.1844 | -11.3327 | -126.3851 | 129.5897 | -11.3327 | -126.3851 | 129.5897
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.994e-09 | 1.9981e-08 | -2.6094e-08 | 8.6598e-10 | -1.0994e-09 | -6.4755e-10 | 1.5354e-08 | -2.4479e-08 | -1.2115e-08 | -5.1785e-10 | -5.4722e-10 | 7.5967e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68449 | 1.2781 | 1.1844 | 0.68449 | 1.2781 | 1.1844 | -11.3327 | -126.3851 | 129.5897 | -11.3327 | -126.3851 | 129.5897
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.994e-09 | 1.9981e-08 | -2.6094e-08 | 8.6598e-10 | -1.0994e-09 | -6.4755e-10 | 1.5354e-08 | -2.4479e-08 | -1.2115e-08 | -5.1785e-10 | -5.4722e-10 | 7.5967e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68449 | 1.2781 | 1.1844 | 0.68449 | 1.2781 | 1.1844 | -11.3327 | -126.3851 | 129.5897 | -11.3327 | -126.3851 | 129.5897
Line9_3_11 | 0.57888 | 0.25374 | 0.29149 | 0.57888 | 0.25374 | 0.29149 | 0.13369 | 0.058598 | 0.067317 | 0.13369 | 0.058598 | 0.067317 | -0.037256 | -0.058807 | 0.0797 | 0.039626 | 0.059306 | -0.079715 | -0.070207 | 0.045259 | 0.0028032 | 0.074766 | -0.044995 | -0.0019171 | 106.822 | 90.2353 | 128.9873 | -73.178 | -89.7647 | -51.0127 |  | 0.59452 | 1.2664 | 1.1847 | 0.63295 | 1.2704 | 1.1845 | -11.1308 | -127.3476 | 131.0017 | -11.1013 | -126.9516 | 130.365

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.65915 | 0.29475 | 0.32263 | 0.65915 | 0.29475 | 0.32263 | 0.15222 | 0.06807 | 0.074509 | 0.15222 | 0.06807 | 0.074509 | -0.038538 | -0.073995 | 0.092329 | 0.041583 | 0.074689 | -0.092377 | -0.077806 | 0.051657 | 0.0084805 | 0.083741 | -0.051271 | -0.0074176 | 104.915 | 87.0381 | 126.5533 | -75.085 | -92.9619 | -53.4467 |  | 0.57039 | 1.3257 | 1.2444 | 0.61421 | 1.3309 | 1.2438 | -11.4345 | -127.8815 | 131.8013 | -11.4928 | -127.4297 | 131.1441
Line10_11_12 | 0.5956 | 0.26315 | 0.29891 | 0.5956 | 0.26315 | 0.29891 | 0.13755 | 0.060771 | 0.06903 | 0.13755 | 0.060771 | 0.06903 | -0.041807 | -0.064561 | 0.085766 | 0.044309 | 0.065094 | -0.085781 | -0.078937 | 0.049008 | 0.0034764 | 0.083761 | -0.048716 | -0.0025542 | 106.5412 | 90.1096 | 128.2499 | -73.4588 | -89.8904 | -51.7501 |  | 0.6494 | 1.3338 | 1.2435 | 0.68891 | 1.3379 | 1.2432 | -11.3657 | -127.0923 | 130.571 | -11.3373 | -126.7013 | 129.9554
Line11_12_13 | 0.5956 | 0.26315 | 0.29891 | 0.5956 | 0.26315 | 0.29891 | 0.13755 | 0.060771 | 0.06903 | 0.13755 | 0.060771 | 0.06903 | -0.044309 | -0.065094 | 0.085781 | 0.04681 | 0.065627 | -0.085797 | -0.083761 | 0.048716 | 0.0025542 | 0.088585 | -0.048424 | -0.0016319 | 106.5412 | 90.1096 | 128.2499 | -73.4588 | -89.8903 | -51.7501 |  | 0.68891 | 1.3379 | 1.2432 | 0.72841 | 1.3421 | 1.2431 | -11.3373 | -126.7013 | 129.9554 | -11.3119 | -126.3127 | 129.3395
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.332e-08 | 6.4857e-08 | -8.5155e-08 | -1.4611e-08 | -4.4462e-08 | 5.6051e-08 | 5.0554e-08 | -7.986e-08 | -3.8607e-08 | -3.4279e-08 | 5.2645e-08 | 2.6551e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72841 | 1.3421 | 1.2431 | 0.72841 | 1.3421 | 1.2431 | -11.3119 | -126.3127 | 129.3395 | -11.3119 | -126.3127 | 129.3395
Line13_13_14 | 0.5956 | 0.26315 | 0.29891 | 0.5956 | 0.26315 | 0.29891 | 0.13755 | 0.060771 | 0.06903 | 0.13755 | 0.060771 | 0.06903 | -0.046811 | -0.065627 | 0.085797 | 0.049312 | 0.066161 | -0.085813 | -0.088585 | 0.048424 | 0.001632 | 0.093409 | -0.048132 | -0.00070972 | 106.5412 | 90.1097 | 128.2498 | -73.4588 | -89.8903 | -51.7502 |  | 0.72841 | 1.3421 | 1.2431 | 0.76792 | 1.3463 | 1.2432 | -11.3119 | -126.3127 | 129.3395 | -11.2891 | -125.9266 | 128.7237
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5547e-08 | 4.3238e-08 | -5.677e-08 | -6.838e-09 | -2.2843e-08 | 2.7666e-08 | 3.3702e-08 | -5.324e-08 | -2.5738e-08 | -1.7427e-08 | 2.6025e-08 | 1.3683e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72841 | 1.3421 | 1.2431 | 0.72841 | 1.3421 | 1.2431 | -11.3119 | -126.3127 | 129.3395 | -11.3119 | -126.3127 | 129.3395
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7734e-09 | 2.1619e-08 | -2.8385e-08 | 9.3538e-10 | -1.224e-09 | -7.1884e-10 | 1.6851e-08 | -2.662e-08 | -1.2869e-08 | -5.7627e-10 | -5.9519e-10 | 8.1368e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72841 | 1.3421 | 1.2431 | 0.72841 | 1.3421 | 1.2431 | -11.3119 | -126.3127 | 129.3395 | -11.3119 | -126.3127 | 129.3395
Line16_4_18 | 3.957 | 0 | 0 | 3.957 | 0 | 0 | 0.91383 | 0 | 0 | 0.91383 | 0 | 0 | 0.13048 | 3.5602e-08 | -3.7266e-08 | 3.1808e-14 | -8.7601e-10 | -2.5606e-10 | 0.26096 | -3.2601e-08 | -2.3124e-08 | -2.6758e-14 | -1.9648e-10 | 6.0618e-10 | -75.3696 | 0 | 0 | 104.6304 | 0 | 0 |  | 0.31928 | 1.3086 | 1.2005 | 0 | 1.2851 | 1.1512 | -11.9346 | -124.7966 | 129.4836 | 0 | -122.1724 | 127.5013
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9816e-09 | 2.7565e-08 | -3.2696e-08 | 1.062e-09 | -1.1479e-09 | -7.6486e-10 | 1.6654e-08 | -3.0692e-08 | -2.0139e-08 | -4.5608e-10 | -7.3323e-10 | 1.0265e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.57039 | 1.3257 | 1.2444 | 0.57039 | 1.3257 | 1.2444 | -11.4345 | -127.8815 | 131.8013 | -11.4345 | -127.8815 | 131.8013
Line1_1_3 | 0.5956 | 0.26315 | 0.29891 | 0.5956 | 0.26315 | 0.29891 | 0.13755 | 0.060771 | 0.06903 | 0.13755 | 0.060771 | 0.06903 | -0.036804 | -0.063495 | 0.085734 | 0.039305 | 0.064028 | -0.08575 | -0.069288 | 0.049592 | 0.0053209 | 0.074113 | -0.0493 | -0.0043986 | 106.5412 | 90.1096 | 128.2499 | -73.4588 | -89.8904 | -51.7501 |  | 0.57039 | 1.3257 | 1.2444 | 0.6099 | 1.3297 | 1.2439 | -11.4345 | -127.8815 | 131.8013 | -11.3979 | -127.4857 | 131.1864
Line2_1_4 | 2.9883 | 0.382 | 0.29695 | 2.9883 | 0.382 | 0.29695 | 0.69013 | 0.088219 | 0.068577 | 0.69013 | 0.088219 | 0.068577 | 0.18147 | -0.10383 | 0.084929 | -0.10328 | 0.10519 | -0.08219 | 0.34932 | 0.053838 | 0.0083242 | -0.19464 | -0.047548 | -0.0047106 | -73.9835 | 79.5267 | 126.2034 | 106.0165 | -100.4733 | -53.7966 |  | 0.57039 | 1.3257 | 1.2444 | 0.31928 | 1.3086 | 1.2005 | -11.4345 | -127.8815 | 131.8013 | -11.9346 | -124.7966 | 129.4836
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1963e-08 | 5.5131e-08 | -6.5392e-08 | -4.9196e-09 | -2.8713e-08 | 3.1931e-08 | 3.3308e-08 | -6.1385e-08 | -4.0278e-08 | -1.711e-08 | 2.9959e-08 | 2.1165e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.57039 | 1.3257 | 1.2444 | 0.57039 | 1.3257 | 1.2444 | -11.4345 | -127.8815 | 131.8013 | -11.4345 | -127.8815 | 131.8013
Line4_2_6 | 0.65915 | 0.29475 | 0.32263 | 0.65915 | 0.29475 | 0.32263 | 0.15222 | 0.06807 | 0.074509 | 0.15222 | 0.06807 | 0.074509 | -0.041583 | -0.074689 | 0.092377 | 0.044629 | 0.075383 | -0.092424 | -0.083741 | 0.051271 | 0.0074176 | 0.089675 | -0.050884 | -0.0063547 | 104.915 | 87.0381 | 126.5533 | -75.085 | -92.9619 | -53.4467 |  | 0.61421 | 1.3309 | 1.2438 | 0.65802 | 1.3361 | 1.2434 | -11.4928 | -127.4297 | 131.1441 | -11.5433 | -126.9813 | 130.4865
Line5_6_7 | 0.65915 | 0.29475 | 0.32263 | 0.65915 | 0.29475 | 0.32264 | 0.15222 | 0.06807 | 0.074509 | 0.15222 | 0.06807 | 0.074509 | -0.044629 | -0.075383 | 0.092424 | 0.047674 | 0.076077 | -0.092472 | -0.089675 | 0.050884 | 0.0063547 | 0.09561 | -0.050497 | -0.0052917 | 104.915 | 87.0381 | 126.5533 | -75.085 | -92.9619 | -53.4467 |  | 0.65802 | 1.3361 | 1.2434 | 0.70184 | 1.3414 | 1.2431 | -11.5433 | -126.9813 | 130.4865 | -11.5875 | -126.5365 | 129.8285
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3028e-08 | 6.7918e-08 | -8.8001e-08 | -1.4385e-08 | -4.6501e-08 | 5.7941e-08 | 5.0844e-08 | -8.2701e-08 | -4.196e-08 | -3.4464e-08 | 5.4518e-08 | 2.8829e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70184 | 1.3414 | 1.2431 | 0.70184 | 1.3414 | 1.2431 | -11.5875 | -126.5365 | 129.8285 | -11.5875 | -126.5365 | 129.8285
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6759e-09 | 2.2639e-08 | -2.9334e-08 | 9.6694e-10 | -1.2227e-09 | -7.2586e-10 | 1.6948e-08 | -2.7567e-08 | -1.3987e-08 | -5.686e-10 | -6.159e-10 | 8.5586e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70184 | 1.3414 | 1.2431 | 0.70184 | 1.3414 | 1.2431 | -11.5875 | -126.5365 | 129.8285 | -11.5875 | -126.5365 | 129.8285
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6759e-09 | 2.2639e-08 | -2.9334e-08 | 9.6694e-10 | -1.2227e-09 | -7.2586e-10 | 1.6948e-08 | -2.7567e-08 | -1.3987e-08 | -5.686e-10 | -6.159e-10 | 8.5586e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70184 | 1.3414 | 1.2431 | 0.70184 | 1.3414 | 1.2431 | -11.5875 | -126.5365 | 129.8285 | -11.5875 | -126.5365 | 129.8285
Line9_3_11 | 0.5956 | 0.26315 | 0.29891 | 0.5956 | 0.26315 | 0.29891 | 0.13755 | 0.060771 | 0.06903 | 0.13755 | 0.060771 | 0.06903 | -0.039305 | -0.064028 | 0.08575 | 0.041807 | 0.064561 | -0.085766 | -0.074113 | 0.0493 | 0.0043986 | 0.078937 | -0.049008 | -0.0034764 | 106.5412 | 90.1096 | 128.2499 | -73.4588 | -89.8904 | -51.7501 |  | 0.6099 | 1.3297 | 1.2439 | 0.6494 | 1.3338 | 1.2435 | -11.3979 | -127.4857 | 131.1864 | -11.3657 | -127.0923 | 130.571

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.12284 | 0.11626 | 0.12003 | 0.12284 | 0.11626 | 0.12003 | 0.028369 | 0.026848 | 0.027719 | 0.028369 | 0.026848 | 0.027719 | -0.0026418 | -0.0018888 | -0.00086255 | 0.002794 | 0.0020273 | 0.0010017 | -0.030588 | -0.029154 | -0.030078 | 0.030884 | 0.029428 | 0.030367 | 94.8757 | -26.2094 | -148.1228 | -85.1243 | 153.7906 | 31.8772 |  | 1.0822 | 1.0882 | 1.0856 | 1.0931 | 1.0987 | 1.0962 | -0.060667 | -119.9163 | 120.2346 | -0.29366 | -120.1504 | 119.9878
Line10_11_12 | 0.10944 | 0.10357 | 0.10713 | 0.10944 | 0.10357 | 0.10713 | 0.025273 | 0.023918 | 0.02474 | 0.025273 | 0.023918 | 0.02474 | -0.0025588 | -0.0018001 | -0.00090981 | 0.0026797 | 0.00191 | 0.0010206 | -0.027725 | -0.026414 | -0.027308 | 0.02796 | 0.026631 | 0.027539 | 94.7983 | -26.435 | -148.297 | -85.2017 | 153.565 | 31.703 |  | 1.1017 | 1.1069 | 1.1044 | 1.1114 | 1.1163 | 1.1139 | -0.47468 | -120.3337 | 119.7948 | -0.67626 | -120.5371 | 119.5805
Line11_12_13 | 0.10944 | 0.10357 | 0.10713 | 0.10944 | 0.10357 | 0.10713 | 0.025273 | 0.023918 | 0.02474 | 0.025273 | 0.023918 | 0.02474 | -0.0026797 | -0.00191 | -0.0010206 | 0.0028007 | 0.0020198 | 0.0011314 | -0.02796 | -0.026631 | -0.027539 | 0.028196 | 0.026849 | 0.027769 | 94.7983 | -26.435 | -148.297 | -85.2017 | 153.565 | 31.703 |  | 1.1114 | 1.1163 | 1.1139 | 1.1211 | 1.1257 | 1.1234 | -0.67626 | -120.5371 | 119.5805 | -0.87433 | -120.7372 | 119.3698
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4196e-09 | 1.0932e-09 | 2.1143e-10 | -1.2393e-09 | -1.0416e-09 | -4.4339e-10 | 6.8613e-10 | -5.48e-10 | 3.6441e-10 | -5.2328e-10 | 3.0958e-10 | -2.9051e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1211 | 1.1257 | 1.1234 | 1.1211 | 1.1257 | 1.1234 | -0.87433 | -120.7372 | 119.3698 | -0.87433 | -120.7372 | 119.3698
Line13_13_14 | 0.10944 | 0.10357 | 0.10713 | 0.10944 | 0.10357 | 0.10713 | 0.025273 | 0.023918 | 0.02474 | 0.025273 | 0.023918 | 0.02474 | -0.0028007 | -0.0020198 | -0.0011314 | 0.0029217 | 0.0021296 | 0.0012422 | -0.028196 | -0.026849 | -0.027769 | 0.028432 | 0.027066 | 0.027999 | 94.7983 | -26.435 | -148.297 | -85.2017 | 153.565 | 31.703 |  | 1.1211 | 1.1257 | 1.1234 | 1.1309 | 1.1351 | 1.1328 | -0.87433 | -120.7372 | 119.3698 | -1.069 | -120.9339 | 119.1626
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4643e-10 | 7.288e-10 | 1.4095e-10 | -7.6611e-10 | -6.7716e-10 | -3.7292e-10 | 4.5742e-10 | -3.6533e-10 | 2.4294e-10 | -2.9457e-10 | 1.2691e-10 | -1.6904e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1211 | 1.1257 | 1.1234 | 1.1211 | 1.1257 | 1.1234 | -0.87433 | -120.7372 | 119.3698 | -0.87433 | -120.7372 | 119.3698
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7321e-10 | 3.644e-10 | 7.0475e-11 | -2.929e-10 | -3.1276e-10 | -3.0244e-10 | 2.2871e-10 | -1.8267e-10 | 1.2147e-10 | -6.5865e-11 | -5.5759e-11 | -4.757e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1211 | 1.1257 | 1.1234 | 1.1211 | 1.1257 | 1.1234 | -0.87433 | -120.7372 | 119.3698 | -0.87433 | -120.7372 | 119.3698
Line16_4_18 | 0.035604 | 0 | 0 | 0.035604 | 0 | 0 | 0.0082224 | 0 | 0 | 0.0082224 | 0 | 0 | 0.0063489 | 3.2977e-10 | -1.4977e-10 | -0.0063383 | -2.0205e-10 | -1.9406e-10 | 0.0063594 | -3.2507e-10 | 4.6949e-11 | -0.0063383 | 9.3606e-13 | 3.9959e-12 | -45.2649 | 0 | 0 | 134.7351 | 0 | 0 |  | 1.0929 | 1.1005 | 1.0983 | 1.0902 | 1.1001 | 1.0982 | -0.21724 | -120.0073 | 120.0835 | -0.26487 | -119.9873 | 120.0541
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2194e-10 | 2.4194e-10 | -1.4209e-10 | -1.2793e-10 | -1.5225e-10 | -1.4161e-10 | 2.1862e-10 | -2.8253e-10 | 4.2535e-11 | -4.4118e-12 | 6.1194e-12 | 1.7112e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0822 | 1.0882 | 1.0856 | 1.0822 | 1.0882 | 1.0856 | -0.060667 | -119.9163 | 120.2346 | -0.060667 | -119.9163 | 120.2346
Line1_1_3 | 0.10944 | 0.10357 | 0.10713 | 0.10944 | 0.10357 | 0.10713 | 0.025273 | 0.023918 | 0.02474 | 0.025273 | 0.023918 | 0.02474 | -0.0023168 | -0.0015804 | -0.00068821 | 0.0024378 | 0.0016903 | 0.00079901 | -0.027254 | -0.025979 | -0.026848 | 0.027489 | 0.026196 | 0.027078 | 94.7983 | -26.435 | -148.297 | -85.2017 | 153.565 | 31.703 |  | 1.0822 | 1.0882 | 1.0856 | 1.0919 | 1.0975 | 1.095 | -0.060667 | -119.9163 | 120.2346 | -0.26952 | -120.1268 | 120.0128
Line2_1_4 | 0.11131 | 0.13196 | 0.13474 | 0.11131 | 0.13196 | 0.13474 | 0.025706 | 0.030475 | 0.031116 | 0.025706 | 0.030475 | 0.031116 | -0.0047285 | -0.0101 | -0.0088881 | 0.0048506 | 0.010266 | 0.0090793 | -0.027415 | -0.031587 | -0.032589 | 0.027672 | 0.031929 | 0.032947 | 99.7251 | -12.1838 | -134.5099 | -80.2749 | 167.8162 | 45.4901 |  | 1.0822 | 1.0882 | 1.0856 | 1.0929 | 1.1005 | 1.0983 | -0.060667 | -119.9163 | 120.2346 | -0.21724 | -120.0073 | 120.0835
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4389e-10 | 4.8387e-10 | -2.8417e-10 | -4.4987e-10 | -3.9419e-10 | 4.7221e-13 | 4.3724e-10 | -5.6506e-10 | 8.507e-11 | -2.2303e-10 | 2.8865e-10 | -2.5423e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0822 | 1.0882 | 1.0856 | 1.0822 | 1.0882 | 1.0856 | -0.060667 | -119.9163 | 120.2346 | -0.060667 | -119.9163 | 120.2346
Line4_2_6 | 0.12284 | 0.11626 | 0.12003 | 0.12284 | 0.11626 | 0.12003 | 0.028369 | 0.026848 | 0.027719 | 0.028369 | 0.026848 | 0.027719 | -0.002794 | -0.0020273 | -0.0010017 | 0.0029463 | 0.0021658 | 0.0011409 | -0.030884 | -0.029428 | -0.030367 | 0.031181 | 0.029702 | 0.030656 | 94.8757 | -26.2094 | -148.1228 | -85.1243 | 153.7906 | 31.8772 |  | 1.0931 | 1.0987 | 1.0962 | 1.104 | 1.1092 | 1.1068 | -0.29366 | -120.1504 | 119.9878 | -0.52205 | -120.38 | 119.7458
Line5_6_7 | 0.12284 | 0.11626 | 0.12003 | 0.12284 | 0.11626 | 0.12003 | 0.028369 | 0.026848 | 0.027719 | 0.028369 | 0.026848 | 0.027719 | -0.0029463 | -0.0021658 | -0.0011409 | 0.0030985 | 0.0023043 | 0.0012801 | -0.031181 | -0.029702 | -0.030656 | 0.031478 | 0.029975 | 0.030946 | 94.8757 | -26.2094 | -148.1228 | -85.1243 | 153.7906 | 31.8772 |  | 1.104 | 1.1092 | 1.1068 | 1.115 | 1.1198 | 1.1174 | -0.52205 | -120.38 | 119.7458 | -0.74596 | -120.6053 | 119.5084
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3525e-09 | 1.0302e-09 | 1.0401e-10 | -1.1677e-09 | -9.7352e-10 | -3.4553e-10 | 6.8129e-10 | -6.0306e-10 | 3.3131e-10 | -5.1008e-10 | 3.5649e-10 | -2.5778e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.115 | 1.1198 | 1.1174 | 1.115 | 1.1198 | 1.1174 | -0.74596 | -120.6053 | 119.5084 | -0.74596 | -120.6053 | 119.5084
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5082e-10 | 3.4341e-10 | 3.467e-11 | -2.6602e-10 | -2.867e-10 | -2.7619e-10 | 2.271e-10 | -2.0102e-10 | 1.1044e-10 | -5.5887e-11 | -4.5545e-11 | -3.6911e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.115 | 1.1198 | 1.1174 | 1.115 | 1.1198 | 1.1174 | -0.74596 | -120.6053 | 119.5084 | -0.74596 | -120.6053 | 119.5084
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5082e-10 | 3.4341e-10 | 3.467e-11 | -2.6602e-10 | -2.867e-10 | -2.7619e-10 | 2.271e-10 | -2.0102e-10 | 1.1044e-10 | -5.5887e-11 | -4.5545e-11 | -3.6911e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.115 | 1.1198 | 1.1174 | 1.115 | 1.1198 | 1.1174 | -0.74596 | -120.6053 | 119.5084 | -0.74596 | -120.6053 | 119.5084
Line9_3_11 | 0.10944 | 0.10357 | 0.10713 | 0.10944 | 0.10357 | 0.10713 | 0.025273 | 0.023918 | 0.02474 | 0.025273 | 0.023918 | 0.02474 | -0.0024378 | -0.0016903 | -0.00079901 | 0.0025588 | 0.0018001 | 0.00090981 | -0.027489 | -0.026196 | -0.027078 | 0.027725 | 0.026414 | 0.027308 | 94.7983 | -26.435 | -148.297 | -85.2017 | 153.565 | 31.703 |  | 1.0919 | 1.0975 | 1.095 | 1.1017 | 1.1069 | 1.1044 | -0.26952 | -120.1268 | 120.0128 | -0.47468 | -120.3337 | 119.7948

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.12388 | 0.11695 | 0.1209 | 0.12388 | 0.11695 | 0.1209 | 0.028608 | 0.027008 | 0.02792 | 0.028608 | 0.027008 | 0.02792 | -0.0028585 | -0.0020317 | -0.00090179 | 0.0030134 | 0.002172 | 0.0010428 | -0.03231 | -0.030731 | -0.031745 | 0.032612 | 0.031008 | 0.032039 | 94.9849 | -26.1371 | -148.1357 | -85.0151 | 153.8629 | 31.8643 |  | 1.1338 | 1.1403 | 1.1375 | 1.1448 | 1.1509 | 1.1481 | -0.070904 | -119.9196 | 120.2371 | -0.2942 | -120.144 | 120
Line10_11_12 | 0.11081 | 0.10461 | 0.10835 | 0.11081 | 0.10461 | 0.10835 | 0.025591 | 0.024159 | 0.025022 | 0.025591 | 0.024159 | 0.025022 | -0.0027683 | -0.0019344 | -0.00094906 | 0.0028924 | 0.0020466 | 0.0010622 | -0.029389 | -0.02794 | -0.028924 | 0.029631 | 0.028162 | 0.029159 | 94.9117 | -26.3608 | -148.3079 | -85.0883 | 153.6392 | 31.6921 |  | 1.1535 | 1.1593 | 1.1566 | 1.1634 | 1.1687 | 1.1661 | -0.46935 | -120.3214 | 119.8128 | -0.66352 | -120.5174 | 119.6058
Line11_12_13 | 0.11081 | 0.10461 | 0.10835 | 0.11081 | 0.10461 | 0.10835 | 0.025591 | 0.024159 | 0.025022 | 0.025591 | 0.024159 | 0.025022 | -0.0028924 | -0.0020466 | -0.0010622 | 0.0030165 | 0.0021588 | 0.0011754 | -0.029631 | -0.028162 | -0.029159 | 0.029872 | 0.028384 | 0.029395 | 94.9117 | -26.3608 | -148.3079 | -85.0883 | 153.6392 | 31.6921 |  | 1.1634 | 1.1687 | 1.1661 | 1.1732 | 1.1783 | 1.1757 | -0.66352 | -120.5174 | 119.6058 | -0.85442 | -120.7102 | 119.4023
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5689e-09 | 1.1959e-09 | 1.7681e-10 | -1.3615e-09 | -1.1357e-09 | -4.4447e-10 | 7.7626e-10 | -6.4768e-10 | 4.0211e-10 | -5.8807e-10 | 3.7288e-10 | -3.1754e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1732 | 1.1783 | 1.1757 | 1.1732 | 1.1783 | 1.1757 | -0.85442 | -120.7102 | 119.4023 | -0.85442 | -120.7102 | 119.4023
Line13_13_14 | 0.11081 | 0.10461 | 0.10835 | 0.11081 | 0.10461 | 0.10835 | 0.025591 | 0.024159 | 0.025022 | 0.025591 | 0.024159 | 0.025022 | -0.0030165 | -0.0021588 | -0.0011754 | 0.0031406 | 0.002271 | 0.0012886 | -0.029872 | -0.028384 | -0.029395 | 0.030114 | 0.028606 | 0.02963 | 94.9117 | -26.3608 | -148.3079 | -85.0882 | 153.6392 | 31.6921 |  | 1.1732 | 1.1783 | 1.1757 | 1.1831 | 1.1878 | 1.1853 | -0.85442 | -120.7102 | 119.4023 | -1.0421 | -120.9 | 119.202
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.046e-09 | 7.9725e-10 | 1.1787e-10 | -8.3848e-10 | -7.3706e-10 | -3.8554e-10 | 5.1751e-10 | -4.3179e-10 | 2.6807e-10 | -3.2932e-10 | 1.5698e-10 | -1.835e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1732 | 1.1783 | 1.1757 | 1.1732 | 1.1783 | 1.1757 | -0.85442 | -120.7102 | 119.4023 | -0.85442 | -120.7102 | 119.4023
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2298e-10 | 3.9862e-10 | 5.8936e-11 | -3.155e-10 | -3.3844e-10 | -3.266e-10 | 2.5875e-10 | -2.1589e-10 | 1.3404e-10 | -7.0563e-11 | -5.8908e-11 | -4.9468e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1732 | 1.1783 | 1.1757 | 1.1732 | 1.1783 | 1.1757 | -0.85442 | -120.7102 | 119.4023 | -0.85442 | -120.7102 | 119.4023
Line16_4_18 | 0.037282 | 0 | 0 | 0.037282 | 0 | 0 | 0.0086099 | 0 | 0 | 0.0086099 | 0 | 0 | 0.0069614 | 3.648e-10 | -1.7949e-10 | -0.0069498 | -2.2058e-10 | -2.1131e-10 | 0.0069729 | -3.6992e-10 | 5.4197e-11 | -0.0069498 | 9.3855e-13 | 4.7604e-12 | -45.2729 | 0 | 0 | 134.7271 | 0 | 0 |  | 1.1444 | 1.1527 | 1.1502 | 1.1415 | 1.1522 | 1.1501 | -0.2253 | -120.0084 | 120.0881 | -0.27293 | -119.9884 | 120.0588
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6304e-10 | 2.7089e-10 | -1.6835e-10 | -1.4067e-10 | -1.6854e-10 | -1.5636e-10 | 2.5059e-10 | -3.2302e-10 | 4.9601e-11 | -5.6593e-12 | 6.4528e-12 | 1.8984e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1338 | 1.1403 | 1.1375 | 1.1338 | 1.1403 | 1.1375 | -0.070904 | -119.9196 | 120.2371 | -0.070904 | -119.9196 | 120.2371
Line1_1_3 | 0.11081 | 0.10461 | 0.10835 | 0.11081 | 0.10461 | 0.10835 | 0.025591 | 0.024159 | 0.025022 | 0.025591 | 0.024159 | 0.025022 | -0.0025202 | -0.00171 | -0.00072272 | 0.0026443 | 0.0018222 | 0.00083589 | -0.028907 | -0.027496 | -0.028453 | 0.029148 | 0.027718 | 0.028688 | 94.9117 | -26.3608 | -148.3079 | -85.0883 | 153.6392 | 31.6921 |  | 1.1338 | 1.1403 | 1.1375 | 1.1437 | 1.1498 | 1.147 | -0.070904 | -119.9196 | 120.2371 | -0.27184 | -120.1222 | 120.0232
Line2_1_4 | 0.11049 | 0.13209 | 0.13501 | 0.11049 | 0.13209 | 0.13501 | 0.025518 | 0.030504 | 0.03118 | 0.025518 | 0.030504 | 0.03118 | -0.0045662 | -0.010468 | -0.0091419 | 0.0046864 | 0.010633 | 0.0093345 | -0.02857 | -0.033172 | -0.034268 | 0.028823 | 0.033515 | 0.034628 | 99.0096 | -12.4055 | -134.8257 | -80.9904 | 167.5945 | 45.1743 |  | 1.1338 | 1.1403 | 1.1375 | 1.1444 | 1.1527 | 1.1502 | -0.070904 | -119.9196 | 120.2371 | -0.2253 | -120.0084 | 120.0881
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2607e-10 | 5.4178e-10 | -3.367e-10 | -5.0371e-10 | -4.3943e-10 | 1.1992e-11 | 5.0119e-10 | -6.4604e-10 | 9.9201e-11 | -2.5625e-10 | 3.2947e-10 | -3.0617e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1338 | 1.1403 | 1.1375 | 1.1338 | 1.1403 | 1.1375 | -0.070904 | -119.9196 | 120.2371 | -0.070904 | -119.9196 | 120.2371
Line4_2_6 | 0.12388 | 0.11695 | 0.1209 | 0.12388 | 0.11695 | 0.1209 | 0.028608 | 0.027008 | 0.02792 | 0.028608 | 0.027008 | 0.02792 | -0.0030134 | -0.002172 | -0.0010428 | 0.0031682 | 0.0023123 | 0.0011838 | -0.032612 | -0.031008 | -0.032039 | 0.032914 | 0.031285 | 0.032332 | 94.9849 | -26.1371 | -148.1357 | -85.0151 | 153.8629 | 31.8643 |  | 1.1448 | 1.1509 | 1.1481 | 1.1558 | 1.1615 | 1.1588 | -0.2942 | -120.144 | 120 | -0.51324 | -120.3643 | 119.7674
Line5_6_7 | 0.12388 | 0.11695 | 0.1209 | 0.12388 | 0.11695 | 0.1209 | 0.028608 | 0.027008 | 0.02792 | 0.028608 | 0.027008 | 0.02792 | -0.0031682 | -0.0023123 | -0.0011838 | 0.003323 | 0.0024527 | 0.0013248 | -0.032914 | -0.031285 | -0.032332 | 0.033216 | 0.031562 | 0.032625 | 94.9849 | -26.1371 | -148.1357 | -85.0151 | 153.8629 | 31.8643 |  | 1.1558 | 1.1615 | 1.1588 | 1.1669 | 1.1721 | 1.1695 | -0.51324 | -120.3643 | 119.7674 | -0.72815 | -120.5805 | 119.5389
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4964e-09 | 1.1289e-09 | 5.9615e-11 | -1.284e-09 | -1.0629e-09 | -3.3798e-10 | 7.7235e-10 | -7.0782e-10 | 3.6584e-10 | -5.7471e-10 | 4.2398e-10 | -2.8185e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1669 | 1.1721 | 1.1695 | 1.1669 | 1.1721 | 1.1695 | -0.72815 | -120.5805 | 119.5389 | -0.72815 | -120.5805 | 119.5389
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9879e-10 | 3.7629e-10 | 1.9872e-11 | -2.8643e-10 | -3.1028e-10 | -2.9824e-10 | 2.5745e-10 | -2.3594e-10 | 1.2195e-10 | -5.981e-11 | -4.7901e-11 | -3.7959e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1669 | 1.1721 | 1.1695 | 1.1669 | 1.1721 | 1.1695 | -0.72815 | -120.5805 | 119.5389 | -0.72815 | -120.5805 | 119.5389
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9879e-10 | 3.7629e-10 | 1.9872e-11 | -2.8643e-10 | -3.1028e-10 | -2.9824e-10 | 2.5745e-10 | -2.3594e-10 | 1.2195e-10 | -5.981e-11 | -4.7901e-11 | -3.7959e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1669 | 1.1721 | 1.1695 | 1.1669 | 1.1721 | 1.1695 | -0.72815 | -120.5805 | 119.5389 | -0.72815 | -120.5805 | 119.5389
Line9_3_11 | 0.11081 | 0.10461 | 0.10835 | 0.11081 | 0.10461 | 0.10835 | 0.025591 | 0.024159 | 0.025022 | 0.025591 | 0.024159 | 0.025022 | -0.0026443 | -0.0018222 | -0.00083589 | 0.0027683 | 0.0019344 | 0.00094906 | -0.029148 | -0.027718 | -0.028688 | 0.029389 | 0.02794 | 0.028924 | 94.9117 | -26.3608 | -148.3079 | -85.0883 | 153.6392 | 31.6921 |  | 1.1437 | 1.1498 | 1.147 | 1.1535 | 1.1593 | 1.1566 | -0.27184 | -120.1222 | 120.0232 | -0.46935 | -120.3214 | 119.8128

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.025972 | 0.025639 | 0.025571 | 0.025972 | 0.025639 | 0.025571 | 0.0059979 | 0.0059211 | 0.0059053 | 0.005998 | 0.0059211 | 0.0059053 | -0.00015404 | -0.004777 | 0.0049528 | 0.00016057 | 0.0047833 | -0.0049466 | -0.00023036 | 0.0081928 | 0.0079031 | 0.00023719 | -0.0081863 | -0.0078968 | 91.7848 | 91.566 | 91.5934 | -88.2152 | -88.434 | -88.4066 |  | 0.046203 | 1.6017 | 1.5794 | 0.047753 | 1.6013 | 1.5779 | -31.986 | -148.1887 | 149.5184 | -32.3115 | -148.1359 | 149.5298
Line10_11_12 | 0.025907 | 0.025575 | 0.025507 | 0.025907 | 0.025575 | 0.025507 | 0.0059829 | 0.0059063 | 0.0058906 | 0.005983 | 0.0059064 | 0.0058906 | -0.00016718 | -0.0047581 | 0.0049468 | 0.00017367 | 0.0047644 | -0.0049406 | -0.000243 | 0.0081706 | 0.0078588 | 0.00024979 | -0.0081642 | -0.0078524 | 91.9206 | 91.7024 | 91.7295 | -88.0794 | -88.2976 | -88.2705 |  | 0.049299 | 1.6008 | 1.5764 | 0.050849 | 1.6004 | 1.5749 | -32.6064 | -148.0834 | 149.5408 | -32.8883 | -148.0308 | 149.552
Line11_12_13 | 0.025907 | 0.025575 | 0.025507 | 0.025908 | 0.025576 | 0.025508 | 0.005983 | 0.0059064 | 0.0058906 | 0.0059831 | 0.0059064 | 0.0058907 | -0.00017367 | -0.0047644 | 0.0049406 | 0.00018016 | 0.0047708 | -0.0049345 | -0.00024979 | 0.0081642 | 0.0078524 | 0.00025659 | -0.0081578 | -0.0078461 | 91.9206 | 91.7024 | 91.7295 | -88.0794 | -88.2976 | -88.2705 |  | 0.050849 | 1.6004 | 1.5749 | 0.052401 | 1.6 | 1.5734 | -32.8883 | -148.0308 | 149.552 | -33.1535 | -147.9781 | 149.5633
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2741e-09 | 1.9403e-07 | -1.744e-07 | -4.04e-09 | -1.3382e-07 | 1.1196e-07 | 9.9179e-09 | -3.012e-07 | -3.0614e-07 | -6.7118e-09 | 1.9818e-07 | 2.068e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.052401 | 1.6 | 1.5734 | 0.052401 | 1.6 | 1.5734 | -33.1535 | -147.9781 | 149.5633 | -33.1535 | -147.9781 | 149.5633
Line13_13_14 | 0.025909 | 0.025577 | 0.025509 | 0.025909 | 0.025577 | 0.025509 | 0.0059833 | 0.0059067 | 0.0058909 | 0.0059834 | 0.0059067 | 0.005891 | -0.00018017 | -0.004771 | 0.0049346 | 0.00018666 | 0.0047773 | -0.0049285 | -0.0002566 | 0.0081581 | 0.0078464 | 0.00026339 | -0.0081517 | -0.00784 | 91.9205 | 91.7023 | 91.7293 | -88.0795 | -88.2977 | -88.2707 |  | 0.052401 | 1.6 | 1.5734 | 0.053953 | 1.5996 | 1.572 | -33.1535 | -147.9781 | 149.5633 | -33.4035 | -147.9253 | 149.5746
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1827e-09 | 1.2935e-07 | -1.1627e-07 | -1.9486e-09 | -6.9141e-08 | 5.3824e-08 | 6.6119e-09 | -2.008e-07 | -2.0409e-07 | -3.4058e-09 | 9.7785e-08 | 1.0475e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.052401 | 1.6 | 1.5734 | 0.052401 | 1.6 | 1.5734 | -33.1535 | -147.9781 | 149.5633 | -33.1535 | -147.9781 | 149.5633
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0914e-09 | 6.4676e-08 | -5.8135e-08 | 1.4275e-10 | -4.4648e-09 | -4.3104e-09 | 3.306e-09 | -1.004e-07 | -1.0205e-07 | -9.9822e-11 | -2.6147e-09 | 2.7042e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.052401 | 1.6 | 1.5734 | 0.052401 | 1.6 | 1.5734 | -33.1535 | -147.9781 | 149.5633 | -33.1535 | -147.9781 | 149.5633
Line16_4_18 | 0.23886 | 0 | 0 | 0.23886 | 0 | 0 | 0.055162 | 0 | 0 | 0.055162 | 0 | 0 | 0.00091285 | 6.6079e-08 | -5.8051e-08 | 3.6664e-15 | -4.4331e-09 | -4.2663e-09 | 0.00095089 | -1.0096e-07 | -1.0354e-07 | -4.7256e-15 | -2.597e-09 | 2.6936e-09 | -78.5167 | 0 | 0 | 101.4833 | 0 | 0 |  | 0.023896 | 1.5992 | 1.5731 | 0 | 1.5971 | 1.5684 | -32.3476 | -147.9818 | 149.5353 | 0 | -147.8272 | 149.5411
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.779e-09 | 6.5178e-08 | -5.8237e-08 | 1.2868e-10 | -4.489e-09 | -4.3591e-09 | 2.9752e-09 | -1.0094e-07 | -1.0318e-07 | -8.5251e-11 | -2.6355e-09 | 2.7107e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.046203 | 1.6017 | 1.5794 | 0.046203 | 1.6017 | 1.5794 | -31.986 | -148.1887 | 149.5184 | -31.986 | -148.1887 | 149.5184
Line1_1_3 | 0.025906 | 0.025574 | 0.025506 | 0.025907 | 0.025575 | 0.025507 | 0.0059828 | 0.0059061 | 0.0058904 | 0.0059829 | 0.0059062 | 0.0058905 | -0.0001542 | -0.0047454 | 0.0049591 | 0.00016069 | 0.0047518 | -0.0049529 | -0.00022941 | 0.0081834 | 0.0078715 | 0.00023621 | -0.008177 | -0.0078651 | 91.9207 | 91.7025 | 91.7296 | -88.0793 | -88.2975 | -88.2704 |  | 0.046203 | 1.6017 | 1.5794 | 0.04775 | 1.6013 | 1.5779 | -31.986 | -148.1887 | 149.5184 | -32.3063 | -148.1361 | 149.5296
Line2_1_4 | 0.21292 | 0.025713 | 0.025592 | 0.21292 | 0.025714 | 0.025592 | 0.049171 | 0.0059382 | 0.0059101 | 0.049171 | 0.0059383 | 0.0059102 | 0.001599 | -0.0048251 | 0.0049428 | -0.00083225 | 0.0048472 | -0.0049209 | 0.0016138 | 0.0081963 | 0.0079184 | -0.0008294 | -0.0081663 | -0.0078886 | -77.2492 | 91.3262 | 91.4913 | 102.7508 | -88.6738 | -88.5087 |  | 0.046203 | 1.6017 | 1.5794 | 0.023896 | 1.5992 | 1.5731 | -31.986 | -148.1887 | 149.5184 | -32.3476 | -147.9818 | 149.5353
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.558e-09 | 1.3036e-07 | -1.1647e-07 | -1.6503e-09 | -6.9667e-08 | 5.3878e-08 | 5.9504e-09 | -2.0187e-07 | -2.0636e-07 | -3.0604e-09 | 9.8302e-08 | 1.0589e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.046203 | 1.6017 | 1.5794 | 0.046203 | 1.6017 | 1.5794 | -31.986 | -148.1887 | 149.5184 | -31.986 | -148.1887 | 149.5184
Line4_2_6 | 0.025972 | 0.025639 | 0.025571 | 0.025972 | 0.02564 | 0.025571 | 0.005998 | 0.0059211 | 0.0059053 | 0.0059981 | 0.0059212 | 0.0059054 | -0.00016057 | -0.0047833 | 0.0049466 | 0.00016709 | 0.0047897 | -0.0049405 | -0.00023719 | 0.0081863 | 0.0078968 | 0.00024402 | -0.0081799 | -0.0078904 | 91.7847 | 91.566 | 91.5934 | -88.2153 | -88.434 | -88.4066 |  | 0.047753 | 1.6013 | 1.5779 | 0.049306 | 1.6009 | 1.5764 | -32.3115 | -148.1359 | 149.5298 | -32.6165 | -148.0831 | 149.5411
Line5_6_7 | 0.025972 | 0.02564 | 0.025571 | 0.025973 | 0.02564 | 0.025572 | 0.0059981 | 0.0059212 | 0.0059054 | 0.0059982 | 0.0059213 | 0.0059055 | -0.00016709 | -0.0047897 | 0.0049404 | 0.00017361 | 0.0047961 | -0.0049343 | -0.00024402 | 0.0081799 | 0.0078904 | 0.00025084 | -0.0081734 | -0.007884 | 91.7847 | 91.5659 | 91.5933 | -88.2153 | -88.4341 | -88.4067 |  | 0.049306 | 1.6009 | 1.5764 | 0.050859 | 1.6004 | 1.5749 | -32.6165 | -148.0831 | 149.5411 | -32.9028 | -148.0303 | 149.5525
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0435e-09 | 1.944e-07 | -1.7448e-07 | -3.8897e-09 | -1.3407e-07 | 1.12e-07 | 9.6719e-09 | -3.016e-07 | -3.0699e-07 | -6.5442e-09 | 1.9845e-07 | 2.0736e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.050859 | 1.6004 | 1.5749 | 0.050859 | 1.6004 | 1.5749 | -32.9028 | -148.0303 | 149.5525 | -32.9028 | -148.0303 | 149.5525
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0145e-09 | 6.4801e-08 | -5.8161e-08 | 1.3926e-10 | -4.4709e-09 | -4.3225e-09 | 3.224e-09 | -1.0053e-07 | -1.0233e-07 | -9.6236e-11 | -2.6198e-09 | 2.7058e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.050859 | 1.6004 | 1.5749 | 0.050859 | 1.6004 | 1.5749 | -32.9028 | -148.0303 | 149.5525 | -32.9028 | -148.0303 | 149.5525
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0145e-09 | 6.4801e-08 | -5.8161e-08 | 1.3926e-10 | -4.4709e-09 | -4.3225e-09 | 3.224e-09 | -1.0053e-07 | -1.0233e-07 | -9.6236e-11 | -2.6198e-09 | 2.7058e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.050859 | 1.6004 | 1.5749 | 0.050859 | 1.6004 | 1.5749 | -32.9028 | -148.0303 | 149.5525 | -32.9028 | -148.0303 | 149.5525
Line9_3_11 | 0.025907 | 0.025575 | 0.025507 | 0.025907 | 0.025575 | 0.025507 | 0.0059829 | 0.0059062 | 0.0058905 | 0.0059829 | 0.0059063 | 0.0058906 | -0.00016069 | -0.0047518 | 0.0049529 | 0.00016718 | 0.0047581 | -0.0049468 | -0.00023621 | 0.008177 | 0.0078651 | 0.000243 | -0.0081706 | -0.0078588 | 91.9207 | 91.7025 | 91.7295 | -88.0793 | -88.2975 | -88.2705 |  | 0.04775 | 1.6013 | 1.5779 | 0.049299 | 1.6008 | 1.5764 | -32.3063 | -148.1361 | 149.5296 | -32.6064 | -148.0834 | 149.5408

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.024605 | 0.02429 | 0.024225 | 0.024605 | 0.02429 | 0.024225 | 0.0056823 | 0.0056094 | 0.0055945 | 0.0056823 | 0.0056095 | 0.0055945 | -0.00013825 | -0.0042874 | 0.0044452 | 0.00014411 | 0.0042931 | -0.0044396 | -0.00020675 | 0.0073531 | 0.0070931 | 0.00021288 | -0.0073473 | -0.0070874 | 91.7848 | 91.566 | 91.5934 | -88.2152 | -88.434 | -88.4066 |  | 0.043771 | 1.5174 | 1.4963 | 0.04524 | 1.517 | 1.4949 | -31.986 | -148.1887 | 149.5184 | -32.3115 | -148.1359 | 149.5298
Line10_11_12 | 0.024543 | 0.024229 | 0.024164 | 0.024544 | 0.024229 | 0.024165 | 0.0056681 | 0.0055954 | 0.0055805 | 0.0056681 | 0.0055955 | 0.0055806 | -0.00015004 | -0.0042704 | 0.0044398 | 0.00015587 | 0.0042761 | -0.0044342 | -0.00021809 | 0.0073332 | 0.0070533 | 0.00022419 | -0.0073274 | -0.0070476 | 91.9206 | 91.7024 | 91.7295 | -88.0794 | -88.2976 | -88.2705 |  | 0.046704 | 1.5166 | 1.4935 | 0.048173 | 1.5162 | 1.492 | -32.6064 | -148.0834 | 149.5408 | -32.8883 | -148.0308 | 149.552
Line11_12_13 | 0.024544 | 0.024229 | 0.024165 | 0.024544 | 0.024229 | 0.024165 | 0.0056681 | 0.0055955 | 0.0055806 | 0.0056682 | 0.0055956 | 0.0055807 | -0.00015587 | -0.0042761 | 0.0044342 | 0.00016169 | 0.0042818 | -0.0044287 | -0.00022419 | 0.0073274 | 0.0070476 | 0.00023029 | -0.0073217 | -0.0070419 | 91.9206 | 91.7024 | 91.7295 | -88.0794 | -88.2976 | -88.2705 |  | 0.048173 | 1.5162 | 1.492 | 0.049643 | 1.5158 | 1.4906 | -32.8883 | -148.0308 | 149.552 | -33.1535 | -147.9781 | 149.5633
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.631e-09 | 1.7414e-07 | -1.5653e-07 | -3.6259e-09 | -1.201e-07 | 1.0048e-07 | 8.9014e-09 | -2.7033e-07 | -2.7476e-07 | -6.0239e-09 | 1.7787e-07 | 1.856e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.049643 | 1.5158 | 1.4906 | 0.049643 | 1.5158 | 1.4906 | -33.1535 | -147.9781 | 149.5633 | -33.1535 | -147.9781 | 149.5633
Line13_13_14 | 0.024545 | 0.02423 | 0.024166 | 0.024545 | 0.024231 | 0.024166 | 0.0056684 | 0.0055958 | 0.0055809 | 0.0056685 | 0.0055958 | 0.005581 | -0.0001617 | -0.004282 | 0.0044289 | 0.00016753 | 0.0042876 | -0.0044233 | -0.0002303 | 0.0073219 | 0.0070422 | 0.0002364 | -0.0073162 | -0.0070365 | 91.9205 | 91.7023 | 91.7293 | -88.0795 | -88.2977 | -88.2707 |  | 0.049643 | 1.5158 | 1.4906 | 0.051114 | 1.5154 | 1.4892 | -33.1535 | -147.9781 | 149.5633 | -33.4035 | -147.9253 | 149.5746
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.754e-09 | 1.1609e-07 | -1.0435e-07 | -1.7489e-09 | -6.2054e-08 | 4.8308e-08 | 5.9343e-09 | -1.8022e-07 | -1.8318e-07 | -3.0567e-09 | 8.7763e-08 | 9.4015e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.049643 | 1.5158 | 1.4906 | 0.049643 | 1.5158 | 1.4906 | -33.1535 | -147.9781 | 149.5633 | -33.1535 | -147.9781 | 149.5633
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.877e-09 | 5.8047e-08 | -5.2176e-08 | 1.2812e-10 | -4.0072e-09 | -3.8686e-09 | 2.9671e-09 | -9.0109e-08 | -9.1588e-08 | -8.9591e-11 | -2.3467e-09 | 2.427e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.049643 | 1.5158 | 1.4906 | 0.049643 | 1.5158 | 1.4906 | -33.1535 | -147.9781 | 149.5633 | -33.1535 | -147.9781 | 149.5633
Line16_4_18 | 0.22629 | 0 | 0 | 0.22629 | 0 | 0 | 0.052259 | 0 | 0 | 0.052259 | 0 | 0 | 0.00081929 | 5.9306e-08 | -5.2102e-08 | 3.2954e-15 | -3.9788e-09 | -3.829e-09 | 0.00085343 | -9.0616e-08 | -9.2924e-08 | -4.2276e-15 | -2.3308e-09 | 2.4175e-09 | -78.5167 | 0 | 0 | 101.4833 | 0 | 0 |  | 0.022638 | 1.515 | 1.4904 | 0 | 1.5131 | 1.4858 | -32.3476 | -147.9818 | 149.5353 | 0 | -147.8272 | 149.5411
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5967e-09 | 5.8497e-08 | -5.2268e-08 | 1.1549e-10 | -4.0289e-09 | -3.9124e-09 | 2.6703e-09 | -9.0592e-08 | -9.2605e-08 | -7.6513e-11 | -2.3654e-09 | 2.4328e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.043771 | 1.5174 | 1.4963 | 0.043771 | 1.5174 | 1.4963 | -31.986 | -148.1887 | 149.5184 | -31.986 | -148.1887 | 149.5184
Line1_1_3 | 0.024543 | 0.024228 | 0.024164 | 0.024543 | 0.024229 | 0.024164 | 0.0056679 | 0.0055953 | 0.0055804 | 0.005668 | 0.0055954 | 0.0055805 | -0.00013839 | -0.0042591 | 0.0044508 | 0.00014422 | 0.0042647 | -0.0044453 | -0.0002059 | 0.0073447 | 0.0070647 | 0.000212 | -0.0073389 | -0.007059 | 91.9207 | 91.7025 | 91.7296 | -88.0793 | -88.2975 | -88.2704 |  | 0.043771 | 1.5174 | 1.4963 | 0.045237 | 1.517 | 1.4949 | -31.986 | -148.1887 | 149.5184 | -32.3063 | -148.1361 | 149.5296
Line2_1_4 | 0.20171 | 0.02436 | 0.024245 | 0.20171 | 0.02436 | 0.024245 | 0.046583 | 0.0056257 | 0.0055991 | 0.046583 | 0.0056257 | 0.0055991 | 0.0014351 | -0.0043306 | 0.0044362 | -0.00074695 | 0.0043504 | -0.0044166 | 0.0014484 | 0.0073563 | 0.0071069 | -0.00074439 | -0.0073293 | -0.0070801 | -77.2492 | 91.3262 | 91.4913 | 102.7508 | -88.6738 | -88.5087 |  | 0.043771 | 1.5174 | 1.4963 | 0.022638 | 1.515 | 1.4904 | -31.986 | -148.1887 | 149.5184 | -32.3476 | -147.9818 | 149.5353
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1933e-09 | 1.1699e-07 | -1.0454e-07 | -1.4812e-09 | -6.2526e-08 | 4.8356e-08 | 5.3405e-09 | -1.8118e-07 | -1.8521e-07 | -2.7468e-09 | 8.8227e-08 | 9.5038e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.043771 | 1.5174 | 1.4963 | 0.043771 | 1.5174 | 1.4963 | -31.986 | -148.1887 | 149.5184 | -31.986 | -148.1887 | 149.5184
Line4_2_6 | 0.024605 | 0.02429 | 0.024225 | 0.024606 | 0.02429 | 0.024225 | 0.0056823 | 0.0056095 | 0.0055945 | 0.0056824 | 0.0056096 | 0.0055946 | -0.00014411 | -0.0042931 | 0.0044396 | 0.00014996 | 0.0042988 | -0.0044341 | -0.00021288 | 0.0073473 | 0.0070874 | 0.00021901 | -0.0073415 | -0.0070817 | 91.7847 | 91.566 | 91.5934 | -88.2153 | -88.434 | -88.4066 |  | 0.04524 | 1.517 | 1.4949 | 0.046711 | 1.5166 | 1.4935 | -32.3115 | -148.1359 | 149.5298 | -32.6165 | -148.0831 | 149.5411
Line5_6_7 | 0.024606 | 0.02429 | 0.024225 | 0.024606 | 0.02429 | 0.024226 | 0.0056824 | 0.0056096 | 0.0055946 | 0.0056825 | 0.0056096 | 0.0055947 | -0.00014996 | -0.0042988 | 0.0044341 | 0.00015582 | 0.0043045 | -0.0044285 | -0.00021901 | 0.0073415 | 0.0070817 | 0.00022513 | -0.0073357 | -0.0070759 | 91.7847 | 91.5659 | 91.5933 | -88.2153 | -88.4341 | -88.4067 |  | 0.046711 | 1.5166 | 1.4935 | 0.048183 | 1.5162 | 1.492 | -32.6165 | -148.0831 | 149.5411 | -32.9028 | -148.0303 | 149.5525
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4241e-09 | 1.7448e-07 | -1.566e-07 | -3.4911e-09 | -1.2033e-07 | 1.0052e-07 | 8.6806e-09 | -2.7069e-07 | -2.7552e-07 | -5.8734e-09 | 1.7811e-07 | 1.8611e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.048183 | 1.5162 | 1.492 | 0.048183 | 1.5162 | 1.492 | -32.9028 | -148.0303 | 149.5525 | -32.9028 | -148.0303 | 149.5525
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.808e-09 | 5.8159e-08 | -5.22e-08 | 1.2498e-10 | -4.0127e-09 | -3.8795e-09 | 2.8935e-09 | -9.023e-08 | -9.1841e-08 | -8.6373e-11 | -2.3513e-09 | 2.4285e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.048183 | 1.5162 | 1.492 | 0.048183 | 1.5162 | 1.492 | -32.9028 | -148.0303 | 149.5525 | -32.9028 | -148.0303 | 149.5525
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.808e-09 | 5.8159e-08 | -5.22e-08 | 1.2498e-10 | -4.0127e-09 | -3.8795e-09 | 2.8935e-09 | -9.023e-08 | -9.1841e-08 | -8.6373e-11 | -2.3513e-09 | 2.4285e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.048183 | 1.5162 | 1.492 | 0.048183 | 1.5162 | 1.492 | -32.9028 | -148.0303 | 149.5525 | -32.9028 | -148.0303 | 149.5525
Line9_3_11 | 0.024543 | 0.024229 | 0.024164 | 0.024543 | 0.024229 | 0.024164 | 0.005668 | 0.0055954 | 0.0055805 | 0.0056681 | 0.0055954 | 0.0055805 | -0.00014422 | -0.0042647 | 0.0044453 | 0.00015004 | 0.0042704 | -0.0044398 | -0.000212 | 0.0073389 | 0.007059 | 0.00021809 | -0.0073332 | -0.0070533 | 91.9207 | 91.7025 | 91.7295 | -88.0793 | -88.2975 | -88.2705 |  | 0.045237 | 1.517 | 1.4949 | 0.046704 | 1.5166 | 1.4935 | -32.3063 | -148.1361 | 149.5296 | -32.6064 | -148.0834 | 149.5408

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0030376 | 0.0029987 | 0.0029907 | 0.0030377 | 0.0029988 | 0.0029908 | 0.00070151 | 0.00069252 | 0.00069068 | 0.00070152 | 0.00069253 | 0.00069069 | -0.00034887 | -0.00031492 | 0.00065619 | 0.00034896 | 0.00031501 | -0.00065612 | -0.00049287 | 0.0006493 | 5.5489e-05 | 0.00049297 | -0.00064922 | -5.5401e-05 | 121.5986 | 121.3798 | 121.4072 | -58.4014 | -58.6202 | -58.5928 |  | 0.86078 | 1.042 | 0.95347 | 0.86096 | 1.042 | 0.95333 | -3.6933 | -122.7464 | 126.2408 | -3.6951 | -122.7371 | 126.2337
Line10_11_12 | 0.0030301 | 0.0029912 | 0.0029833 | 0.0030301 | 0.0029913 | 0.0029833 | 0.00069976 | 0.00069079 | 0.00068896 | 0.00069977 | 0.0006908 | 0.00068897 | -0.00034934 | -0.00031276 | 0.00065452 | 0.00034943 | 0.00031285 | -0.00065444 | -0.000491 | 0.00064825 | 5.3619e-05 | 0.0004911 | -0.00064817 | -5.3531e-05 | 121.7345 | 121.5163 | 121.5433 | -58.2655 | -58.4837 | -58.4567 |  | 0.86115 | 1.0419 | 0.9532 | 0.86133 | 1.0419 | 0.95307 | -3.6968 | -122.7279 | 126.2266 | -3.6985 | -122.7187 | 126.2195
Line11_12_13 | 0.0030301 | 0.0029913 | 0.0029833 | 0.0030301 | 0.0029913 | 0.0029833 | 0.00069977 | 0.0006908 | 0.00068897 | 0.00069978 | 0.00069081 | 0.00068897 | -0.00034943 | -0.00031285 | 0.00065444 | 0.00034953 | 0.00031294 | -0.00065437 | -0.0004911 | 0.00064817 | 5.3532e-05 | 0.0004912 | -0.00064809 | -5.3444e-05 | 121.7344 | 121.5162 | 121.5433 | -58.2656 | -58.4838 | -58.4567 |  | 0.86133 | 1.0419 | 0.95307 | 0.86151 | 1.0418 | 0.95293 | -3.6985 | -122.7187 | 126.2195 | -3.7003 | -122.7095 | 126.2124
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2184e-08 | 1.2912e-08 | -2.4762e-08 | -7.8495e-09 | -8.9626e-09 | 1.6479e-08 | 1.8995e-08 | -2.4036e-08 | -3.1132e-09 | -1.2857e-08 | 1.5853e-08 | 2.4347e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86151 | 1.0418 | 0.95293 | 0.86151 | 1.0418 | 0.95293 | -3.7003 | -122.7095 | 126.2124 | -3.7003 | -122.7095 | 126.2124
Line13_13_14 | 0.0030302 | 0.0029914 | 0.0029835 | 0.0030303 | 0.0029915 | 0.0029835 | 0.0006998 | 0.00069084 | 0.000689 | 0.00069981 | 0.00069085 | 0.00068901 | -0.00034954 | -0.00031295 | 0.00065439 | 0.00034963 | 0.00031304 | -0.00065432 | -0.00049122 | 0.00064811 | 5.3447e-05 | 0.00049132 | -0.00064803 | -5.336e-05 | 121.7343 | 121.5161 | 121.5432 | -58.2657 | -58.4839 | -58.4568 |  | 0.86151 | 1.0418 | 0.95293 | 0.86169 | 1.0417 | 0.9528 | -3.7003 | -122.7095 | 126.2124 | -3.7021 | -122.7003 | 126.2054
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1228e-09 | 8.6079e-09 | -1.6508e-08 | -3.7881e-09 | -4.6587e-09 | 8.2244e-09 | 1.2663e-08 | -1.6024e-08 | -2.0755e-09 | -6.5253e-09 | 7.8406e-09 | 1.3969e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86151 | 1.0418 | 0.95293 | 0.86151 | 1.0418 | 0.95293 | -3.7003 | -122.7095 | 126.2124 | -3.7003 | -122.7095 | 126.2124
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0614e-09 | 4.304e-09 | -8.2542e-09 | 2.7327e-10 | -3.5473e-10 | -2.974e-11 | 6.3316e-09 | -8.0121e-09 | -1.0377e-09 | -1.9367e-10 | -1.7155e-10 | 3.5921e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86151 | 1.0418 | 0.95293 | 0.86151 | 1.0418 | 0.95293 | -3.7003 | -122.7095 | 126.2124 | -3.7003 | -122.7095 | 126.2124
Line16_4_18 | 0.027937 | 0 | 0 | 0.027937 | 0 | 0 | 0.0064517 | 0 | 0 | 0.0064517 | 0 | 0 | 0.0039148 | 4.4092e-09 | -8.3366e-09 | -0.0039023 | -3.5309e-10 | -2.8492e-11 | 0.0039153 | -8.0666e-09 | -1.1093e-09 | -0.0039023 | -1.6987e-10 | 3.573e-10 | -48.7029 | 0 | 0 | 131.2971 | 0 | 0 |  | 0.85817 | 1.0417 | 0.95298 | 0.85538 | 1.0414 | 0.95263 | -3.6991 | -122.7106 | 126.2075 | -3.7029 | -122.684 | 126.1813
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0472e-09 | 4.3597e-09 | -8.2946e-09 | 2.7536e-10 | -3.5587e-10 | -3.1801e-11 | 6.3778e-09 | -8.0363e-09 | -1.0871e-09 | -1.9314e-10 | -1.7392e-10 | 3.6104e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86078 | 1.042 | 0.95347 | 0.86078 | 1.042 | 0.95347 | -3.6933 | -122.7464 | 126.2408 | -3.6933 | -122.7464 | 126.2408
Line1_1_3 | 0.00303 | 0.0029911 | 0.0029832 | 0.00303 | 0.0029912 | 0.0029832 | 0.00069974 | 0.00069078 | 0.00068894 | 0.00069975 | 0.00069078 | 0.00068895 | -0.00034915 | -0.00031258 | 0.00065467 | 0.00034925 | 0.00031267 | -0.0006546 | -0.0004908 | 0.00064841 | 5.3794e-05 | 0.0004909 | -0.00064833 | -5.3706e-05 | 121.7346 | 121.5163 | 121.5434 | -58.2655 | -58.4837 | -58.4566 |  | 0.86078 | 1.042 | 0.95347 | 0.86096 | 1.042 | 0.95333 | -3.6933 | -122.7464 | 126.2408 | -3.695 | -122.7372 | 126.2337
Line2_1_4 | 0.024902 | 0.0030074 | 0.0029932 | 0.024902 | 0.0030074 | 0.0029932 | 0.005751 | 0.00069453 | 0.00069124 | 0.005751 | 0.00069454 | 0.00069125 | 0.0035764 | -0.00031855 | 0.00065663 | -0.0035659 | 0.00031886 | -0.00065634 | 0.0034227 | 0.00064986 | 5.6704e-05 | -0.003412 | -0.00064945 | -5.6295e-05 | -47.4354 | 121.14 | 121.3052 | 132.5646 | -58.86 | -58.6948 |  | 0.86078 | 1.042 | 0.95347 | 0.85817 | 1.0417 | 0.95298 | -3.6933 | -122.7464 | 126.2408 | -3.6991 | -122.7106 | 126.2075
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0944e-09 | 8.7194e-09 | -1.6589e-08 | -3.7718e-09 | -4.7156e-09 | 8.2628e-09 | 1.2756e-08 | -1.6073e-08 | -2.1743e-09 | -6.571e-09 | 7.8624e-09 | 1.4482e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86078 | 1.042 | 0.95347 | 0.86078 | 1.042 | 0.95347 | -3.6933 | -122.7464 | 126.2408 | -3.6933 | -122.7464 | 126.2408
Line4_2_6 | 0.0030377 | 0.0029988 | 0.0029908 | 0.0030377 | 0.0029988 | 0.0029908 | 0.00070152 | 0.00069253 | 0.00069069 | 0.00070153 | 0.00069254 | 0.00069069 | -0.00034896 | -0.00031501 | 0.00065612 | 0.00034906 | 0.0003151 | -0.00065604 | -0.00049297 | 0.00064922 | 5.5401e-05 | 0.00049307 | -0.00064914 | -5.5313e-05 | 121.5986 | 121.3798 | 121.4072 | -58.4014 | -58.6202 | -58.5928 |  | 0.86096 | 1.042 | 0.95333 | 0.86115 | 1.0419 | 0.9532 | -3.6951 | -122.7371 | 126.2337 | -3.6969 | -122.7279 | 126.2266
Line5_6_7 | 0.0030377 | 0.0029988 | 0.0029908 | 0.0030378 | 0.0029988 | 0.0029908 | 0.00070153 | 0.00069254 | 0.00069069 | 0.00070154 | 0.00069255 | 0.0006907 | -0.00034906 | -0.0003151 | 0.00065604 | 0.00034915 | 0.00031519 | -0.00065596 | -0.00049307 | 0.00064914 | 5.5313e-05 | 0.00049317 | -0.00064906 | -5.5225e-05 | 121.5986 | 121.3798 | 121.4072 | -58.4014 | -58.6202 | -58.5928 |  | 0.86115 | 1.0419 | 0.9532 | 0.86133 | 1.0419 | 0.95306 | -3.6969 | -122.7279 | 126.2266 | -3.6986 | -122.7186 | 126.2195
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2174e-08 | 1.2953e-08 | -2.4793e-08 | -7.8422e-09 | -8.9905e-09 | 1.6498e-08 | 1.9029e-08 | -2.4055e-08 | -3.1498e-09 | -1.288e-08 | 1.5864e-08 | 2.4595e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86133 | 1.0419 | 0.95306 | 0.86133 | 1.0419 | 0.95306 | -3.6986 | -122.7186 | 126.2195 | -3.6986 | -122.7186 | 126.2195
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.058e-09 | 4.3178e-09 | -8.2643e-09 | 2.7379e-10 | -3.5502e-10 | -3.0249e-11 | 6.3431e-09 | -8.0182e-09 | -1.0499e-09 | -1.9355e-10 | -1.7213e-10 | 3.5967e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86133 | 1.0419 | 0.95306 | 0.86133 | 1.0419 | 0.95306 | -3.6986 | -122.7186 | 126.2195 | -3.6986 | -122.7186 | 126.2195
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.058e-09 | 4.3178e-09 | -8.2643e-09 | 2.7379e-10 | -3.5502e-10 | -3.0249e-11 | 6.3431e-09 | -8.0182e-09 | -1.0499e-09 | -1.9355e-10 | -1.7213e-10 | 3.5967e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86133 | 1.0419 | 0.95306 | 0.86133 | 1.0419 | 0.95306 | -3.6986 | -122.7186 | 126.2195 | -3.6986 | -122.7186 | 126.2195
Line9_3_11 | 0.00303 | 0.0029912 | 0.0029832 | 0.0030301 | 0.0029912 | 0.0029833 | 0.00069975 | 0.00069078 | 0.00068895 | 0.00069976 | 0.00069079 | 0.00068896 | -0.00034925 | -0.00031267 | 0.0006546 | 0.00034934 | 0.00031276 | -0.00065452 | -0.0004909 | 0.00064833 | 5.3706e-05 | 0.000491 | -0.00064825 | -5.3619e-05 | 121.7345 | 121.5163 | 121.5434 | -58.2655 | -58.4837 | -58.4566 |  | 0.86096 | 1.042 | 0.95333 | 0.86115 | 1.0419 | 0.9532 | -3.695 | -122.7372 | 126.2337 | -3.6968 | -122.7279 | 126.2266

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0028778 | 0.0028409 | 0.0028333 | 0.0028778 | 0.0028409 | 0.0028333 | 0.00066459 | 0.00065607 | 0.00065432 | 0.0006646 | 0.00065608 | 0.00065433 | -0.00031311 | -0.00028264 | 0.00058894 | 0.0003132 | 0.00028272 | -0.00058887 | -0.00044236 | 0.00058275 | 4.9802e-05 | 0.00044245 | -0.00058268 | -4.9722e-05 | 121.5986 | 121.3798 | 121.4072 | -58.4014 | -58.6202 | -58.5928 |  | 0.81548 | 0.9872 | 0.90328 | 0.81565 | 0.98715 | 0.90316 | -3.6933 | -122.7464 | 126.2408 | -3.6951 | -122.7371 | 126.2337
Line10_11_12 | 0.0028706 | 0.0028338 | 0.0028263 | 0.0028706 | 0.0028338 | 0.0028263 | 0.00066293 | 0.00065444 | 0.0006527 | 0.00066294 | 0.00065444 | 0.0006527 | -0.00031354 | -0.0002807 | 0.00058744 | 0.00031362 | 0.00028078 | -0.00058737 | -0.00044068 | 0.00058181 | 4.8123e-05 | 0.00044077 | -0.00058174 | -4.8045e-05 | 121.7345 | 121.5163 | 121.5433 | -58.2655 | -58.4837 | -58.4567 |  | 0.81582 | 0.98709 | 0.90303 | 0.81599 | 0.98703 | 0.9029 | -3.6968 | -122.7279 | 126.2266 | -3.6985 | -122.7187 | 126.2195
Line11_12_13 | 0.0028706 | 0.0028338 | 0.0028263 | 0.0028706 | 0.0028339 | 0.0028263 | 0.00066294 | 0.00065444 | 0.0006527 | 0.00066295 | 0.00065445 | 0.00065271 | -0.00031362 | -0.00028078 | 0.00058737 | 0.0003137 | 0.00028086 | -0.0005873 | -0.00044077 | 0.00058174 | 4.8045e-05 | 0.00044086 | -0.00058166 | -4.7966e-05 | 121.7344 | 121.5162 | 121.5433 | -58.2656 | -58.4838 | -58.4567 |  | 0.81599 | 0.98703 | 0.9029 | 0.81617 | 0.98697 | 0.90278 | -3.6985 | -122.7187 | 126.2195 | -3.7003 | -122.7095 | 126.2124
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0935e-08 | 1.1588e-08 | -2.2225e-08 | -7.045e-09 | -8.044e-09 | 1.479e-08 | 1.7048e-08 | -2.1573e-08 | -2.7941e-09 | -1.1539e-08 | 1.4228e-08 | 2.1852e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81617 | 0.98697 | 0.90278 | 0.81617 | 0.98697 | 0.90278 | -3.7003 | -122.7095 | 126.2124 | -3.7003 | -122.7095 | 126.2124
Line13_13_14 | 0.0028708 | 0.002834 | 0.0028264 | 0.0028708 | 0.002834 | 0.0028265 | 0.00066297 | 0.00065448 | 0.00065274 | 0.00066298 | 0.00065449 | 0.00065275 | -0.00031371 | -0.00028088 | 0.00058732 | 0.0003138 | 0.00028096 | -0.00058725 | -0.00044087 | 0.00058169 | 4.7969e-05 | 0.00044096 | -0.00058161 | -4.7891e-05 | 121.7343 | 121.5161 | 121.5432 | -58.2657 | -58.4839 | -58.4568 |  | 0.81617 | 0.98697 | 0.90278 | 0.81634 | 0.98691 | 0.90265 | -3.7003 | -122.7095 | 126.2124 | -3.7021 | -122.7003 | 126.2054
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2903e-09 | 7.7257e-09 | -1.4816e-08 | -3.3999e-09 | -4.1812e-09 | 7.3815e-09 | 1.1365e-08 | -1.4382e-08 | -1.8628e-09 | -5.8565e-09 | 7.037e-09 | 1.2538e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81617 | 0.98697 | 0.90278 | 0.81617 | 0.98697 | 0.90278 | -3.7003 | -122.7095 | 126.2124 | -3.7003 | -122.7095 | 126.2124
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6451e-09 | 3.8628e-09 | -7.4082e-09 | 2.4527e-10 | -3.1837e-10 | -2.6692e-11 | 5.6827e-09 | -7.191e-09 | -9.3138e-10 | -1.7382e-10 | -1.5396e-10 | 3.2239e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81617 | 0.98697 | 0.90278 | 0.81617 | 0.98697 | 0.90278 | -3.7003 | -122.7095 | 126.2124 | -3.7003 | -122.7095 | 126.2124
Line16_4_18 | 0.026466 | 0 | 0 | 0.026466 | 0 | 0 | 0.0061121 | 0 | 0 | 0.0061121 | 0 | 0 | 0.0035135 | 3.9573e-09 | -7.4821e-09 | -0.0035023 | -3.169e-10 | -2.5572e-11 | 0.003514 | -7.2398e-09 | -9.9558e-10 | -0.0035023 | -1.5246e-10 | 3.2068e-10 | -48.7029 | 0 | 0 | 131.2971 | 0 | 0 |  | 0.81301 | 0.98688 | 0.90283 | 0.81036 | 0.98661 | 0.9025 | -3.6991 | -122.7106 | 126.2075 | -3.7029 | -122.684 | 126.1813
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6324e-09 | 3.9129e-09 | -7.4444e-09 | 2.4714e-10 | -3.194e-10 | -2.8542e-11 | 5.7241e-09 | -7.2126e-09 | -9.7572e-10 | -1.7335e-10 | -1.561e-10 | 3.2404e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81548 | 0.9872 | 0.90328 | 0.81548 | 0.9872 | 0.90328 | -3.6933 | -122.7464 | 126.2408 | -3.6933 | -122.7464 | 126.2408
Line1_1_3 | 0.0028705 | 0.0028337 | 0.0028262 | 0.0028705 | 0.0028338 | 0.0028262 | 0.00066291 | 0.00065442 | 0.00065268 | 0.00066292 | 0.00065443 | 0.00065269 | -0.00031337 | -0.00028054 | 0.00058757 | 0.00031345 | 0.00028062 | -0.00058751 | -0.0004405 | 0.00058195 | 4.828e-05 | 0.00044059 | -0.00058188 | -4.8201e-05 | 121.7346 | 121.5163 | 121.5434 | -58.2655 | -58.4837 | -58.4566 |  | 0.81548 | 0.9872 | 0.90328 | 0.81565 | 0.98714 | 0.90316 | -3.6933 | -122.7464 | 126.2408 | -3.695 | -122.7372 | 126.2337
Line2_1_4 | 0.023592 | 0.0028491 | 0.0028356 | 0.023592 | 0.0028491 | 0.0028357 | 0.0054483 | 0.00065797 | 0.00065486 | 0.0054483 | 0.00065798 | 0.00065487 | 0.0032099 | -0.0002859 | 0.00058933 | -0.0032004 | 0.00028618 | -0.00058907 | 0.0030719 | 0.00058325 | 5.0892e-05 | -0.0030623 | -0.00058289 | -5.0525e-05 | -47.4354 | 121.14 | 121.3052 | 132.5646 | -58.86 | -58.6948 |  | 0.81548 | 0.9872 | 0.90328 | 0.81301 | 0.98688 | 0.90283 | -3.6933 | -122.7464 | 126.2408 | -3.6991 | -122.7106 | 126.2075
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2648e-09 | 7.8257e-09 | -1.4889e-08 | -3.3852e-09 | -4.2323e-09 | 7.4159e-09 | 1.1448e-08 | -1.4425e-08 | -1.9514e-09 | -5.8975e-09 | 7.0566e-09 | 1.2998e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.81548 | 0.9872 | 0.90328 | 0.81548 | 0.9872 | 0.90328 | -3.6933 | -122.7464 | 126.2408 | -3.6933 | -122.7464 | 126.2408
Line4_2_6 | 0.0028778 | 0.0028409 | 0.0028333 | 0.0028778 | 0.002841 | 0.0028334 | 0.0006646 | 0.00065608 | 0.00065433 | 0.00066461 | 0.00065609 | 0.00065434 | -0.0003132 | -0.00028272 | 0.00058887 | 0.00031328 | 0.0002828 | -0.0005888 | -0.00044245 | 0.00058268 | 4.9723e-05 | 0.00044254 | -0.00058261 | -4.9644e-05 | 121.5986 | 121.3798 | 121.4072 | -58.4014 | -58.6202 | -58.5928 |  | 0.81565 | 0.98715 | 0.90316 | 0.81582 | 0.98709 | 0.90303 | -3.6951 | -122.7371 | 126.2337 | -3.6969 | -122.7279 | 126.2266
Line5_6_7 | 0.0028778 | 0.002841 | 0.0028334 | 0.0028779 | 0.002841 | 0.0028334 | 0.00066461 | 0.00065609 | 0.00065434 | 0.00066462 | 0.0006561 | 0.00065435 | -0.00031328 | -0.0002828 | 0.0005888 | 0.00031336 | 0.00028288 | -0.00058873 | -0.00044254 | 0.00058261 | 4.9644e-05 | 0.00044263 | -0.00058254 | -4.9565e-05 | 121.5986 | 121.3798 | 121.4072 | -58.4014 | -58.6202 | -58.5928 |  | 0.81582 | 0.98709 | 0.90303 | 0.816 | 0.98703 | 0.9029 | -3.6969 | -122.7279 | 126.2266 | -3.6986 | -122.7186 | 126.2195
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0926e-08 | 1.1626e-08 | -2.2252e-08 | -7.0384e-09 | -8.0691e-09 | 1.4807e-08 | 1.7079e-08 | -2.1589e-08 | -2.827e-09 | -1.156e-08 | 1.4238e-08 | 2.2074e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.816 | 0.98703 | 0.9029 | 0.816 | 0.98703 | 0.9029 | -3.6986 | -122.7186 | 126.2195 | -3.6986 | -122.7186 | 126.2195
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6421e-09 | 3.8752e-09 | -7.4172e-09 | 2.4573e-10 | -3.1863e-10 | -2.7148e-11 | 5.693e-09 | -7.1964e-09 | -9.4232e-10 | -1.7371e-10 | -1.5449e-10 | 3.228e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.816 | 0.98703 | 0.9029 | 0.816 | 0.98703 | 0.9029 | -3.6986 | -122.7186 | 126.2195 | -3.6986 | -122.7186 | 126.2195
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6421e-09 | 3.8752e-09 | -7.4172e-09 | 2.4573e-10 | -3.1863e-10 | -2.7148e-11 | 5.693e-09 | -7.1964e-09 | -9.4232e-10 | -1.7371e-10 | -1.5449e-10 | 3.228e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.816 | 0.98703 | 0.9029 | 0.816 | 0.98703 | 0.9029 | -3.6986 | -122.7186 | 126.2195 | -3.6986 | -122.7186 | 126.2195
Line9_3_11 | 0.0028705 | 0.0028338 | 0.0028262 | 0.0028706 | 0.0028338 | 0.0028263 | 0.00066292 | 0.00065443 | 0.00065269 | 0.00066293 | 0.00065444 | 0.0006527 | -0.00031345 | -0.00028062 | 0.00058751 | 0.00031354 | 0.0002807 | -0.00058744 | -0.00044059 | 0.00058188 | 4.8202e-05 | 0.00044068 | -0.00058181 | -4.8123e-05 | 121.7345 | 121.5163 | 121.5434 | -58.2655 | -58.4837 | -58.4566 |  | 0.81565 | 0.98714 | 0.90316 | 0.81582 | 0.98709 | 0.90303 | -3.695 | -122.7372 | 126.2337 | -3.6968 | -122.7279 | 126.2266

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.19175 | 0.51231 | 0.55745 | 0.19175 | 0.51231 | 0.55745 | 0.044282 | 0.11831 | 0.12874 | 0.044282 | 0.11831 | 0.12874 | 0.0097445 | 0.027302 | -0.083452 | -0.0097113 | -0.0265 | 0.086678 | 0.057108 | -0.073081 | -0.038958 | -0.057089 | 0.077264 | 0.042878 | -78.0701 | -43.4365 | -106.0714 | 101.9298 | 136.5635 | 73.9286 |  | 1.3083 | 0.6594 | 0.71538 | 1.3077 | 0.6904 | 0.75117 | 2.2466 | -112.9515 | 98.9531 | 2.2758 | -114.5056 | 100.2496
Line10_11_12 | 0.17701 | 0.46383 | 0.49772 | 0.17701 | 0.46383 | 0.49772 | 0.040879 | 0.10712 | 0.11494 | 0.040879 | 0.10712 | 0.11494 | 0.013183 | 0.021972 | -0.080684 | -0.013173 | -0.021298 | 0.083274 | 0.051745 | -0.073478 | -0.038774 | -0.051704 | 0.076881 | 0.041875 | -73.4632 | -42.2298 | -104.381 | 106.5368 | 137.7702 | 75.619 |  | 1.3062 | 0.71598 | 0.77878 | 1.3052 | 0.74477 | 0.81091 | 2.2441 | -115.5816 | 101.2864 | 2.2428 | -116.7455 | 102.3153
Line11_12_13 | 0.17701 | 0.46383 | 0.49772 | 0.17701 | 0.46383 | 0.49772 | 0.040879 | 0.10712 | 0.11494 | 0.040879 | 0.10712 | 0.11494 | 0.013173 | 0.021298 | -0.083274 | -0.013164 | -0.020625 | 0.085864 | 0.051704 | -0.076881 | -0.041875 | -0.051663 | 0.080285 | 0.044977 | -73.4632 | -42.2298 | -104.381 | 106.5368 | 137.7702 | 75.619 |  | 1.3052 | 0.74477 | 0.81091 | 1.3042 | 0.77384 | 0.84328 | 2.2428 | -116.7455 | 102.3153 | 2.2415 | -117.8224 | 103.2656
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3603e-08 | -3.959e-08 | 5.3003e-08 | 7.8493e-09 | 2.7175e-08 | -3.4833e-08 | -8.3112e-08 | 3.3054e-08 | 2.0525e-09 | 5.5604e-08 | -2.1923e-08 | -2.3032e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3042 | 0.77384 | 0.84328 | 1.3042 | 0.77384 | 0.84328 | 2.2415 | -117.8224 | 103.2656 | 2.2415 | -117.8224 | 103.2656
Line13_13_14 | 0.17701 | 0.46383 | 0.49772 | 0.17701 | 0.46383 | 0.49772 | 0.040879 | 0.10712 | 0.11494 | 0.040879 | 0.10712 | 0.11494 | 0.013164 | 0.020625 | -0.085864 | -0.013155 | -0.019951 | 0.088454 | 0.051663 | -0.080285 | -0.044977 | -0.051623 | 0.083688 | 0.048079 | -73.4632 | -42.2299 | -104.381 | 106.5368 | 137.7701 | 75.619 |  | 1.3042 | 0.77384 | 0.84328 | 1.3032 | 0.80317 | 0.87587 | 2.2415 | -117.8224 | 103.2656 | 2.2402 | -118.821 | 104.1453
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.0688e-09 | -2.6394e-08 | 3.5335e-08 | 3.3149e-09 | 1.3978e-08 | -1.7166e-08 | -5.5408e-08 | 2.2036e-08 | 1.3683e-09 | 2.79e-08 | -1.0905e-08 | -1.619e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3042 | 0.77384 | 0.84328 | 1.3042 | 0.77384 | 0.84328 | 2.2415 | -117.8224 | 103.2656 | 2.2415 | -117.8224 | 103.2656
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5344e-09 | -1.3197e-08 | 1.7668e-08 | -1.2195e-09 | 7.8142e-10 | 5.0168e-10 | -2.7704e-08 | 1.1018e-08 | 6.8417e-10 | 1.9639e-10 | 1.132e-10 | -9.3483e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3042 | 0.77384 | 0.84328 | 1.3042 | 0.77384 | 0.84328 | 2.2415 | -117.8224 | 103.2656 | 2.2415 | -117.8224 | 103.2656
Line16_4_18 | 0 | 3.8647 | 4.3154 | 0 | 3.8647 | 4.3154 | 0 | 0.89251 | 0.99659 | 0 | 0.89251 | 0.99659 | -8.2477e-10 | 0.09883 | 0.21586 | -7.0957e-10 | 7.8243e-14 | 3.4944e-14 | -4.0031e-08 | 0.30555 | 0.32384 | 3.3221e-10 | 8.3622e-15 | 9.2542e-15 | 0 | 172.8895 | 43.8122 | 0 | -7.1105 | -136.1878 |  | 1.2618 | 0.35981 | 0.39052 | 1.2076 | 0 | 0 | 3.2567 | -115.0343 | 100.1256 | 4.0976 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9162e-09 | -1.5761e-08 | 1.8301e-08 | -1.2429e-09 | 9.2521e-10 | 6.9398e-10 | -3.4686e-08 | 8.9859e-09 | 9.3284e-10 | 1.9745e-10 | 3.1152e-10 | -9.8913e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3083 | 0.6594 | 0.71538 | 1.3083 | 0.6594 | 0.71538 | 2.2466 | -112.9515 | 98.9531 | 2.2466 | -112.9515 | 98.9531
Line1_1_3 | 0.17701 | 0.46383 | 0.49772 | 0.17701 | 0.46383 | 0.49772 | 0.040879 | 0.10712 | 0.11494 | 0.040879 | 0.10712 | 0.11494 | 0.013201 | 0.02332 | -0.075504 | -0.013192 | -0.022646 | 0.078094 | 0.051826 | -0.066671 | -0.03257 | -0.051785 | 0.070075 | 0.035672 | -73.4632 | -42.2298 | -104.381 | 106.5368 | 137.7702 | 75.619 |  | 1.3083 | 0.6594 | 0.71538 | 1.3073 | 0.6875 | 0.74693 | 2.2466 | -112.9515 | 98.9531 | 2.2454 | -114.3206 | 100.1692
Line2_1_4 | 0.20275 | 3.1722 | 3.4885 | 0.20275 | 3.1722 | 3.4885 | 0.046823 | 0.73259 | 0.80564 | 0.046823 | 0.73259 | 0.80564 | -0.020115 | 0.18701 | 0.29351 | 0.02038 | -0.11081 | -0.15465 | 0.057862 | 0.4454 | 0.496 | -0.055453 | -0.23917 | -0.27398 | -106.9228 | 179.8248 | 39.5686 | 73.0772 | -0.17521 | -140.4314 |  | 1.3083 | 0.6594 | 0.71538 | 1.2618 | 0.35981 | 0.39052 | 2.2466 | -112.9515 | 98.9531 | 3.2567 | -115.0343 | 100.1256
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8324e-09 | -3.1523e-08 | 3.6602e-08 | 1.6733e-09 | 1.6687e-08 | -1.7607e-08 | -6.9372e-08 | 1.7972e-08 | 1.8657e-09 | 3.4884e-08 | -8.6744e-09 | -1.922e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3083 | 0.6594 | 0.71538 | 1.3083 | 0.6594 | 0.71538 | 2.2466 | -112.9515 | 98.9531 | 2.2466 | -112.9515 | 98.9531
Line4_2_6 | 0.19175 | 0.51231 | 0.55745 | 0.19175 | 0.51231 | 0.55745 | 0.044282 | 0.11831 | 0.12874 | 0.044282 | 0.11831 | 0.12874 | 0.0097113 | 0.0265 | -0.086678 | -0.0096781 | -0.025698 | 0.089904 | 0.057089 | -0.077264 | -0.042878 | -0.05707 | 0.081447 | 0.046799 | -78.0702 | -43.4365 | -106.0714 | 101.9298 | 136.5635 | 73.9286 |  | 1.3077 | 0.6904 | 0.75117 | 1.3072 | 0.72186 | 0.7873 | 2.2758 | -114.5056 | 100.2496 | 2.305 | -115.9252 | 101.4276
Line5_6_7 | 0.19175 | 0.51231 | 0.55745 | 0.19175 | 0.51231 | 0.55745 | 0.044282 | 0.11831 | 0.12874 | 0.044282 | 0.11831 | 0.12874 | 0.0096781 | 0.025698 | -0.089904 | -0.0096449 | -0.024896 | 0.093131 | 0.05707 | -0.081447 | -0.046799 | -0.05705 | 0.08563 | 0.05072 | -78.0702 | -43.4365 | -106.0714 | 101.9298 | 136.5635 | 73.9286 |  | 1.3072 | 0.72186 | 0.7873 | 1.3066 | 0.75373 | 0.82373 | 2.305 | -115.9252 | 101.4276 | 2.3342 | -117.2255 | 102.5018
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3284e-08 | -4.0969e-08 | 5.3898e-08 | 7.6226e-09 | 2.8128e-08 | -3.5396e-08 | -8.7021e-08 | 3.2691e-08 | 1.9369e-09 | 5.8219e-08 | -2.1654e-08 | -2.2448e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3066 | 0.75373 | 0.82373 | 1.3066 | 0.75373 | 0.82373 | 2.3342 | -117.2255 | 102.5018 | 2.3342 | -117.2255 | 102.5018
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4281e-09 | -1.3656e-08 | 1.7966e-08 | -1.2336e-09 | 8.1539e-10 | 5.3665e-10 | -2.9007e-08 | 1.0897e-08 | 6.4563e-10 | 2.0488e-10 | 1.4047e-10 | -9.5356e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3066 | 0.75373 | 0.82373 | 1.3066 | 0.75373 | 0.82373 | 2.3342 | -117.2255 | 102.5018 | 2.3342 | -117.2255 | 102.5018
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4281e-09 | -1.3656e-08 | 1.7966e-08 | -1.2336e-09 | 8.1539e-10 | 5.3665e-10 | -2.9007e-08 | 1.0897e-08 | 6.4563e-10 | 2.0488e-10 | 1.4047e-10 | -9.5356e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3066 | 0.75373 | 0.82373 | 1.3066 | 0.75373 | 0.82373 | 2.3342 | -117.2255 | 102.5018 | 2.3342 | -117.2255 | 102.5018
Line9_3_11 | 0.17701 | 0.46383 | 0.49772 | 0.17701 | 0.46383 | 0.49772 | 0.040879 | 0.10712 | 0.11494 | 0.040879 | 0.10712 | 0.11494 | 0.013192 | 0.022646 | -0.078094 | -0.013183 | -0.021972 | 0.080684 | 0.051785 | -0.070075 | -0.035672 | -0.051745 | 0.073478 | 0.038774 | -73.4632 | -42.2298 | -104.381 | 106.5368 | 137.7702 | 75.619 |  | 1.3073 | 0.6875 | 0.74693 | 1.3062 | 0.71598 | 0.77878 | 2.2454 | -114.3206 | 100.1692 | 2.2441 | -115.5816 | 101.2864

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.19668 | 0.52267 | 0.57085 | 0.19668 | 0.52267 | 0.57085 | 0.045421 | 0.12071 | 0.13183 | 0.045421 | 0.12071 | 0.13183 | 0.0095905 | 0.028639 | -0.088177 | -0.0095473 | -0.027813 | 0.091562 | 0.061646 | -0.077013 | -0.041166 | -0.061624 | 0.08138 | 0.045286 | -78.9066 | -43.3499 | -106.466 | 101.0934 | 136.6501 | 73.534 |  | 1.3735 | 0.6807 | 0.73816 | 1.3729 | 0.71249 | 0.77484 | 2.2505 | -112.9509 | 98.5598 | 2.2867 | -114.4811 | 99.8504
Line10_11_12 | 0.18205 | 0.47497 | 0.51185 | 0.18205 | 0.47497 | 0.51185 | 0.042044 | 0.10969 | 0.11821 | 0.042044 | 0.10969 | 0.11821 | 0.013278 | 0.023194 | -0.085568 | -0.013261 | -0.022495 | 0.088308 | 0.056108 | -0.077662 | -0.041207 | -0.056066 | 0.081243 | 0.044495 | -74.4216 | -42.1795 | -104.8249 | 105.5784 | 137.8205 | 75.1751 |  | 1.3714 | 0.73891 | 0.80346 | 1.3703 | 0.76852 | 0.83654 | 2.2638 | -115.5513 | 100.8892 | 2.2705 | -116.7026 | 101.9168
Line11_12_13 | 0.18205 | 0.47497 | 0.51185 | 0.18206 | 0.47497 | 0.51185 | 0.042044 | 0.10969 | 0.11821 | 0.042044 | 0.10969 | 0.11821 | 0.013261 | 0.022495 | -0.088308 | -0.013245 | -0.021797 | 0.091048 | 0.056066 | -0.081243 | -0.044495 | -0.056023 | 0.084824 | 0.047782 | -74.4216 | -42.1795 | -104.8249 | 105.5784 | 137.8204 | 75.1751 |  | 1.3703 | 0.76852 | 0.83654 | 1.3692 | 0.79842 | 0.86988 | 2.2705 | -116.7026 | 101.9168 | 2.2772 | -117.7681 | 102.8658
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4736e-08 | -4.4029e-08 | 5.8457e-08 | 8.4679e-09 | 3.0233e-08 | -3.8393e-08 | -9.3528e-08 | 3.623e-08 | 2.1999e-09 | 6.2572e-08 | -2.4028e-08 | -2.5003e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3692 | 0.79842 | 0.86988 | 1.3692 | 0.79842 | 0.86988 | 2.2772 | -117.7681 | 102.8658 | 2.2772 | -117.7681 | 102.8658
Line13_13_14 | 0.18206 | 0.47497 | 0.51185 | 0.18206 | 0.47497 | 0.51185 | 0.042044 | 0.10969 | 0.11821 | 0.042044 | 0.10969 | 0.11821 | 0.013245 | 0.021797 | -0.091048 | -0.013228 | -0.021099 | 0.093788 | 0.056023 | -0.084824 | -0.047782 | -0.055981 | 0.088404 | 0.05107 | -74.4216 | -42.1796 | -104.8249 | 105.5784 | 137.8204 | 75.1751 |  | 1.3692 | 0.79842 | 0.86988 | 1.3682 | 0.82858 | 0.90344 | 2.2772 | -117.7681 | 102.8658 | 2.2838 | -118.7564 | 103.7446
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.8239e-09 | -2.9353e-08 | 3.8971e-08 | 3.556e-09 | 1.5557e-08 | -1.8907e-08 | -6.2352e-08 | 2.4153e-08 | 1.4666e-09 | 3.1396e-08 | -1.1951e-08 | -1.767e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3692 | 0.79842 | 0.86988 | 1.3692 | 0.79842 | 0.86988 | 2.2772 | -117.7681 | 102.8658 | 2.2772 | -117.7681 | 102.8658
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.912e-09 | -1.4676e-08 | 1.9486e-08 | -1.356e-09 | 8.8044e-10 | 5.7826e-10 | -3.1176e-08 | 1.2077e-08 | 7.3331e-10 | 2.1943e-10 | 1.2541e-10 | -1.0336e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3692 | 0.79842 | 0.86988 | 1.3692 | 0.79842 | 0.86988 | 2.2772 | -117.7681 | 102.8658 | 2.2772 | -117.7681 | 102.8658
Line16_4_18 | 0 | 3.9759 | 4.4382 | 0 | 3.9759 | 4.4382 | 0 | 0.91819 | 1.025 | 0 | 0.91819 | 1.025 | -8.5012e-10 | 0.10523 | 0.2282 | -8.0902e-10 | 1.3178e-13 | 9.7626e-14 | -4.4376e-08 | 0.32365 | 0.34321 | 3.6313e-10 | -4.4568e-14 | -3.8481e-14 | 0 | 173.0223 | 43.3487 | 0 | -6.9777 | -136.6513 |  | 1.3259 | 0.37065 | 0.40211 | 1.2709 | 0 | 0 | 3.24 | -114.9894 | 99.7292 | 4.0625 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1358e-09 | -1.7316e-08 | 2.0034e-08 | -1.3818e-09 | 1.0258e-09 | 7.7332e-10 | -3.8672e-08 | 9.8035e-09 | 9.4625e-10 | 2.1754e-10 | 3.3693e-10 | -1.0883e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3735 | 0.6807 | 0.73816 | 1.3735 | 0.6807 | 0.73816 | 2.2505 | -112.9509 | 98.5598 | 2.2505 | -112.9509 | 98.5598
Line1_1_3 | 0.18205 | 0.47497 | 0.51185 | 0.18205 | 0.47497 | 0.51185 | 0.042044 | 0.10969 | 0.11821 | 0.042044 | 0.10969 | 0.11821 | 0.013312 | 0.024591 | -0.080088 | -0.013295 | -0.023892 | 0.082828 | 0.056193 | -0.070501 | -0.034632 | -0.05615 | 0.074082 | 0.037919 | -74.4216 | -42.1795 | -104.8249 | 105.5784 | 137.8205 | 75.1751 |  | 1.3735 | 0.6807 | 0.73816 | 1.3724 | 0.70963 | 0.77065 | 2.2505 | -112.9509 | 98.5598 | 2.2571 | -114.3044 | 99.7739
Line2_1_4 | 0.20744 | 3.2799 | 3.6067 | 0.20744 | 3.2799 | 3.6067 | 0.047907 | 0.75747 | 0.83293 | 0.047907 | 0.75747 | 0.83293 | -0.021324 | 0.19962 | 0.31267 | 0.02162 | -0.11783 | -0.1644 | 0.06225 | 0.4754 | 0.5294 | -0.059728 | -0.25483 | -0.29181 | -106.6587 | 179.8261 | 39.1263 | 73.3413 | -0.17386 | -140.8737 |  | 1.3735 | 0.6807 | 0.73816 | 1.3259 | 0.37065 | 0.40211 | 2.2505 | -112.9509 | 98.5598 | 3.24 | -114.9894 | 99.7292
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.2716e-09 | -3.4632e-08 | 4.0069e-08 | 1.754e-09 | 1.8342e-08 | -1.9261e-08 | -7.7343e-08 | 1.9607e-08 | 1.8925e-09 | 3.8889e-08 | -9.4666e-09 | -2.0345e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3735 | 0.6807 | 0.73816 | 1.3735 | 0.6807 | 0.73816 | 2.2505 | -112.9509 | 98.5598 | 2.2505 | -112.9509 | 98.5598
Line4_2_6 | 0.19668 | 0.52267 | 0.57085 | 0.19668 | 0.52267 | 0.57085 | 0.045421 | 0.12071 | 0.13183 | 0.045421 | 0.12071 | 0.13183 | 0.0095473 | 0.027813 | -0.091562 | -0.0095041 | -0.026987 | 0.094948 | 0.061624 | -0.08138 | -0.045286 | -0.061603 | 0.085748 | 0.049405 | -78.9066 | -43.3499 | -106.466 | 101.0934 | 136.6501 | 73.534 |  | 1.3729 | 0.71249 | 0.77484 | 1.3723 | 0.74474 | 0.81188 | 2.2867 | -114.4811 | 99.8504 | 2.323 | -115.8798 | 101.0239
Line5_6_7 | 0.19668 | 0.52267 | 0.57085 | 0.19668 | 0.52268 | 0.57085 | 0.045421 | 0.12071 | 0.13183 | 0.045421 | 0.12071 | 0.13183 | 0.0095041 | 0.026987 | -0.094948 | -0.009461 | -0.026161 | 0.098333 | 0.061603 | -0.085748 | -0.049405 | -0.061582 | 0.090116 | 0.053525 | -78.9066 | -43.3499 | -106.466 | 101.0934 | 136.6501 | 73.534 |  | 1.3723 | 0.74474 | 0.81188 | 1.3717 | 0.77739 | 0.84923 | 2.323 | -115.8798 | 101.0239 | 2.3593 | -117.1616 | 102.0945
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4334e-08 | -4.5486e-08 | 5.9342e-08 | 8.1848e-09 | 3.124e-08 | -3.8947e-08 | -9.7794e-08 | 3.575e-08 | 2.0687e-09 | 6.5423e-08 | -2.3678e-08 | -2.4322e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3717 | 0.77739 | 0.84923 | 1.3717 | 0.77739 | 0.84923 | 2.3593 | -117.1616 | 102.0945 | 2.3593 | -117.1616 | 102.0945
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7781e-09 | -1.5162e-08 | 1.9781e-08 | -1.3713e-09 | 9.1572e-10 | 6.1495e-10 | -3.2598e-08 | 1.1917e-08 | 6.8958e-10 | 2.2775e-10 | 1.5527e-10 | -1.0531e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3717 | 0.77739 | 0.84923 | 1.3717 | 0.77739 | 0.84923 | 2.3593 | -117.1616 | 102.0945 | 2.3593 | -117.1616 | 102.0945
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7781e-09 | -1.5162e-08 | 1.9781e-08 | -1.3713e-09 | 9.1572e-10 | 6.1495e-10 | -3.2598e-08 | 1.1917e-08 | 6.8958e-10 | 2.2775e-10 | 1.5527e-10 | -1.0531e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3717 | 0.77739 | 0.84923 | 1.3717 | 0.77739 | 0.84923 | 2.3593 | -117.1616 | 102.0945 | 2.3593 | -117.1616 | 102.0945
Line9_3_11 | 0.18205 | 0.47497 | 0.51185 | 0.18205 | 0.47497 | 0.51185 | 0.042044 | 0.10969 | 0.11821 | 0.042044 | 0.10969 | 0.11821 | 0.013295 | 0.023892 | -0.082828 | -0.013278 | -0.023194 | 0.085568 | 0.05615 | -0.074082 | -0.037919 | -0.056108 | 0.077662 | 0.041207 | -74.4216 | -42.1795 | -104.8249 | 105.5784 | 137.8205 | 75.1751 |  | 1.3724 | 0.70963 | 0.77065 | 1.3714 | 0.73891 | 0.80346 | 2.2571 | -114.3044 | 99.7739 | 2.2638 | -115.5513 | 100.8892

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11693 | 0.12345 | 0.11981 | 0.11693 | 0.12345 | 0.11981 | 0.027004 | 0.028511 | 0.027668 | 0.027004 | 0.028511 | 0.027668 | -0.0010948 | -0.0018474 | -0.0028725 | 0.0012301 | 0.0019962 | 0.0030208 | -0.029352 | -0.030786 | -0.029864 | 0.02963 | 0.031087 | 0.03015 | 92.3375 | -26.5083 | -144.5994 | -87.6625 | 153.4917 | 35.4006 |  | 1.0877 | 1.0818 | 1.0843 | 1.0982 | 1.0926 | 1.0951 | 0.2013 | -119.9423 | 119.9065 | -0.039854 | -120.1825 | 119.6791
Line10_11_12 | 0.1043 | 0.11011 | 0.10666 | 0.1043 | 0.11011 | 0.10666 | 0.024087 | 0.025428 | 0.024632 | 0.024087 | 0.025428 | 0.024632 | -0.0010819 | -0.00184 | -0.0027296 | 0.0011894 | 0.0019585 | 0.0028472 | -0.026627 | -0.027939 | -0.027046 | 0.026848 | 0.028178 | 0.027273 | 92.0978 | -26.6014 | -144.7351 | -87.9022 | 153.3986 | 35.2649 |  | 1.1064 | 1.1011 | 1.1036 | 1.1157 | 1.1108 | 1.1132 | -0.22901 | -120.3694 | 119.5019 | -0.43876 | -120.5774 | 119.3049
Line11_12_13 | 0.1043 | 0.11011 | 0.10666 | 0.1043 | 0.11011 | 0.10666 | 0.024087 | 0.025428 | 0.024632 | 0.024087 | 0.025428 | 0.024632 | -0.0011894 | -0.0019585 | -0.0028472 | 0.0012968 | 0.002077 | 0.0029649 | -0.026848 | -0.028178 | -0.027273 | 0.02707 | 0.028417 | 0.027499 | 92.0978 | -26.6014 | -144.7351 | -87.9022 | 153.3986 | 35.2649 |  | 1.1157 | 1.1108 | 1.1132 | 1.1251 | 1.1205 | 1.1229 | -0.43876 | -120.5774 | 119.3049 | -0.64501 | -120.7817 | 119.1112
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9015e-10 | 7.1653e-10 | 1.5961e-09 | -5.7023e-10 | -7.6795e-10 | -1.3646e-09 | -3.4643e-10 | 8.8827e-10 | -2.2837e-11 | 1.8219e-10 | -6.5103e-10 | -5.1834e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1251 | 1.1205 | 1.1229 | 1.1251 | 1.1205 | 1.1229 | -0.64501 | -120.7817 | 119.1112 | -0.64501 | -120.7817 | 119.1112
Line13_13_14 | 0.1043 | 0.11011 | 0.10666 | 0.1043 | 0.11011 | 0.10666 | 0.024087 | 0.025428 | 0.024632 | 0.024087 | 0.025428 | 0.024632 | -0.0012968 | -0.0020771 | -0.0029649 | 0.0014043 | 0.0021956 | 0.0030825 | -0.02707 | -0.028417 | -0.027499 | 0.027291 | 0.028657 | 0.027726 | 92.0978 | -26.6014 | -144.7351 | -87.9022 | 153.3986 | 35.2649 |  | 1.1251 | 1.1205 | 1.1229 | 1.1345 | 1.1303 | 1.1325 | -0.64501 | -120.7817 | 119.1112 | -0.84785 | -120.9825 | 118.9208
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.601e-10 | 4.7769e-10 | 1.0641e-09 | -4.4018e-10 | -5.2911e-10 | -8.3259e-10 | -2.3096e-10 | 5.9218e-10 | -1.5225e-11 | 6.6715e-11 | -3.5495e-10 | -5.9446e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1251 | 1.1205 | 1.1229 | 1.1251 | 1.1205 | 1.1229 | -0.64501 | -120.7817 | 119.1112 | -0.64501 | -120.7817 | 119.1112
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3005e-10 | 2.3884e-10 | 5.3205e-10 | -3.1013e-10 | -2.9026e-10 | -3.0055e-10 | -1.1548e-10 | 2.9609e-10 | -7.6124e-12 | -4.8763e-11 | -5.8858e-11 | -6.7059e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1251 | 1.1205 | 1.1229 | 1.1251 | 1.1205 | 1.1229 | -0.64501 | -120.7817 | 119.1112 | -0.64501 | -120.7817 | 119.1112
Line16_4_18 | 0 | 0.035581 | 0.035642 | 0 | 0.035581 | 0.035642 | 0 | 0.008217 | 0.0082312 | 0 | 0.008217 | 0.0082312 | -1.6879e-11 | 0.0063379 | 0.0063671 | -1.99e-10 | -0.0063299 | -0.0063518 | -2.7772e-10 | 0.006355 | 0.0063733 | 4.9286e-12 | -0.0063299 | -0.0063518 | 0 | -165.2107 | 74.7478 | 0 | 14.7893 | -105.2522 |  | 1.0999 | 1.0923 | 1.0945 | 1.0994 | 1.0894 | 1.0913 | 0.075988 | -120.1335 | 119.7755 | 0.066718 | -120.2107 | 119.7478
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3452e-11 | 3.6699e-11 | 4.1951e-10 | -1.5028e-10 | -1.2594e-10 | -1.3654e-10 | -2.3097e-10 | 2.7043e-10 | -5.4106e-11 | 1.4712e-11 | 4.1928e-12 | -6.8107e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0877 | 1.0818 | 1.0843 | 1.0877 | 1.0818 | 1.0843 | 0.2013 | -119.9423 | 119.9065 | 0.2013 | -119.9423 | 119.9065
Line1_1_3 | 0.1043 | 0.11011 | 0.10666 | 0.1043 | 0.11011 | 0.10666 | 0.024087 | 0.025428 | 0.024632 | 0.024087 | 0.025428 | 0.024632 | -0.00086703 | -0.001603 | -0.0024942 | 0.00097448 | 0.0017215 | 0.0026119 | -0.026185 | -0.02746 | -0.026593 | 0.026406 | 0.027699 | 0.026819 | 92.0978 | -26.6014 | -144.7351 | -87.9022 | 153.3986 | 35.2649 |  | 1.0877 | 1.0818 | 1.0843 | 1.097 | 1.0914 | 1.094 | 0.2013 | -119.9423 | 119.9065 | -0.015688 | -120.1578 | 119.7024
Line2_1_4 | 0.13178 | 0.11161 | 0.10812 | 0.13178 | 0.11161 | 0.10812 | 0.030434 | 0.025775 | 0.02497 | 0.030434 | 0.025775 | 0.02497 | -0.009268 | -0.0039085 | -0.0050832 | 0.0094426 | 0.0040395 | 0.0051921 | -0.031778 | -0.027607 | -0.026595 | 0.032115 | 0.027862 | 0.026831 | 106.4606 | -21.8841 | -139.2726 | -73.5394 | 158.1159 | 40.7274 |  | 1.0877 | 1.0818 | 1.0843 | 1.0999 | 1.0923 | 1.0945 | 0.2013 | -119.9423 | 119.9065 | 0.075988 | -120.1335 | 119.7755
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.6903e-11 | 7.3398e-11 | 8.3902e-10 | -1.0682e-10 | -1.6264e-10 | -5.5605e-10 | -4.6195e-10 | 5.4086e-10 | -1.0821e-10 | 2.4568e-10 | -2.6624e-10 | 4.7296e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0877 | 1.0818 | 1.0843 | 1.0877 | 1.0818 | 1.0843 | 0.2013 | -119.9423 | 119.9065 | 0.2013 | -119.9423 | 119.9065
Line4_2_6 | 0.11693 | 0.12345 | 0.11981 | 0.11693 | 0.12345 | 0.11981 | 0.027004 | 0.028511 | 0.027668 | 0.027004 | 0.028511 | 0.027668 | -0.0012301 | -0.0019962 | -0.0030208 | 0.0013654 | 0.0021451 | 0.0031691 | -0.02963 | -0.031087 | -0.03015 | 0.029908 | 0.031388 | 0.030435 | 92.3375 | -26.5083 | -144.5994 | -87.6625 | 153.4917 | 35.4006 |  | 1.0982 | 1.0926 | 1.0951 | 1.1087 | 1.1035 | 1.106 | -0.039854 | -120.1825 | 119.6791 | -0.27644 | -120.4179 | 119.4561
Line5_6_7 | 0.11693 | 0.12345 | 0.11981 | 0.11693 | 0.12345 | 0.11981 | 0.027004 | 0.028511 | 0.027668 | 0.027004 | 0.028511 | 0.027668 | -0.0013654 | -0.0021451 | -0.0031691 | 0.0015007 | 0.002294 | 0.0033174 | -0.029908 | -0.031388 | -0.030435 | 0.030186 | 0.031689 | 0.030721 | 92.3375 | -26.5083 | -144.5994 | -87.6625 | 153.4917 | 35.4006 |  | 1.1087 | 1.1035 | 1.106 | 1.1192 | 1.1144 | 1.1168 | -0.27644 | -120.4179 | 119.4561 | -0.50859 | -120.6487 | 119.2374
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9869e-10 | 6.2092e-10 | 1.5447e-09 | -4.8324e-10 | -6.7738e-10 | -1.3037e-09 | -4.0342e-10 | 8.8154e-10 | -5.1457e-11 | 2.307e-10 | -6.3627e-10 | -2.2919e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1192 | 1.1144 | 1.1168 | 1.1192 | 1.1144 | 1.1168 | -0.50859 | -120.6487 | 119.2374 | -0.50859 | -120.6487 | 119.2374
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9565e-11 | 2.0697e-10 | 5.1492e-10 | -2.8411e-10 | -2.6343e-10 | -2.7391e-10 | -1.3447e-10 | 2.9385e-10 | -1.7152e-11 | -3.8247e-11 | -4.8578e-11 | -5.7224e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1192 | 1.1144 | 1.1168 | 1.1192 | 1.1144 | 1.1168 | -0.50859 | -120.6487 | 119.2374 | -0.50859 | -120.6487 | 119.2374
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9565e-11 | 2.0697e-10 | 5.1492e-10 | -2.8411e-10 | -2.6343e-10 | -2.7391e-10 | -1.3447e-10 | 2.9385e-10 | -1.7152e-11 | -3.8247e-11 | -4.8578e-11 | -5.7224e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1192 | 1.1144 | 1.1168 | 1.1192 | 1.1144 | 1.1168 | -0.50859 | -120.6487 | 119.2374 | -0.50859 | -120.6487 | 119.2374
Line9_3_11 | 0.1043 | 0.11011 | 0.10666 | 0.1043 | 0.11011 | 0.10666 | 0.024087 | 0.025428 | 0.024632 | 0.024087 | 0.025428 | 0.024632 | -0.00097449 | -0.0017215 | -0.0026119 | 0.0010819 | 0.00184 | 0.0027296 | -0.026406 | -0.027699 | -0.026819 | 0.026627 | 0.027939 | 0.027046 | 92.0978 | -26.6014 | -144.7351 | -87.9022 | 153.3986 | 35.2649 |  | 1.097 | 1.0914 | 1.094 | 1.1064 | 1.1011 | 1.1036 | -0.015688 | -120.1578 | 119.7024 | -0.22901 | -120.3694 | 119.5019

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11765 | 0.12451 | 0.1207 | 0.11765 | 0.12451 | 0.1207 | 0.02717 | 0.028754 | 0.027874 | 0.02717 | 0.028754 | 0.027874 | -0.0011591 | -0.0019854 | -0.0031139 | 0.001296 | 0.0021367 | 0.0032646 | -0.030946 | -0.032527 | -0.031515 | 0.031228 | 0.032833 | 0.031805 | 92.3477 | -26.4549 | -144.4619 | -87.6523 | 153.5451 | 35.5381 |  | 1.1398 | 1.1333 | 1.1361 | 1.1503 | 1.1443 | 1.147 | 0.20267 | -119.9478 | 119.8952 | -0.028768 | -120.1783 | 119.6775
Line10_11_12 | 0.10537 | 0.1115 | 0.10789 | 0.10537 | 0.1115 | 0.10789 | 0.024335 | 0.025751 | 0.024916 | 0.024335 | 0.025751 | 0.024916 | -0.001142 | -0.0019753 | -0.0029597 | 0.0012517 | 0.0020967 | 0.0030802 | -0.028173 | -0.029623 | -0.028641 | 0.028399 | 0.029868 | 0.028873 | 92.1093 | -26.5444 | -144.5939 | -87.8907 | 153.4556 | 35.4061 |  | 1.1587 | 1.1529 | 1.1556 | 1.1681 | 1.1627 | 1.1654 | -0.21206 | -120.3594 | 119.5063 | -0.41439 | -120.5599 | 119.3167
Line11_12_13 | 0.10537 | 0.1115 | 0.10789 | 0.10537 | 0.1115 | 0.10789 | 0.024335 | 0.025751 | 0.024916 | 0.024335 | 0.025751 | 0.024916 | -0.0012517 | -0.0020967 | -0.0030802 | 0.0013613 | 0.0022181 | 0.0032008 | -0.028399 | -0.029868 | -0.028873 | 0.028624 | 0.030114 | 0.029105 | 92.1093 | -26.5444 | -144.5939 | -87.8907 | 153.4556 | 35.4061 |  | 1.1681 | 1.1627 | 1.1654 | 1.1776 | 1.1726 | 1.1751 | -0.41439 | -120.5599 | 119.3167 | -0.61347 | -120.7571 | 119.1302
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8478e-10 | 7.5776e-10 | 1.7741e-09 | -5.9195e-10 | -8.1767e-10 | -1.507e-09 | -4.1708e-10 | 1.0075e-09 | -4.0641e-11 | 2.272e-10 | -7.3416e-10 | -4.4855e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1776 | 1.1726 | 1.1751 | 1.1776 | 1.1726 | 1.1751 | -0.61347 | -120.7571 | 119.1302 | -0.61347 | -120.7571 | 119.1302
Line13_13_14 | 0.10537 | 0.1115 | 0.10789 | 0.10537 | 0.1115 | 0.10789 | 0.024335 | 0.025751 | 0.024916 | 0.024335 | 0.025751 | 0.024916 | -0.0013613 | -0.0022181 | -0.0032008 | 0.0014709 | 0.0023395 | 0.0033214 | -0.028624 | -0.030114 | -0.029105 | 0.02885 | 0.030359 | 0.029337 | 92.1093 | -26.5444 | -144.5939 | -87.8907 | 153.4556 | 35.4061 |  | 1.1776 | 1.1726 | 1.1751 | 1.1871 | 1.1824 | 1.1849 | -0.61347 | -120.7571 | 119.1302 | -0.80936 | -120.9511 | 118.9468
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5652e-10 | 5.0517e-10 | 1.1828e-09 | -4.6369e-10 | -5.6508e-10 | -9.1567e-10 | -2.7805e-10 | 6.7167e-10 | -2.7094e-11 | 8.8172e-11 | -3.9833e-10 | -5.8402e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1776 | 1.1726 | 1.1751 | 1.1776 | 1.1726 | 1.1751 | -0.61347 | -120.7571 | 119.1302 | -0.61347 | -120.7571 | 119.1302
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2826e-10 | 2.5259e-10 | 5.9138e-10 | -3.3543e-10 | -3.1249e-10 | -3.2429e-10 | -1.3903e-10 | 3.3583e-10 | -1.3547e-11 | -5.0854e-11 | -6.2496e-11 | -7.1949e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1776 | 1.1726 | 1.1751 | 1.1776 | 1.1726 | 1.1751 | -0.61347 | -120.7571 | 119.1302 | -0.61347 | -120.7571 | 119.1302
Line16_4_18 | 0 | 0.037257 | 0.037325 | 0 | 0.037257 | 0.037325 | 0 | 0.008604 | 0.0086198 | 0 | 0.008604 | 0.0086198 | -2.9156e-11 | 0.006949 | 0.0069824 | -2.1712e-10 | -0.0069403 | -0.0069657 | -3.1522e-10 | 0.0069677 | 0.0069892 | 5.6945e-12 | -0.0069403 | -0.0069657 | 0 | -165.2141 | 74.7387 | 0 | 14.7859 | -105.2613 |  | 1.152 | 1.1437 | 1.1461 | 1.1514 | 1.1407 | 1.1428 | 0.079515 | -120.1369 | 119.7664 | 0.070255 | -120.2141 | 119.7387
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.5741e-11 | 3.6565e-11 | 4.7434e-10 | -1.6626e-10 | -1.3839e-10 | -1.5052e-10 | -2.6364e-10 | 3.1026e-10 | -6.1708e-11 | 1.6261e-11 | 4.1629e-12 | -8.3812e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1398 | 1.1333 | 1.1361 | 1.1398 | 1.1333 | 1.1361 | 0.20267 | -119.9478 | 119.8952 | 0.20267 | -119.9478 | 119.8952
Line1_1_3 | 0.10537 | 0.1115 | 0.10789 | 0.10537 | 0.1115 | 0.10789 | 0.024335 | 0.025751 | 0.024916 | 0.024335 | 0.025751 | 0.024916 | -0.00092278 | -0.0017325 | -0.0027186 | 0.0010324 | 0.0018539 | 0.0028391 | -0.027721 | -0.029132 | -0.028177 | 0.027947 | 0.029377 | 0.028409 | 92.1093 | -26.5444 | -144.5939 | -87.8907 | 153.4556 | 35.4061 |  | 1.1398 | 1.1333 | 1.1361 | 1.1492 | 1.1431 | 1.1459 | 0.20267 | -119.9478 | 119.8952 | -0.0064007 | -120.1554 | 119.6991
Line2_1_4 | 0.13191 | 0.11085 | 0.10714 | 0.13191 | 0.11085 | 0.10714 | 0.030464 | 0.0256 | 0.024742 | 0.030464 | 0.0256 | 0.024742 | -0.0095554 | -0.0036675 | -0.0049508 | 0.0097303 | 0.003797 | 0.0050571 | -0.033381 | -0.02878 | -0.027671 | 0.033718 | 0.029032 | 0.027904 | 106.1765 | -22.6858 | -139.9611 | -73.8235 | 157.3142 | 40.0389 |  | 1.1398 | 1.1333 | 1.1361 | 1.152 | 1.1437 | 1.1461 | 0.20267 | -119.9478 | 119.8952 | 0.079515 | -120.1369 | 119.7664
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1148e-10 | 7.3129e-11 | 9.4869e-10 | -1.1052e-10 | -1.7495e-10 | -6.2486e-10 | -5.2728e-10 | 6.2052e-10 | -1.2342e-10 | 2.799e-10 | -3.061e-10 | 5.3327e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1398 | 1.1333 | 1.1361 | 1.1398 | 1.1333 | 1.1361 | 0.20267 | -119.9478 | 119.8952 | 0.20267 | -119.9478 | 119.8952
Line4_2_6 | 0.11765 | 0.12451 | 0.1207 | 0.11765 | 0.12451 | 0.1207 | 0.02717 | 0.028754 | 0.027874 | 0.02717 | 0.028754 | 0.027874 | -0.001296 | -0.0021367 | -0.0032646 | 0.0014329 | 0.002288 | 0.0034154 | -0.031228 | -0.032833 | -0.031805 | 0.03151 | 0.033139 | 0.032095 | 92.3477 | -26.4549 | -144.4619 | -87.6523 | 153.5451 | 35.5381 |  | 1.1503 | 1.1443 | 1.147 | 1.1609 | 1.1552 | 1.1579 | -0.028768 | -120.1783 | 119.6775 | -0.25599 | -120.4044 | 119.4639
Line5_6_7 | 0.11765 | 0.12451 | 0.1207 | 0.11765 | 0.12451 | 0.1207 | 0.02717 | 0.028754 | 0.027874 | 0.02717 | 0.028754 | 0.027874 | -0.0014329 | -0.002288 | -0.0034154 | 0.0015698 | 0.0024392 | 0.0035661 | -0.03151 | -0.033139 | -0.032095 | 0.031792 | 0.033445 | 0.032385 | 92.3477 | -26.4549 | -144.4619 | -87.6523 | 153.5451 | 35.5381 |  | 1.1609 | 1.1552 | 1.1579 | 1.1715 | 1.1662 | 1.1689 | -0.25599 | -120.4044 | 119.4639 | -0.47911 | -120.6262 | 119.2542
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8587e-10 | 6.5337e-10 | 1.7197e-09 | -4.9791e-10 | -7.1906e-10 | -1.4419e-09 | -4.7985e-10 | 1.001e-09 | -7.0946e-11 | 2.8039e-10 | -7.1874e-10 | -1.4065e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1715 | 1.1662 | 1.1689 | 1.1715 | 1.1662 | 1.1689 | -0.47911 | -120.6262 | 119.2542 | -0.47911 | -120.6262 | 119.2542
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5289e-11 | 2.1779e-10 | 5.7322e-10 | -3.0734e-10 | -2.8348e-10 | -2.9548e-10 | -1.5995e-10 | 3.3367e-10 | -2.3649e-11 | -3.9511e-11 | -5.1407e-11 | -6.1362e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1715 | 1.1662 | 1.1689 | 1.1715 | 1.1662 | 1.1689 | -0.47911 | -120.6262 | 119.2542 | -0.47911 | -120.6262 | 119.2542
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5289e-11 | 2.1779e-10 | 5.7322e-10 | -3.0734e-10 | -2.8348e-10 | -2.9548e-10 | -1.5995e-10 | 3.3367e-10 | -2.3649e-11 | -3.9511e-11 | -5.1407e-11 | -6.1362e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1715 | 1.1662 | 1.1689 | 1.1715 | 1.1662 | 1.1689 | -0.47911 | -120.6262 | 119.2542 | -0.47911 | -120.6262 | 119.2542
Line9_3_11 | 0.10537 | 0.1115 | 0.10789 | 0.10537 | 0.1115 | 0.10789 | 0.024335 | 0.025751 | 0.024916 | 0.024335 | 0.025751 | 0.024916 | -0.0010324 | -0.0018539 | -0.0028391 | 0.001142 | 0.0019753 | 0.0029597 | -0.027947 | -0.029377 | -0.028409 | 0.028173 | 0.029623 | 0.028641 | 92.1093 | -26.5444 | -144.5939 | -87.8907 | 153.4556 | 35.4061 |  | 1.1492 | 1.1431 | 1.1459 | 1.1587 | 1.1529 | 1.1556 | -0.0064007 | -120.1554 | 119.6991 | -0.21206 | -120.3594 | 119.5063

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.013479 | 0.011577 | 0.015935 | 0.01348 | 0.011577 | 0.015935 | 0.0031129 | 0.0026735 | 0.0036801 | 0.003113 | 0.0026735 | 0.0036801 | -0.00019192 | 0.0013693 | -0.0022299 | 0.00019378 | -0.0013687 | 0.0022332 | 0.004388 | -0.00083279 | 4.6701e-05 | -0.0043863 | 0.00083447 | -4.4092e-05 | -92.3124 | -71.0711 | -99.5641 | 87.6876 | 108.9286 | 80.436 |  | 1.4109 | 0.59947 | 0.60607 | 1.4104 | 0.59958 | 0.60694 | 0.19196 | -102.3777 | 79.2361 | 0.21718 | -102.4413 | 79.3049
Line10_11_12 | 0.013446 | 0.011549 | 0.015893 | 0.013447 | 0.011549 | 0.015893 | 0.0031053 | 0.0026671 | 0.0036703 | 0.0031054 | 0.0026672 | 0.0036703 | -0.00018382 | 0.0013629 | -0.0022303 | 0.00018567 | -0.0013623 | 0.0022336 | 0.0043743 | -0.00083706 | 4.6495e-05 | -0.0043726 | 0.00083873 | -4.3901e-05 | -92.1642 | -70.948 | -99.4323 | 87.8359 | 109.0518 | 80.5678 |  | 1.4099 | 0.59969 | 0.6078 | 1.4094 | 0.5998 | 0.60867 | 0.24217 | -102.5045 | 79.3734 | 0.2673 | -102.5679 | 79.4418
Line11_12_13 | 0.013447 | 0.011549 | 0.015893 | 0.013447 | 0.011549 | 0.015893 | 0.0031054 | 0.0026672 | 0.0036703 | 0.0031054 | 0.0026672 | 0.0036704 | -0.00018567 | 0.0013623 | -0.0022336 | 0.00018752 | -0.0013616 | 0.0022368 | 0.0043726 | -0.00083873 | 4.3899e-05 | -0.0043709 | 0.0008404 | -4.1305e-05 | -92.1642 | -70.9483 | -99.4323 | 87.8359 | 109.0515 | 80.5678 |  | 1.4094 | 0.5998 | 0.60867 | 1.4088 | 0.59992 | 0.60953 | 0.2673 | -102.5679 | 79.4418 | 0.29245 | -102.6313 | 79.5099
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.452e-09 | -6.9891e-08 | 6.8768e-08 | -6.0048e-09 | 4.7269e-08 | -4.5593e-08 | -1.6397e-07 | 1.4426e-08 | -9.8352e-09 | 1.0934e-07 | -8.9938e-09 | 5.1782e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4088 | 0.59992 | 0.60953 | 1.4088 | 0.59992 | 0.60953 | 0.29245 | -102.6313 | 79.5099 | 0.29245 | -102.6313 | 79.5099
Line13_13_14 | 0.013447 | 0.01155 | 0.015894 | 0.013447 | 0.01155 | 0.015894 | 0.0031055 | 0.0026673 | 0.0036705 | 0.0031056 | 0.0026674 | 0.0036705 | -0.00018753 | 0.0013617 | -0.0022369 | 0.00018938 | -0.0013611 | 0.0022401 | 0.0043711 | -0.00084041 | 4.1313e-05 | -0.0043694 | 0.00084208 | -3.8719e-05 | -92.1641 | -70.9494 | -99.432 | 87.8359 | 109.0503 | 80.5681 |  | 1.4088 | 0.59992 | 0.60953 | 1.4083 | 0.60003 | 0.6104 | 0.29245 | -102.6313 | 79.5099 | 0.31762 | -102.6947 | 79.5779
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6347e-09 | -4.6594e-08 | 4.5845e-08 | -4.1875e-09 | 2.3972e-08 | -2.267e-08 | -1.0932e-07 | 9.6176e-09 | -6.5568e-09 | 5.4683e-08 | -4.185e-09 | 1.8998e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4088 | 0.59992 | 0.60953 | 1.4088 | 0.59992 | 0.60953 | 0.29245 | -102.6313 | 79.5099 | 0.29245 | -102.6313 | 79.5099
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8173e-09 | -2.3297e-08 | 2.2923e-08 | -2.3702e-09 | 6.7479e-10 | 2.5246e-10 | -5.4658e-08 | 4.8088e-09 | -3.2784e-09 | 2.5048e-11 | 6.2382e-10 | -1.3786e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4088 | 0.59992 | 0.60953 | 1.4088 | 0.59992 | 0.60953 | 0.29245 | -102.6313 | 79.5099 | 0.29245 | -102.6313 | 79.5099
Line16_4_18 | 0 | 2.492 | 2.5377 | 0 | 2.492 | 2.5377 | 0 | 0.57549 | 0.58605 | 0 | 0.57549 | 0.58605 | 2.2221e-09 | 0.1186 | 0.12422 | -2.3534e-09 | -2.4863e-14 | 1.1823e-14 | -5.5222e-08 | 0.12548 | 0.12746 | 2.8213e-11 | -2.2497e-14 | 1.9719e-14 | 0 | -149.09 | 33.5418 | 0 | 30.91 | -146.4582 |  | 1.4084 | 0.30003 | 0.30369 | 1.4064 | 0 | 0 | 0.27414 | -102.4756 | 79.279 | 0.32997 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9938e-09 | -2.3441e-08 | 2.2907e-08 | -2.3847e-09 | 6.7249e-10 | 2.5214e-10 | -5.5007e-08 | 4.6146e-09 | -3.2757e-09 | 1.6467e-11 | 6.3218e-10 | -1.3785e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4109 | 0.59947 | 0.60607 | 1.4109 | 0.59947 | 0.60607 | 0.19196 | -102.3777 | 79.2361 | 0.19196 | -102.3777 | 79.2361
Line1_1_3 | 0.013446 | 0.011549 | 0.015893 | 0.013446 | 0.011549 | 0.015893 | 0.0031053 | 0.0026671 | 0.0036702 | 0.0031053 | 0.0026671 | 0.0036703 | -0.00018012 | 0.0013642 | -0.0022238 | 0.00018197 | -0.0013636 | 0.0022271 | 0.0043776 | -0.00083373 | 5.1685e-05 | -0.004376 | 0.0008354 | -4.9091e-05 | -92.1642 | -70.9474 | -99.4325 | 87.8359 | 109.0524 | 80.5676 |  | 1.4109 | 0.59947 | 0.60607 | 1.4104 | 0.59958 | 0.60694 | 0.19196 | -102.3777 | 79.2361 | 0.21706 | -102.4411 | 79.3049
Line2_1_4 | 0.013171 | 2.4905 | 2.5231 | 0.013171 | 2.4905 | 2.5231 | 0.0030417 | 0.57515 | 0.58269 | 0.0030417 | 0.57515 | 0.58269 | -0.00045341 | 0.23784 | 0.24574 | 0.00045871 | -0.11925 | -0.12304 | 0.0042676 | 0.24961 | 0.25364 | -0.0042594 | -0.12473 | -0.12718 | -95.8727 | -148.7608 | 33.3296 | 84.1274 | 31.2392 | -146.6704 |  | 1.4109 | 0.59947 | 0.60607 | 1.4084 | 0.30003 | 0.30369 | 0.19196 | -102.3777 | 79.2361 | 0.27414 | -102.4756 | 79.279
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9876e-09 | -4.6881e-08 | 4.5814e-08 | -4.3785e-09 | 2.4113e-08 | -2.2655e-08 | -1.1001e-07 | 9.2292e-09 | -6.5514e-09 | 5.5024e-08 | -3.9824e-09 | 1.8972e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4109 | 0.59947 | 0.60607 | 1.4109 | 0.59947 | 0.60607 | 0.19196 | -102.3777 | 79.2361 | 0.19196 | -102.3777 | 79.2361
Line4_2_6 | 0.01348 | 0.011577 | 0.015935 | 0.01348 | 0.011577 | 0.015936 | 0.003113 | 0.0026735 | 0.0036801 | 0.003113 | 0.0026736 | 0.0036802 | -0.00019378 | 0.0013687 | -0.0022332 | 0.00019564 | -0.001368 | 0.0022365 | 0.0043863 | -0.00083447 | 4.4091e-05 | -0.0043846 | 0.00083614 | -4.1483e-05 | -92.3124 | -71.0714 | -99.5641 | 87.6876 | 108.9283 | 80.4361 |  | 1.4104 | 0.59958 | 0.60694 | 1.4099 | 0.59969 | 0.60781 | 0.21718 | -102.4413 | 79.3049 | 0.24241 | -102.5049 | 79.3734
Line5_6_7 | 0.01348 | 0.011577 | 0.015936 | 0.01348 | 0.011577 | 0.015936 | 0.003113 | 0.0026736 | 0.0036802 | 0.0031131 | 0.0026736 | 0.0036802 | -0.00019564 | 0.001368 | -0.0022365 | 0.0001975 | -0.0013674 | 0.0022397 | 0.0043846 | -0.00083614 | 4.1481e-05 | -0.004383 | 0.00083782 | -3.8873e-05 | -92.3124 | -71.0717 | -99.564 | 87.6876 | 108.928 | 80.4361 |  | 1.4099 | 0.59969 | 0.60781 | 1.4094 | 0.5998 | 0.60868 | 0.24241 | -102.5049 | 79.3734 | 0.26766 | -102.5685 | 79.4418
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5825e-09 | -6.9998e-08 | 6.8757e-08 | -6.0955e-09 | 4.734e-08 | -4.5586e-08 | -1.6424e-07 | 1.4283e-08 | -9.834e-09 | 1.0951e-07 | -8.896e-09 | 5.1774e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4094 | 0.5998 | 0.60868 | 1.4094 | 0.5998 | 0.60868 | 0.26766 | -102.5685 | 79.4418 | 0.26766 | -102.5685 | 79.4418
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8608e-09 | -2.3333e-08 | 2.2919e-08 | -2.3738e-09 | 6.7423e-10 | 2.5237e-10 | -5.4745e-08 | 4.761e-09 | -3.278e-09 | 2.2934e-11 | 6.2589e-10 | -1.3786e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4094 | 0.5998 | 0.60868 | 1.4094 | 0.5998 | 0.60868 | 0.26766 | -102.5685 | 79.4418 | 0.26766 | -102.5685 | 79.4418
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8608e-09 | -2.3333e-08 | 2.2919e-08 | -2.3738e-09 | 6.7423e-10 | 2.5237e-10 | -5.4745e-08 | 4.761e-09 | -3.278e-09 | 2.2934e-11 | 6.2589e-10 | -1.3786e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4094 | 0.5998 | 0.60868 | 1.4094 | 0.5998 | 0.60868 | 0.26766 | -102.5685 | 79.4418 | 0.26766 | -102.5685 | 79.4418
Line9_3_11 | 0.013446 | 0.011549 | 0.015893 | 0.013446 | 0.011549 | 0.015893 | 0.0031053 | 0.0026671 | 0.0036703 | 0.0031053 | 0.0026671 | 0.0036703 | -0.00018197 | 0.0013636 | -0.0022271 | 0.00018382 | -0.0013629 | 0.0022303 | 0.004376 | -0.0008354 | 4.909e-05 | -0.0043743 | 0.00083706 | -4.6496e-05 | -92.1642 | -70.9477 | -99.4324 | 87.8359 | 109.0521 | 80.5677 |  | 1.4104 | 0.59958 | 0.60694 | 1.4099 | 0.59969 | 0.6078 | 0.21706 | -102.4411 | 79.3049 | 0.24217 | -102.5045 | 79.3734

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.01277 | 0.010967 | 0.015097 | 0.01277 | 0.010967 | 0.015097 | 0.0029491 | 0.0025328 | 0.0034864 | 0.0029491 | 0.0025328 | 0.0034864 | -0.00017225 | 0.001229 | -0.0020014 | 0.00017392 | -0.0012284 | 0.0020043 | 0.0039383 | -0.00074743 | 4.1914e-05 | -0.0039368 | 0.00074894 | -3.9573e-05 | -92.3124 | -71.0711 | -99.5641 | 87.6876 | 108.9286 | 80.436 |  | 1.3367 | 0.56792 | 0.57418 | 1.3362 | 0.56803 | 0.575 | 0.19196 | -102.3777 | 79.2361 | 0.21718 | -102.4413 | 79.3049
Line10_11_12 | 0.012739 | 0.010941 | 0.015056 | 0.012739 | 0.010941 | 0.015057 | 0.0029419 | 0.0025268 | 0.0034771 | 0.0029419 | 0.0025268 | 0.0034772 | -0.00016498 | 0.0012232 | -0.0020017 | 0.00016664 | -0.0012227 | 0.0020047 | 0.003926 | -0.00075127 | 4.1729e-05 | -0.0039245 | 0.00075277 | -3.9401e-05 | -92.1642 | -70.948 | -99.4323 | 87.8359 | 109.0518 | 80.5678 |  | 1.3357 | 0.56813 | 0.57581 | 1.3352 | 0.56824 | 0.57663 | 0.24217 | -102.5045 | 79.3734 | 0.2673 | -102.5679 | 79.4418
Line11_12_13 | 0.012739 | 0.010941 | 0.015057 | 0.012739 | 0.010941 | 0.015057 | 0.0029419 | 0.0025268 | 0.0034772 | 0.002942 | 0.0025268 | 0.0034772 | -0.00016664 | 0.0012227 | -0.0020047 | 0.0001683 | -0.0012221 | 0.0020076 | 0.0039245 | -0.00075277 | 3.94e-05 | -0.0039229 | 0.00075426 | -3.7072e-05 | -92.1642 | -70.9483 | -99.4323 | 87.8359 | 109.0515 | 80.5678 |  | 1.3352 | 0.56824 | 0.57663 | 1.3347 | 0.56834 | 0.57745 | 0.2673 | -102.5679 | 79.4418 | 0.29245 | -102.6313 | 79.5099
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8932e-09 | -6.2728e-08 | 6.172e-08 | -5.3894e-09 | 4.2424e-08 | -4.092e-08 | -1.4717e-07 | 1.2948e-08 | -8.8272e-09 | 9.8134e-08 | -8.072e-09 | 4.6475e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3347 | 0.56834 | 0.57745 | 1.3347 | 0.56834 | 0.57745 | 0.29245 | -102.6313 | 79.5099 | 0.29245 | -102.6313 | 79.5099
Line13_13_14 | 0.01274 | 0.010942 | 0.015057 | 0.01274 | 0.010942 | 0.015057 | 0.0029421 | 0.0025269 | 0.0034773 | 0.0029421 | 0.002527 | 0.0034773 | -0.00016831 | 0.0012221 | -0.0020076 | 0.00016997 | -0.0012216 | 0.0020105 | 0.0039231 | -0.00075428 | 3.7079e-05 | -0.0039216 | 0.00075577 | -3.4751e-05 | -92.1641 | -70.9494 | -99.432 | 87.8359 | 109.0503 | 80.5681 |  | 1.3347 | 0.56834 | 0.57745 | 1.3342 | 0.56845 | 0.57827 | 0.29245 | -102.6313 | 79.5099 | 0.31762 | -102.6947 | 79.5779
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2621e-09 | -4.1819e-08 | 4.1147e-08 | -3.7583e-09 | 2.1515e-08 | -2.0347e-08 | -9.8112e-08 | 8.6318e-09 | -5.8848e-09 | 4.9078e-08 | -3.756e-09 | 1.7051e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3347 | 0.56834 | 0.57745 | 1.3347 | 0.56834 | 0.57745 | 0.29245 | -102.6313 | 79.5099 | 0.29245 | -102.6313 | 79.5099
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6311e-09 | -2.0909e-08 | 2.0573e-08 | -2.1272e-09 | 6.0563e-10 | 2.2658e-10 | -4.9056e-08 | 4.3159e-09 | -2.9424e-09 | 2.2481e-11 | 5.5988e-10 | -1.2373e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3347 | 0.56834 | 0.57745 | 1.3347 | 0.56834 | 0.57745 | 0.29245 | -102.6313 | 79.5099 | 0.29245 | -102.6313 | 79.5099
Line16_4_18 | 0 | 2.3608 | 2.4041 | 0 | 2.3608 | 2.4041 | 0 | 0.5452 | 0.55521 | 0 | 0.5452 | 0.55521 | 1.9944e-09 | 0.10645 | 0.11149 | -2.1122e-09 | -2.2358e-14 | 1.0796e-14 | -4.9562e-08 | 0.11262 | 0.11439 | 2.5321e-11 | -1.8784e-14 | 1.6731e-14 | 0 | -149.09 | 33.5418 | 0 | 30.91 | -146.4582 |  | 1.3343 | 0.28424 | 0.28771 | 1.3323 | 0 | 0 | 0.27414 | -102.4756 | 79.279 | 0.32997 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7894e-09 | -2.1038e-08 | 2.0559e-08 | -2.1403e-09 | 6.0356e-10 | 2.263e-10 | -4.937e-08 | 4.1416e-09 | -2.94e-09 | 1.4779e-11 | 5.6738e-10 | -1.2372e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3367 | 0.56792 | 0.57418 | 1.3367 | 0.56792 | 0.57418 | 0.19196 | -102.3777 | 79.2361 | 0.19196 | -102.3777 | 79.2361
Line1_1_3 | 0.012738 | 0.010941 | 0.015056 | 0.012739 | 0.010941 | 0.015056 | 0.0029418 | 0.0025267 | 0.003477 | 0.0029419 | 0.0025267 | 0.0034771 | -0.00016166 | 0.0012244 | -0.0019959 | 0.00016332 | -0.0012238 | 0.0019988 | 0.003929 | -0.00074828 | 4.6388e-05 | -0.0039275 | 0.00074977 | -4.406e-05 | -92.1642 | -70.9474 | -99.4325 | 87.8359 | 109.0524 | 80.5676 |  | 1.3367 | 0.56792 | 0.57418 | 1.3362 | 0.56803 | 0.57499 | 0.19196 | -102.3777 | 79.2361 | 0.21706 | -102.4411 | 79.3049
Line2_1_4 | 0.012478 | 2.3594 | 2.3903 | 0.012478 | 2.3594 | 2.3903 | 0.0028816 | 0.54488 | 0.55202 | 0.0028816 | 0.54488 | 0.55202 | -0.00040694 | 0.21347 | 0.22055 | 0.0004117 | -0.10703 | -0.11043 | 0.0038302 | 0.22403 | 0.22764 | -0.0038229 | -0.11194 | -0.11415 | -95.8727 | -148.7608 | 33.3296 | 84.1274 | 31.2392 | -146.6704 |  | 1.3367 | 0.56792 | 0.57418 | 1.3343 | 0.28424 | 0.28771 | 0.19196 | -102.3777 | 79.2361 | 0.27414 | -102.4756 | 79.279
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5789e-09 | -4.2076e-08 | 4.1118e-08 | -3.9298e-09 | 2.1642e-08 | -2.0333e-08 | -9.8739e-08 | 8.2833e-09 | -5.88e-09 | 4.9384e-08 | -3.5743e-09 | 1.7028e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3367 | 0.56792 | 0.57418 | 1.3367 | 0.56792 | 0.57418 | 0.19196 | -102.3777 | 79.2361 | 0.19196 | -102.3777 | 79.2361
Line4_2_6 | 0.01277 | 0.010967 | 0.015097 | 0.01277 | 0.010968 | 0.015097 | 0.0029491 | 0.0025328 | 0.0034864 | 0.0029492 | 0.0025329 | 0.0034865 | -0.00017392 | 0.0012284 | -0.0020043 | 0.00017559 | -0.0012278 | 0.0020072 | 0.0039368 | -0.00074894 | 3.9572e-05 | -0.0039352 | 0.00075044 | -3.7231e-05 | -92.3124 | -71.0714 | -99.5641 | 87.6876 | 108.9283 | 80.4361 |  | 1.3362 | 0.56803 | 0.575 | 1.3357 | 0.56813 | 0.57582 | 0.21718 | -102.4413 | 79.3049 | 0.24241 | -102.5049 | 79.3734
Line5_6_7 | 0.01277 | 0.010968 | 0.015097 | 0.01277 | 0.010968 | 0.015097 | 0.0029492 | 0.0025329 | 0.0034865 | 0.0029492 | 0.0025329 | 0.0034865 | -0.00017559 | 0.0012278 | -0.0020072 | 0.00017726 | -0.0012272 | 0.0020102 | 0.0039352 | -0.00075044 | 3.723e-05 | -0.0039337 | 0.00075195 | -3.4888e-05 | -92.3124 | -71.0717 | -99.564 | 87.6876 | 108.928 | 80.4361 |  | 1.3357 | 0.56813 | 0.57582 | 1.3352 | 0.56823 | 0.57664 | 0.24241 | -102.5049 | 79.3734 | 0.26766 | -102.5685 | 79.4418
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0103e-09 | -6.2824e-08 | 6.171e-08 | -5.4707e-09 | 4.2488e-08 | -4.0914e-08 | -1.474e-07 | 1.2819e-08 | -8.8261e-09 | 9.8289e-08 | -7.9842e-09 | 4.6467e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3352 | 0.56823 | 0.57664 | 1.3352 | 0.56823 | 0.57664 | 0.26766 | -102.5685 | 79.4418 | 0.26766 | -102.5685 | 79.4418
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6701e-09 | -2.0941e-08 | 2.057e-08 | -2.1305e-09 | 6.0513e-10 | 2.2651e-10 | -4.9134e-08 | 4.273e-09 | -2.942e-09 | 2.0584e-11 | 5.6174e-10 | -1.2373e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3352 | 0.56823 | 0.57664 | 1.3352 | 0.56823 | 0.57664 | 0.26766 | -102.5685 | 79.4418 | 0.26766 | -102.5685 | 79.4418
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6701e-09 | -2.0941e-08 | 2.057e-08 | -2.1305e-09 | 6.0513e-10 | 2.2651e-10 | -4.9134e-08 | 4.273e-09 | -2.942e-09 | 2.0583e-11 | 5.6174e-10 | -1.2373e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3352 | 0.56823 | 0.57664 | 1.3352 | 0.56823 | 0.57664 | 0.26766 | -102.5685 | 79.4418 | 0.26766 | -102.5685 | 79.4418
Line9_3_11 | 0.012739 | 0.010941 | 0.015056 | 0.012739 | 0.010941 | 0.015056 | 0.0029419 | 0.0025267 | 0.0034771 | 0.0029419 | 0.0025268 | 0.0034771 | -0.00016332 | 0.0012238 | -0.0019988 | 0.00016498 | -0.0012232 | 0.0020017 | 0.0039275 | -0.00074977 | 4.4059e-05 | -0.003926 | 0.00075127 | -4.173e-05 | -92.1642 | -70.9477 | -99.4324 | 87.8359 | 109.0521 | 80.5677 |  | 1.3362 | 0.56803 | 0.57499 | 1.3357 | 0.56813 | 0.57581 | 0.21706 | -102.4411 | 79.3049 | 0.24217 | -102.5045 | 79.3734

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0027383 | 0.0027423 | 0.0027756 | 0.0027384 | 0.0027424 | 0.0027756 | 0.00063239 | 0.00063331 | 0.000641 | 0.0006324 | 0.00063332 | 0.000641 | 0.0002845 | 0.00030538 | -0.00060732 | -0.00028443 | -0.00030532 | 0.00060741 | 0.0005891 | -0.00045753 | 3.8484e-05 | -0.00058904 | 0.00045761 | -3.8408e-05 | -61.7367 | -60.5605 | -62.213 | 118.2633 | 119.4395 | 117.787 |  | 1.0345 | 0.86858 | 0.94937 | 1.0343 | 0.86862 | 0.94948 | 2.4855 | -116.839 | 114.1613 | 2.4883 | -116.8495 | 114.1689
Line10_11_12 | 0.0027315 | 0.0027355 | 0.0027686 | 0.0027315 | 0.0027355 | 0.0027687 | 0.00063081 | 0.00063174 | 0.00063939 | 0.00063082 | 0.00063174 | 0.0006394 | 0.00028505 | 0.0003034 | -0.00060586 | -0.00028499 | -0.00030334 | 0.00060594 | 0.00058681 | -0.00045726 | 3.9674e-05 | -0.00058674 | 0.00045734 | -3.9598e-05 | -61.5999 | -60.4251 | -62.0768 | 118.4001 | 119.5749 | 117.9232 |  | 1.0342 | 0.86865 | 0.94959 | 1.034 | 0.86869 | 0.9497 | 2.4911 | -116.8599 | 114.1766 | 2.4939 | -116.8704 | 114.1842
Line11_12_13 | 0.0027315 | 0.0027355 | 0.0027687 | 0.0027316 | 0.0027356 | 0.0027687 | 0.00063082 | 0.00063174 | 0.0006394 | 0.00063083 | 0.00063175 | 0.0006394 | 0.00028498 | 0.00030334 | -0.00060594 | -0.00028492 | -0.00030327 | 0.00060602 | 0.00058674 | -0.00045734 | 3.9598e-05 | -0.00058668 | 0.00045742 | -3.9522e-05 | -61.5999 | -60.4252 | -62.0768 | 118.4001 | 119.5748 | 117.9232 |  | 1.034 | 0.86869 | 0.9497 | 1.0339 | 0.86873 | 0.9498 | 2.4939 | -116.8704 | 114.1842 | 2.4967 | -116.8809 | 114.1919
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.9066e-09 | -1.2556e-08 | 2.2712e-08 | 6.283e-09 | 8.6248e-09 | -1.5158e-08 | -2.2696e-08 | 1.6627e-08 | -7.2716e-10 | 1.5287e-08 | -1.092e-08 | 1.4997e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0339 | 0.86873 | 0.9498 | 1.0339 | 0.86873 | 0.9498 | 2.4967 | -116.8809 | 114.1919 | 2.4967 | -116.8809 | 114.1919
Line13_13_14 | 0.0027317 | 0.0027357 | 0.0027688 | 0.0027317 | 0.0027357 | 0.0027688 | 0.00063085 | 0.00063178 | 0.00063943 | 0.00063086 | 0.00063178 | 0.00063944 | 0.00028493 | 0.00030328 | -0.00060604 | -0.00028486 | -0.00030322 | 0.00060613 | 0.0005867 | -0.00045744 | 3.9522e-05 | -0.00058663 | 0.00045752 | -3.9446e-05 | -61.6 | -60.4253 | -62.0769 | 118.4 | 119.5747 | 117.9231 |  | 1.0339 | 0.86873 | 0.9498 | 1.0337 | 0.86877 | 0.94991 | 2.4967 | -116.8809 | 114.1919 | 2.4996 | -116.8914 | 114.1995
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.6044e-09 | -8.3704e-09 | 1.5141e-08 | 2.9808e-09 | 4.4396e-09 | -7.587e-09 | -1.513e-08 | 1.1085e-08 | -4.8478e-10 | 7.7221e-09 | -5.3777e-09 | -9.2422e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0339 | 0.86873 | 0.9498 | 1.0339 | 0.86873 | 0.9498 | 2.4967 | -116.8809 | 114.1919 | 2.4967 | -116.8809 | 114.1919
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3022e-09 | -4.1852e-09 | 7.5707e-09 | -3.2139e-10 | 2.5439e-10 | -1.6305e-11 | -7.5652e-09 | 5.5423e-09 | -2.4239e-10 | 1.5688e-10 | 1.6465e-10 | -3.3481e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0339 | 0.86873 | 0.9498 | 1.0339 | 0.86873 | 0.9498 | 2.4967 | -116.8809 | 114.1919 | 2.4967 | -116.8809 | 114.1919
Line16_4_18 | 0 | 0.02816 | 0.030785 | 0 | 0.02816 | 0.030785 | 0 | 0.0065034 | 0.0071095 | 0 | 0.0065034 | 0.0071095 | -3.2826e-09 | 0.0039772 | 0.0047578 | -3.1915e-10 | -0.003965 | -0.0047386 | -7.6711e-09 | 0.0039822 | 0.0047541 | 1.5677e-10 | -0.003965 | -0.0047386 | 0 | -161.9216 | 69.2132 | 0 | 18.0784 | -110.7868 |  | 1.0338 | 0.86543 | 0.94604 | 1.0333 | 0.86223 | 0.9426 | 2.4923 | -116.8855 | 114.1909 | 2.4962 | -116.9216 | 114.2132
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.286e-09 | -4.236e-09 | 7.6061e-09 | -3.2391e-10 | 2.5471e-10 | -1.4952e-11 | -7.6227e-09 | 5.5459e-09 | -2.1131e-10 | 1.5627e-10 | 1.6684e-10 | -3.3641e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0345 | 0.86858 | 0.94937 | 1.0345 | 0.86858 | 0.94937 | 2.4855 | -116.839 | 114.1613 | 2.4855 | -116.839 | 114.1613
Line1_1_3 | 0.0027314 | 0.0027354 | 0.0027686 | 0.0027315 | 0.0027355 | 0.0027686 | 0.0006308 | 0.00063172 | 0.00063937 | 0.00063081 | 0.00063173 | 0.00063938 | 0.00028519 | 0.00030353 | -0.00060569 | -0.00028512 | -0.00030347 | 0.00060577 | 0.00058694 | -0.0004571 | 3.9826e-05 | -0.00058688 | 0.00045718 | -3.975e-05 | -61.5998 | -60.425 | -62.0768 | 118.4002 | 119.575 | 117.9232 |  | 1.0345 | 0.86858 | 0.94937 | 1.0343 | 0.86862 | 0.94948 | 2.4855 | -116.839 | 114.1613 | 2.4883 | -116.8495 | 114.1689
Line2_1_4 | 0.0027373 | 0.027714 | 0.028964 | 0.0027373 | 0.027714 | 0.028964 | 0.00063215 | 0.0064003 | 0.0066889 | 0.00063216 | 0.0064003 | 0.0066889 | 0.0002812 | 0.0042933 | 0.0041653 | -0.00028095 | -0.0042806 | -0.0041482 | 0.00059041 | 0.0035315 | 0.0047933 | -0.00059008 | -0.0035152 | -0.0047787 | -62.0475 | -156.278 | 65.1509 | 117.9525 | 23.7221 | -114.8492 |  | 1.0345 | 0.86858 | 0.94937 | 1.0338 | 0.86543 | 0.94604 | 2.4855 | -116.839 | 114.1613 | 2.4923 | -116.8855 | 114.1909
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.5719e-09 | -8.4719e-09 | 1.5212e-08 | 2.9621e-09 | 4.4907e-09 | -7.621e-09 | -1.5245e-08 | 1.1092e-08 | -4.2262e-10 | 7.779e-09 | -5.3791e-09 | -1.251e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0345 | 0.86858 | 0.94937 | 1.0345 | 0.86858 | 0.94937 | 2.4855 | -116.839 | 114.1613 | 2.4855 | -116.839 | 114.1613
Line4_2_6 | 0.0027384 | 0.0027424 | 0.0027756 | 0.0027384 | 0.0027424 | 0.0027757 | 0.0006324 | 0.00063332 | 0.000641 | 0.0006324 | 0.00063333 | 0.00064101 | 0.00028443 | 0.00030532 | -0.00060741 | -0.00028436 | -0.00030525 | 0.00060749 | 0.00058904 | -0.00045761 | 3.8407e-05 | -0.00058897 | 0.00045769 | -3.8331e-05 | -61.7367 | -60.5606 | -62.213 | 118.2633 | 119.4394 | 117.787 |  | 1.0343 | 0.86862 | 0.94948 | 1.0342 | 0.86865 | 0.94959 | 2.4883 | -116.8495 | 114.1689 | 2.4912 | -116.86 | 114.1766
Line5_6_7 | 0.0027384 | 0.0027424 | 0.0027757 | 0.0027384 | 0.0027424 | 0.0027757 | 0.0006324 | 0.00063333 | 0.00064101 | 0.00063241 | 0.00063334 | 0.00064102 | 0.00028436 | 0.00030525 | -0.00060749 | -0.0002843 | -0.00030518 | 0.00060757 | 0.00058897 | -0.00045769 | 3.8331e-05 | -0.0005889 | 0.00045777 | -3.8254e-05 | -61.7368 | -60.5606 | -62.213 | 118.2632 | 119.4394 | 117.787 |  | 1.0342 | 0.86865 | 0.94959 | 1.034 | 0.86869 | 0.9497 | 2.4912 | -116.86 | 114.1766 | 2.494 | -116.8705 | 114.1842
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.8948e-09 | -1.2593e-08 | 2.2739e-08 | 6.2745e-09 | 8.65e-09 | -1.5175e-08 | -2.2739e-08 | 1.663e-08 | -7.0424e-10 | 1.5316e-08 | -1.0921e-08 | 1.3428e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.034 | 0.86869 | 0.9497 | 1.034 | 0.86869 | 0.9497 | 2.494 | -116.8705 | 114.1842 | 2.494 | -116.8705 | 114.1842
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2983e-09 | -4.1978e-09 | 7.5795e-09 | -3.2202e-10 | 2.5447e-10 | -1.5973e-11 | -7.5795e-09 | 5.5433e-09 | -2.3475e-10 | 1.5674e-10 | 1.6519e-10 | -3.3521e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.034 | 0.86869 | 0.9497 | 1.034 | 0.86869 | 0.9497 | 2.494 | -116.8705 | 114.1842 | 2.494 | -116.8705 | 114.1842
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.2983e-09 | -4.1978e-09 | 7.5795e-09 | -3.2202e-10 | 2.5447e-10 | -1.5973e-11 | -7.5795e-09 | 5.5433e-09 | -2.3475e-10 | 1.5674e-10 | 1.6519e-10 | -3.3521e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.034 | 0.86869 | 0.9497 | 1.034 | 0.86869 | 0.9497 | 2.494 | -116.8705 | 114.1842 | 2.494 | -116.8705 | 114.1842
Line9_3_11 | 0.0027315 | 0.0027355 | 0.0027686 | 0.0027315 | 0.0027355 | 0.0027686 | 0.00063081 | 0.00063173 | 0.00063938 | 0.00063081 | 0.00063174 | 0.00063939 | 0.00028512 | 0.00030347 | -0.00060577 | -0.00028505 | -0.0003034 | 0.00060586 | 0.00058688 | -0.00045718 | 3.975e-05 | -0.00058681 | 0.00045726 | -3.9674e-05 | -61.5998 | -60.4251 | -62.0768 | 118.4002 | 119.5749 | 117.9232 |  | 1.0343 | 0.86862 | 0.94948 | 1.0342 | 0.86865 | 0.94959 | 2.4883 | -116.8495 | 114.1689 | 2.4911 | -116.8599 | 114.1766

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0025942 | 0.002598 | 0.0026295 | 0.0025942 | 0.002598 | 0.0026295 | 0.0005991 | 0.00059998 | 0.00060726 | 0.00059911 | 0.00059999 | 0.00060727 | 0.00025534 | 0.00027408 | -0.00054508 | -0.00025528 | -0.00027402 | 0.00054515 | 0.00052872 | -0.00041063 | 3.454e-05 | -0.00052866 | 0.00041071 | -3.4471e-05 | -61.7367 | -60.5605 | -62.213 | 118.2633 | 119.4395 | 117.787 |  | 0.98005 | 0.82286 | 0.8994 | 0.9799 | 0.8229 | 0.8995 | 2.4855 | -116.839 | 114.1613 | 2.4883 | -116.8495 | 114.1689
Line10_11_12 | 0.0025877 | 0.0025915 | 0.0026229 | 0.0025878 | 0.0025916 | 0.0026229 | 0.00059761 | 0.00059849 | 0.00060574 | 0.00059762 | 0.00059849 | 0.00060574 | 0.00025584 | 0.0002723 | -0.00054376 | -0.00025578 | -0.00027225 | 0.00054383 | 0.00052667 | -0.00041039 | 3.5608e-05 | -0.00052661 | 0.00041047 | -3.554e-05 | -61.5999 | -60.4251 | -62.0768 | 118.4001 | 119.5749 | 117.9232 |  | 0.97976 | 0.82294 | 0.89961 | 0.97961 | 0.82297 | 0.89971 | 2.4911 | -116.8599 | 114.1766 | 2.4939 | -116.8704 | 114.1842
Line11_12_13 | 0.0025878 | 0.0025916 | 0.0026229 | 0.0025878 | 0.0025916 | 0.002623 | 0.00059762 | 0.00059849 | 0.00060574 | 0.00059763 | 0.0005985 | 0.00060575 | 0.00025578 | 0.00027225 | -0.00054383 | -0.00025571 | -0.00027219 | 0.00054391 | 0.00052661 | -0.00041047 | 3.5539e-05 | -0.00052655 | 0.00041054 | -3.5471e-05 | -61.5999 | -60.4252 | -62.0768 | 118.4001 | 119.5748 | 117.9232 |  | 0.97961 | 0.82297 | 0.89971 | 0.97946 | 0.82301 | 0.89982 | 2.4939 | -116.8704 | 114.1842 | 2.4967 | -116.8809 | 114.1919
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.8912e-09 | -1.1269e-08 | 2.0384e-08 | 5.639e-09 | 7.7408e-09 | -1.3604e-08 | -2.0369e-08 | 1.4923e-08 | -6.5263e-10 | 1.372e-08 | -9.8008e-09 | 1.346e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97946 | 0.82301 | 0.89982 | 0.97946 | 0.82301 | 0.89982 | 2.4967 | -116.8809 | 114.1919 | 2.4967 | -116.8809 | 114.1919
Line13_13_14 | 0.0025879 | 0.0025917 | 0.0026231 | 0.0025879 | 0.0025917 | 0.0026231 | 0.00059765 | 0.00059853 | 0.00060577 | 0.00059766 | 0.00059853 | 0.00060578 | 0.00025572 | 0.0002722 | -0.00054393 | -0.00025566 | -0.00027214 | 0.000544 | 0.00052657 | -0.00041055 | 3.5472e-05 | -0.00052651 | 0.00041063 | -3.5403e-05 | -61.6 | -60.4253 | -62.0769 | 118.4 | 119.5747 | 117.9231 |  | 0.97946 | 0.82301 | 0.89982 | 0.97932 | 0.82304 | 0.89992 | 2.4967 | -116.8809 | 114.1919 | 2.4996 | -116.8914 | 114.1995
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9275e-09 | -7.5125e-09 | 1.3589e-08 | 2.6753e-09 | 3.9845e-09 | -6.8094e-09 | -1.358e-08 | 9.9485e-09 | -4.3509e-10 | 6.9306e-09 | -4.8265e-09 | -8.2949e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97946 | 0.82301 | 0.89982 | 0.97946 | 0.82301 | 0.89982 | 2.4967 | -116.8809 | 114.1919 | 2.4967 | -116.8809 | 114.1919
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9637e-09 | -3.7562e-09 | 6.7947e-09 | -2.8845e-10 | 2.2832e-10 | -1.4634e-11 | -6.7898e-09 | 4.9743e-09 | -2.1754e-10 | 1.408e-10 | 1.4778e-10 | -3.0049e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97946 | 0.82301 | 0.89982 | 0.97946 | 0.82301 | 0.89982 | 2.4967 | -116.8809 | 114.1919 | 2.4967 | -116.8809 | 114.1919
Line16_4_18 | 0 | 0.026678 | 0.029165 | 0 | 0.026678 | 0.029165 | 0 | 0.0061611 | 0.0067353 | 0 | 0.0061611 | 0.0067353 | -2.9462e-09 | 0.0035696 | 0.0042702 | -2.8644e-10 | -0.0035587 | -0.004253 | -6.8849e-09 | 0.0035741 | 0.0042668 | 1.407e-10 | -0.0035587 | -0.004253 | 0 | -161.9216 | 69.2132 | 0 | 18.0784 | -110.7868 |  | 0.97943 | 0.81988 | 0.89625 | 0.97895 | 0.81685 | 0.89299 | 2.4923 | -116.8855 | 114.1909 | 2.4962 | -116.9216 | 114.2132
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9492e-09 | -3.8018e-09 | 6.8265e-09 | -2.9071e-10 | 2.286e-10 | -1.342e-11 | -6.8415e-09 | 4.9775e-09 | -1.8965e-10 | 1.4025e-10 | 1.4974e-10 | -3.0193e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98005 | 0.82286 | 0.8994 | 0.98005 | 0.82286 | 0.8994 | 2.4855 | -116.839 | 114.1613 | 2.4855 | -116.839 | 114.1613
Line1_1_3 | 0.0025877 | 0.0025915 | 0.0026228 | 0.0025877 | 0.0025915 | 0.0026229 | 0.0005976 | 0.00059847 | 0.00060572 | 0.00059761 | 0.00059848 | 0.00060573 | 0.00025596 | 0.00027242 | -0.00054361 | -0.0002559 | -0.00027236 | 0.00054369 | 0.00052678 | -0.00041025 | 3.5744e-05 | -0.00052672 | 0.00041032 | -3.5676e-05 | -61.5998 | -60.425 | -62.0768 | 118.4002 | 119.575 | 117.9232 |  | 0.98005 | 0.82286 | 0.8994 | 0.9799 | 0.8229 | 0.8995 | 2.4855 | -116.839 | 114.1613 | 2.4883 | -116.8495 | 114.1689
Line2_1_4 | 0.0025932 | 0.026255 | 0.027439 | 0.0025932 | 0.026255 | 0.027439 | 0.00059888 | 0.0060634 | 0.0063369 | 0.00059889 | 0.0060634 | 0.0063369 | 0.00025238 | 0.0038533 | 0.0037383 | -0.00025215 | -0.0038419 | -0.003723 | 0.0005299 | 0.0031695 | 0.004302 | -0.0005296 | -0.0031549 | -0.0042889 | -62.0475 | -156.278 | 65.1509 | 117.9525 | 23.7221 | -114.8492 |  | 0.98005 | 0.82286 | 0.8994 | 0.97943 | 0.81988 | 0.89625 | 2.4855 | -116.839 | 114.1613 | 2.4923 | -116.8855 | 114.1909
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.8983e-09 | -7.6036e-09 | 1.3653e-08 | 2.6585e-09 | 4.0304e-09 | -6.8399e-09 | -1.3683e-08 | 9.955e-09 | -3.793e-10 | 6.9817e-09 | -4.8278e-09 | -1.1228e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.98005 | 0.82286 | 0.8994 | 0.98005 | 0.82286 | 0.8994 | 2.4855 | -116.839 | 114.1613 | 2.4855 | -116.839 | 114.1613
Line4_2_6 | 0.0025942 | 0.002598 | 0.0026295 | 0.0025943 | 0.0025981 | 0.0026296 | 0.00059911 | 0.00059999 | 0.00060727 | 0.00059912 | 0.0006 | 0.00060727 | 0.00025528 | 0.00027402 | -0.00054515 | -0.00025522 | -0.00027396 | 0.00054523 | 0.00052866 | -0.00041071 | 3.4471e-05 | -0.0005286 | 0.00041078 | -3.4402e-05 | -61.7367 | -60.5606 | -62.213 | 118.2633 | 119.4394 | 117.787 |  | 0.9799 | 0.8229 | 0.8995 | 0.97976 | 0.82293 | 0.89961 | 2.4883 | -116.8495 | 114.1689 | 2.4912 | -116.86 | 114.1766
Line5_6_7 | 0.0025943 | 0.0025981 | 0.0026296 | 0.0025943 | 0.0025981 | 0.0026296 | 0.00059912 | 0.0006 | 0.00060727 | 0.00059913 | 0.0006 | 0.00060728 | 0.00025522 | 0.00027396 | -0.00054523 | -0.00025516 | -0.0002739 | 0.0005453 | 0.0005286 | -0.00041078 | 3.4402e-05 | -0.00052854 | 0.00041085 | -3.4334e-05 | -61.7368 | -60.5606 | -62.213 | 118.2632 | 119.4394 | 117.787 |  | 0.97976 | 0.82293 | 0.89961 | 0.97961 | 0.82297 | 0.89971 | 2.4912 | -116.86 | 114.1766 | 2.494 | -116.8705 | 114.1842
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.8806e-09 | -1.1303e-08 | 2.0408e-08 | 5.6314e-09 | 7.7634e-09 | -1.362e-08 | -2.0408e-08 | 1.4925e-08 | -6.3206e-10 | 1.3746e-08 | -9.802e-09 | 1.2052e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97961 | 0.82297 | 0.89971 | 0.97961 | 0.82297 | 0.89971 | 2.494 | -116.8705 | 114.1842 | 2.494 | -116.8705 | 114.1842
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9602e-09 | -3.7675e-09 | 6.8027e-09 | -2.8901e-10 | 2.2839e-10 | -1.4335e-11 | -6.8027e-09 | 4.9751e-09 | -2.1069e-10 | 1.4067e-10 | 1.4826e-10 | -3.0085e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97961 | 0.82297 | 0.89971 | 0.97961 | 0.82297 | 0.89971 | 2.494 | -116.8705 | 114.1842 | 2.494 | -116.8705 | 114.1842
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9602e-09 | -3.7675e-09 | 6.8027e-09 | -2.8901e-10 | 2.2839e-10 | -1.4336e-11 | -6.8027e-09 | 4.9751e-09 | -2.1069e-10 | 1.4067e-10 | 1.4826e-10 | -3.0085e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97961 | 0.82297 | 0.89971 | 0.97961 | 0.82297 | 0.89971 | 2.494 | -116.8705 | 114.1842 | 2.494 | -116.8705 | 114.1842
Line9_3_11 | 0.0025877 | 0.0025915 | 0.0026229 | 0.0025877 | 0.0025915 | 0.0026229 | 0.00059761 | 0.00059848 | 0.00060573 | 0.00059761 | 0.00059849 | 0.00060574 | 0.0002559 | 0.00027236 | -0.00054369 | -0.00025584 | -0.0002723 | 0.00054376 | 0.00052672 | -0.00041032 | 3.5676e-05 | -0.00052667 | 0.00041039 | -3.5608e-05 | -61.5998 | -60.4251 | -62.0768 | 118.4002 | 119.5749 | 117.9232 |  | 0.9799 | 0.8229 | 0.8995 | 0.97976 | 0.82294 | 0.89961 | 2.4883 | -116.8495 | 114.1689 | 2.4911 | -116.8599 | 114.1766