## LLL_max_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.32497 | 0.32497 | 0 | 0 | 0.22515 | 0.22515 | -0.081585 | 0.084753 | -0.15129 | 0.15762 | 112.3024 | -67.6976 | 0.76342 | 0.79487 | -6.0346 | -5.9644
Line10_11_12 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.078736 | 0.08124 | -0.14384 | 0.14885 | 112.8171 | -67.1829 | 0.81932 | 0.84727 | -5.8785 | -5.8082
Line11_12_13 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.08124 | 0.083744 | -0.14885 | 0.15386 | 112.8171 | -67.1829 | 0.84727 | 0.87523 | -5.8082 | -5.7423
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87523 | 0.87523 | -5.7423 | -5.7423
Line13_13_14 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.083744 | 0.086247 | -0.15386 | 0.15886 | 112.8171 | -67.1829 | 0.87523 | 0.90318 | -5.7423 | -5.6806
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87523 | 0.87523 | -5.7423 | -5.7423
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87523 | 0.87523 | -5.7423 | -5.7423
Line16_4_18 | 4.2793 | 4.2793 | 0 | 8.0393 | 2.9648 | 2.9648 | 0.54938 | -1e-07 | 1.0988 | -1e-07 | -69.5382 | 110.4618 | 0.41434 | 0 | -6.1032 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76342 | 0.76342 | -6.0346 | -6.0346
Line1_1_3 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.073729 | 0.076233 | -0.13383 | 0.13883 | 112.8171 | -67.1829 | 0.76342 | 0.79137 | -6.0346 | -5.9538
Line2_1_4 | 3.6053 | 3.6053 | 0 | 0 | 2.4978 | 2.4978 | 0.8552 | -0.46526 | 1.7043 | -0.92447 | -69.388 | 110.612 | 0.76342 | 0.41434 | -6.0346 | -6.1032
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76342 | 0.76342 | -6.0346 | -6.0346
Line4_2_6 | 0.32497 | 0.32497 | 0 | 0 | 0.22515 | 0.22515 | -0.084753 | 0.087921 | -0.15762 | 0.16396 | 112.3024 | -67.6976 | 0.79487 | 0.82632 | -5.9644 | -5.8996
Line5_6_7 | 0.32497 | 0.32497 | 0 | 0 | 0.22515 | 0.22515 | -0.087921 | 0.09109 | -0.16396 | 0.1703 | 112.3024 | -67.6976 | 0.82632 | 0.85778 | -5.8996 | -5.8396
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85778 | 0.85778 | -5.8396 | -5.8396
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85778 | 0.85778 | -5.8396 | -5.8396
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85778 | 0.85778 | -5.8396 | -5.8396
Line9_3_11 | 0.28888 | 0.28888 | 0 | 0 | 0.20014 | 0.20014 | -0.076233 | 0.078736 | -0.13883 | 0.14384 | 112.8171 | -67.1829 | 0.79137 | 0.81932 | -5.9538 | -5.8785

## LLL_max_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.3348 | 0.3348 | 0 | 0 | 0.23196 | 0.23196 | -0.087546 | 0.090909 | -0.16063 | 0.16736 | 112.3588 | -67.6412 | 0.78869 | 0.82109 | -6.232 | -6.152
Line10_11_12 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.084782 | 0.087462 | -0.15341 | 0.15877 | 112.8681 | -67.1319 | 0.84651 | 0.87543 | -6.0587 | -5.9806
Line11_12_13 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.087462 | 0.090142 | -0.15877 | 0.16413 | 112.8681 | -67.1319 | 0.87543 | 0.90434 | -5.9806 | -5.9076
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90434 | 0.90434 | -5.9076 | -5.9076
Line13_13_14 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.090142 | 0.092822 | -0.16413 | 0.16949 | 112.8681 | -67.1319 | 0.90434 | 0.93326 | -5.9076 | -5.8391
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90434 | 0.90434 | -5.9076 | -5.9076
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90434 | 0.90434 | -5.9076 | -5.9076
Line16_4_18 | 4.4124 | 4.4124 | 0 | 8.3118 | 3.057 | 3.057 | 0.58408 | -1e-07 | 1.1682 | -1e-07 | -69.7214 | 110.2786 | 0.42723 | 0 | -6.2864 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78869 | 0.78869 | -6.232 | -6.232
Line1_1_3 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.079423 | 0.082103 | -0.14269 | 0.14805 | 112.8681 | -67.1319 | 0.78869 | 0.8176 | -6.232 | -6.1423
Line2_1_4 | 3.7331 | 3.7331 | 0 | 0 | 2.5864 | 2.5864 | 0.9143 | -0.49621 | 1.8235 | -0.9873 | -69.6025 | 110.3975 | 0.78869 | 0.42723 | -6.232 | -6.2864
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78869 | 0.78869 | -6.232 | -6.232
Line4_2_6 | 0.3348 | 0.3348 | 0 | 0 | 0.23196 | 0.23196 | -0.090909 | 0.094272 | -0.16736 | 0.17408 | 112.3588 | -67.6412 | 0.82109 | 0.85348 | -6.152 | -6.0781
Line5_6_7 | 0.3348 | 0.3348 | 0 | 0 | 0.23196 | 0.23196 | -0.094272 | 0.097635 | -0.17408 | 0.18081 | 112.3588 | -67.6412 | 0.85348 | 0.88588 | -6.0781 | -6.0096
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88588 | 0.88588 | -6.0096 | -6.0096
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88588 | 0.88588 | -6.0096 | -6.0096
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88588 | 0.88588 | -6.0096 | -6.0096
Line9_3_11 | 0.29887 | 0.29887 | 0 | 0 | 0.20706 | 0.20706 | -0.082103 | 0.084782 | -0.14805 | 0.15341 | 112.8681 | -67.1319 | 0.8176 | 0.84651 | -6.1423 | -6.0587

## LLL_max_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.12039 | 0.12039 | 0 | 0 | 0.083411 | 0.083411 | -0.006237 | 0.0066719 | -0.09019 | 0.09106 | 93.9805 | -86.0195 | 1.0839 | 1.0946 | 0.024519 | -0.21006
Line10_11_12 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0060352 | 0.0063806 | -0.081782 | 0.082473 | 93.8274 | -86.1726 | 1.103 | 1.1127 | -0.3931 | -0.5965
Line11_12_13 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0063806 | 0.0067261 | -0.082473 | 0.083164 | 93.8274 | -86.1726 | 1.1127 | 1.1223 | -0.5965 | -0.79641
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1223 | 1.1223 | -0.79641 | -0.79641
Line13_13_14 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0067261 | 0.0070715 | -0.083164 | 0.083855 | 93.8274 | -86.1726 | 1.1223 | 1.1319 | -0.79641 | -0.99292
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1223 | 1.1223 | -0.79641 | -0.79641
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1223 | 1.1223 | -0.79641 | -0.79641
Line16_4_18 | 0.035619 | 0.035619 | 0 | 0.066915 | 0.024677 | 0.024677 | 0.019068 | -0.01903 | 0.019106 | -0.01903 | -45.1981 | 134.8019 | 1.0939 | 1.0906 | -0.14093 | -0.19806
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0839 | 1.0839 | 0.024519 | 0.024519
Line1_1_3 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0053443 | 0.0056897 | -0.080401 | 0.081091 | 93.8274 | -86.1726 | 1.0839 | 1.0934 | 0.024519 | -0.18612
Line2_1_4 | 0.10837 | 0.10837 | 0 | 0 | 0.07508 | 0.07508 | -0.012793 | 0.013146 | -0.080364 | 0.081069 | 99.0698 | -80.9302 | 1.0839 | 1.0939 | 0.024519 | -0.14093
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0839 | 1.0839 | 0.024519 | 0.024519
Line4_2_6 | 0.12039 | 0.12039 | 0 | 0 | 0.083411 | 0.083411 | -0.0066719 | 0.0071067 | -0.09106 | 0.09193 | 93.9805 | -86.0195 | 1.0946 | 1.1054 | -0.21006 | -0.44005
Line5_6_7 | 0.12039 | 0.12039 | 0 | 0 | 0.083411 | 0.083411 | -0.0071067 | 0.0075416 | -0.09193 | 0.0928 | 93.9805 | -86.0195 | 1.1054 | 1.1162 | -0.44005 | -0.6656
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1162 | 1.1162 | -0.6656 | -0.6656
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1162 | 1.1162 | -0.6656 | -0.6656
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1162 | 1.1162 | -0.6656 | -0.6656
Line9_3_11 | 0.10731 | 0.10731 | 0 | 0 | 0.074344 | 0.074344 | -0.0056897 | 0.0060352 | -0.081091 | 0.081782 | 93.8274 | -86.1726 | 1.0934 | 1.103 | -0.18612 | -0.3931

## LLL_max_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.1213 | 0.1213 | 0 | 0 | 0.084041 | 0.084041 | -0.0067259 | 0.0071674 | -0.095199 | 0.096082 | 94.0592 | -85.9408 | 1.1356 | 1.1465 | 0.017899 | -0.20695
Line10_11_12 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0065032 | 0.0068567 | -0.086627 | 0.087334 | 93.9091 | -86.0909 | 1.155 | 1.1648 | -0.3841 | -0.58006
Line11_12_13 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0068567 | 0.0072103 | -0.087334 | 0.088041 | 93.9091 | -86.0909 | 1.1648 | 1.1745 | -0.58006 | -0.77278
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1745 | 1.1745 | -0.77278 | -0.77278
Line13_13_14 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0072103 | 0.0075638 | -0.088041 | 0.088748 | 93.9091 | -86.0909 | 1.1745 | 1.1843 | -0.77278 | -0.96232
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1745 | 1.1745 | -0.77278 | -0.77278
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1745 | 1.1745 | -0.77278 | -0.77278
Line16_4_18 | 0.037299 | 0.037299 | 0 | 0.070262 | 0.025842 | 0.025842 | 0.02091 | -0.020868 | 0.020952 | -0.020868 | -45.2026 | 134.7974 | 1.1455 | 1.1421 | -0.14543 | -0.20255
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1356 | 1.1356 | 0.017899 | 0.017899
Line1_1_3 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0057961 | 0.0061496 | -0.085213 | 0.08592 | 93.9091 | -86.0909 | 1.1356 | 1.1453 | 0.017899 | -0.1848
Line2_1_4 | 0.10744 | 0.10744 | 0 | 0 | 0.074435 | 0.074435 | -0.01216 | 0.012506 | -0.083649 | 0.084342 | 98.2891 | -81.7109 | 1.1356 | 1.1455 | 0.017899 | -0.14543
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1356 | 1.1356 | 0.017899 | 0.017899
Line4_2_6 | 0.1213 | 0.1213 | 0 | 0 | 0.084041 | 0.084041 | -0.0071674 | 0.0076088 | -0.096082 | 0.096965 | 94.0592 | -85.9408 | 1.1465 | 1.1573 | -0.20695 | -0.42758
Line5_6_7 | 0.1213 | 0.1213 | 0 | 0 | 0.084041 | 0.084041 | -0.0076088 | 0.0080502 | -0.096965 | 0.097848 | 94.0592 | -85.9408 | 1.1573 | 1.1682 | -0.42758 | -0.6441
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1682 | 1.1682 | -0.6441 | -0.6441
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1682 | 1.1682 | -0.6441 | -0.6441
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1682 | 1.1682 | -0.6441 | -0.6441
Line9_3_11 | 0.10856 | 0.10856 | 0 | 0 | 0.075212 | 0.075212 | -0.0061496 | 0.0065032 | -0.08592 | 0.086627 | 93.9091 | -86.0909 | 1.1453 | 1.155 | -0.1848 | -0.3841

## LLL_min_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.0049477 | 0.0049477 | 0 | 0 | 0.0034279 | 0.0034279 | -0.0019748 | 0.0019762 | -0.0013385 | 0.0013399 | 134.3184 | -45.6816 | 0.69595 | 0.69653 | -11.5528 | -11.5426
Line10_11_12 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019731 | 0.0019745 | -0.0013332 | 0.0013347 | 134.4202 | -45.5798 | 0.69711 | 0.69769 | -11.5323 | -11.5221
Line11_12_13 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019745 | 0.0019759 | -0.0013347 | 0.0013361 | 134.4202 | -45.5798 | 0.69769 | 0.69827 | -11.5221 | -11.5119
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69827 | 0.69827 | -11.5119 | -11.5119
Line13_13_14 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019758 | 0.0019772 | -0.0013361 | 0.0013376 | 134.42 | -45.58 | 0.69827 | 0.69885 | -11.5119 | -11.5018
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69827 | 0.69827 | -11.5119 | -11.5119
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69827 | 0.69827 | -11.5119 | -11.5119
Line16_4_18 | 2.9036 | 2.9036 | 0 | 4.7948 | 2.0117 | 2.0117 | 0.48561 | -1e-07 | 0.50584 | -1e-07 | -57.7375 | 122.2625 | 0.34857 | 0 | -11.5684 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69595 | 0.69595 | -11.5528 | -11.5528
Line1_1_3 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019703 | 0.0019717 | -0.0013303 | 0.0013318 | 134.4203 | -45.5797 | 0.69595 | 0.69653 | -11.5528 | -11.5425
Line2_1_4 | 2.8936 | 2.8936 | 0 | 0 | 2.0048 | 2.0048 | 0.96651 | -0.48422 | 1.0062 | -0.50385 | -57.7063 | 122.2937 | 0.69595 | 0.34857 | -11.5528 | -11.5684
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69595 | 0.69595 | -11.5528 | -11.5528
Line4_2_6 | 0.0049477 | 0.0049477 | 0 | 0 | 0.0034279 | 0.0034279 | -0.0019762 | 0.0019776 | -0.0013399 | 0.0013414 | 134.3184 | -45.6816 | 0.69653 | 0.69711 | -11.5426 | -11.5324
Line5_6_7 | 0.0049477 | 0.0049477 | 0 | 0 | 0.0034279 | 0.0034279 | -0.0019776 | 0.001979 | -0.0013414 | 0.0013429 | 134.3183 | -45.6817 | 0.69711 | 0.6977 | -11.5324 | -11.5223
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6977 | 0.6977 | -11.5223 | -11.5223
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6977 | 0.6977 | -11.5223 | -11.5223
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6977 | 0.6977 | -11.5223 | -11.5223
Line9_3_11 | 0.0049304 | 0.0049304 | 0 | 0 | 0.0034159 | 0.0034159 | -0.0019717 | 0.0019731 | -0.0013318 | 0.0013332 | 134.4203 | -45.5797 | 0.69653 | 0.69711 | -11.5425 | -11.5323

## LLL_min_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 0.0046873 | 0.0046873 | 0 | 0 | 0.0032475 | 0.0032475 | -0.0017724 | 0.0017737 | -0.0012013 | 0.0012026 | 134.3184 | -45.6816 | 0.65932 | 0.65987 | -11.5528 | -11.5426
Line10_11_12 | 0.0046709 | 0.0046709 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017708 | 0.0017721 | -0.0011966 | 0.0011979 | 134.4202 | -45.5798 | 0.66042 | 0.66097 | -11.5323 | -11.5221
Line11_12_13 | 0.0046709 | 0.0046709 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017721 | 0.0017733 | -0.0011979 | 0.0011992 | 134.4202 | -45.5798 | 0.66097 | 0.66152 | -11.5221 | -11.5119
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66152 | 0.66152 | -11.5119 | -11.5119
Line13_13_14 | 0.0046709 | 0.0046709 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017733 | 0.0017746 | -0.0011992 | 0.0012005 | 134.42 | -45.58 | 0.66152 | 0.66207 | -11.5119 | -11.5018
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66152 | 0.66152 | -11.5119 | -11.5119
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66152 | 0.66152 | -11.5119 | -11.5119
Line16_4_18 | 2.7508 | 2.7508 | 0 | 4.5424 | 1.9058 | 1.9058 | 0.43584 | -1e-07 | 0.454 | -1e-07 | -57.7375 | 122.2625 | 0.33023 | 0 | -11.5684 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65932 | 0.65932 | -11.5528 | -11.5528
Line1_1_3 | 0.004671 | 0.004671 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017683 | 0.0017696 | -0.001194 | 0.0011953 | 134.4203 | -45.5797 | 0.65932 | 0.65987 | -11.5528 | -11.5425
Line2_1_4 | 2.7413 | 2.7413 | 0 | 0 | 1.8992 | 1.8992 | 0.86745 | -0.43459 | 0.9031 | -0.45221 | -57.7063 | 122.2937 | 0.65932 | 0.33023 | -11.5528 | -11.5684
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65932 | 0.65932 | -11.5528 | -11.5528
Line4_2_6 | 0.0046873 | 0.0046873 | 0 | 0 | 0.0032475 | 0.0032475 | -0.0017736 | 0.0017749 | -0.0012026 | 0.0012039 | 134.3184 | -45.6816 | 0.65987 | 0.66042 | -11.5426 | -11.5324
Line5_6_7 | 0.0046873 | 0.0046873 | 0 | 0 | 0.0032475 | 0.0032475 | -0.0017749 | 0.0017762 | -0.0012039 | 0.0012053 | 134.3183 | -45.6817 | 0.66042 | 0.66097 | -11.5324 | -11.5223
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66097 | 0.66097 | -11.5223 | -11.5223
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66097 | 0.66097 | -11.5223 | -11.5223
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66097 | 0.66097 | -11.5223 | -11.5223
Line9_3_11 | 0.004671 | 0.004671 | 0 | 0 | 0.0032361 | 0.0032361 | -0.0017696 | 0.0017708 | -0.0011953 | 0.0011966 | 134.4203 | -45.5797 | 0.65987 | 0.66042 | -11.5425 | -11.5323

## LLL_min_fault_6
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 5.2325e-05 | 5.2325e-05 | 0 | 0 | 3.6252e-05 | 3.6252e-05 | -2.8824e-05 | 2.8824e-05 | -1.8685e-05 | 1.8685e-05 | 146.9224 | -33.0776 | 0.94756 | 0.94756 | -0.1244 | -0.12431
Line10_11_12 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8757e-05 | 2.8757e-05 | -1.8569e-05 | 1.8569e-05 | 147.0242 | -32.9758 | 0.94757 | 0.94757 | -0.12422 | -0.12414
Line11_12_13 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8757e-05 | 2.8757e-05 | -1.8569e-05 | 1.8569e-05 | 147.0241 | -32.9759 | 0.94757 | 0.94758 | -0.12414 | -0.12405
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94758 | 0.94758 | -0.12405 | -0.12405
Line13_13_14 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8757e-05 | 2.8757e-05 | -1.857e-05 | 1.857e-05 | 147.0239 | -32.9761 | 0.94758 | 0.94759 | -0.12405 | -0.12396
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94758 | 0.94758 | -0.12405 | -0.12405
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94758 | 0.94758 | -0.12405 | -0.12405
Line16_4_18 | 0.030707 | 0.030707 | 0 | 0.050707 | 0.021274 | 0.021274 | 0.014198 | -0.014144 | 0.0142 | -0.014144 | -45.1336 | 134.8664 | 0.94388 | 0.9402 | -0.12903 | -0.1336
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.1244 | -0.1244
Line1_1_3 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8756e-05 | 2.8757e-05 | -1.8569e-05 | 1.8569e-05 | 147.0243 | -32.9757 | 0.94756 | 0.94756 | -0.1244 | -0.12431
Line2_1_4 | 0.030601 | 0.030601 | 0 | 0 | 0.021201 | 0.021201 | 0.014211 | -0.014157 | 0.0142 | -0.014144 | -45.1023 | 134.8977 | 0.94756 | 0.94388 | -0.1244 | -0.12903
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94756 | 0.94756 | -0.1244 | -0.1244
Line4_2_6 | 5.2325e-05 | 5.2325e-05 | 0 | 0 | 3.6252e-05 | 3.6252e-05 | -2.8824e-05 | 2.8824e-05 | -1.8685e-05 | 1.8685e-05 | 146.9223 | -33.0777 | 0.94756 | 0.94757 | -0.12431 | -0.12422
Line5_6_7 | 5.2325e-05 | 5.2325e-05 | 0 | 0 | 3.6252e-05 | 3.6252e-05 | -2.8824e-05 | 2.8824e-05 | -1.8685e-05 | 1.8686e-05 | 146.9222 | -33.0778 | 0.94757 | 0.94757 | -0.12422 | -0.12414
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94757 | 0.94757 | -0.12414 | -0.12414
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94757 | 0.94757 | -0.12414 | -0.12414
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94757 | 0.94757 | -0.12414 | -0.12414
Line9_3_11 | 5.2142e-05 | 5.2142e-05 | 0 | 0 | 3.6125e-05 | 3.6125e-05 | -2.8756e-05 | 2.8757e-05 | -1.8569e-05 | 1.8569e-05 | 147.0242 | -32.9758 | 0.94756 | 0.94757 | -0.12431 | -0.12422

## LLL_min_fault_10
name | pf_ikss_from_ka | pf_ikss_to_ka | pf_ip_from_ka | pf_ip_to_ka | pf_skss_from_mw | pf_skss_to_mw | pf_p_from_mw | pf_p_to_mw | pf_q_from_mvar | pf_q_to_mvar | pf_ikss_from_degree | pf_ikss_to_degree | pf_vm_from_pu | pf_vm_to_pu | pf_va_from_degree | pf_va_to_degree
Line0_1_2 | 4.9571e-05 | 4.9571e-05 | 0 | 0 | 3.4344e-05 | 3.4344e-05 | -2.587e-05 | 2.587e-05 | -1.677e-05 | 1.677e-05 | 146.9224 | -33.0776 | 0.89769 | 0.89769 | -0.1244 | -0.12431
Line10_11_12 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.5809e-05 | -1.6666e-05 | 1.6666e-05 | 147.0242 | -32.9758 | 0.8977 | 0.8977 | -0.12422 | -0.12414
Line11_12_13 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.581e-05 | -1.6666e-05 | 1.6666e-05 | 147.0241 | -32.9759 | 0.8977 | 0.89771 | -0.12414 | -0.12405
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89771 | 0.89771 | -0.12405 | -0.12405
Line13_13_14 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.581e-05 | -1.6666e-05 | 1.6666e-05 | 147.0239 | -32.9761 | 0.89771 | 0.89771 | -0.12405 | -0.12396
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89771 | 0.89771 | -0.12405 | -0.12405
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89771 | 0.89771 | -0.12405 | -0.12405
Line16_4_18 | 0.029091 | 0.029091 | 0 | 0.048038 | 0.020155 | 0.020155 | 0.012743 | -0.012694 | 0.012745 | -0.012694 | -45.1336 | 134.8664 | 0.89421 | 0.89071 | -0.12903 | -0.1336
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.1244 | -0.1244
Line1_1_3 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.5809e-05 | -1.6666e-05 | 1.6666e-05 | 147.0243 | -32.9757 | 0.89769 | 0.89769 | -0.1244 | -0.12431
Line2_1_4 | 0.028991 | 0.028991 | 0 | 0 | 0.020085 | 0.020085 | 0.012754 | -0.012706 | 0.012745 | -0.012694 | -45.1023 | 134.8977 | 0.89769 | 0.89421 | -0.1244 | -0.12903
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89769 | 0.89769 | -0.1244 | -0.1244
Line4_2_6 | 4.9571e-05 | 4.9571e-05 | 0 | 0 | 3.4344e-05 | 3.4344e-05 | -2.587e-05 | 2.587e-05 | -1.677e-05 | 1.677e-05 | 146.9223 | -33.0777 | 0.89769 | 0.8977 | -0.12431 | -0.12422
Line5_6_7 | 4.9571e-05 | 4.9571e-05 | 0 | 0 | 3.4344e-05 | 3.4344e-05 | -2.587e-05 | 2.587e-05 | -1.677e-05 | 1.677e-05 | 146.9222 | -33.0778 | 0.8977 | 0.8977 | -0.12422 | -0.12414
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8977 | 0.8977 | -0.12414 | -0.12414
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8977 | 0.8977 | -0.12414 | -0.12414
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8977 | 0.8977 | -0.12414 | -0.12414
Line9_3_11 | 4.9398e-05 | 4.9398e-05 | 0 | 0 | 3.4224e-05 | 3.4224e-05 | -2.5809e-05 | 2.5809e-05 | -1.6666e-05 | 1.6666e-05 | 147.0242 | -32.9758 | 0.89769 | 0.8977 | -0.12431 | -0.12422

## LL_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.12004 | 0.27826 | 0.2879 | 0.12004 | 0.27826 | 0.2879 | 0.027723 | 0.06426 | 0.066487 | 0.027723 | 0.06426 | 0.066487 | -0.0066356 | -0.043731 | 0.0053609 | 0.0067797 | 0.044505 | -0.004532 | -0.02942 | -0.038454 | -0.05306 | 0.029708 | 0.040002 | 0.054718 | 103.3755 | 5.6755 | -149.9183 | -76.6245 | -174.3245 | 30.0817 | 1.0879 | 0.9062 | 0.80211 | 1.0992 | 0.93122 | 0.8258 | 0.66504 | -132.9982 | 125.851 | 0.51995 | -132.3743 | 124.8165
Line10_11_12 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0054328 | -0.040559 | 0.0029652 | 0.0055444 | 0.041166 | -0.0022943 | -0.026465 | -0.035746 | -0.050471 | 0.026688 | 0.03696 | 0.051813 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.1076 | 0.95025 | 0.84519 | 1.1175 | 0.9724 | 0.86702 | 0.38687 | -131.8661 | 124.0632 | 0.25148 | -131.3386 | 123.2363
Line11_12_13 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0055444 | -0.041166 | 0.0022943 | 0.0056559 | 0.041773 | -0.0016234 | -0.026688 | -0.03696 | -0.051813 | 0.026911 | 0.038174 | 0.053154 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.1175 | 0.9724 | 0.86702 | 1.1274 | 0.99463 | 0.88902 | 0.25148 | -131.3386 | 123.2363 | 0.11846 | -130.8346 | 122.4502
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5966e-10 | -4.0105e-10 | -1.5649e-09 | -9.5966e-10 | 4.0105e-10 | 1.5649e-09 | -2.6922e-11 | 2.1594e-09 | -4.3897e-10 | 2.6922e-11 | -2.1594e-09 | 4.3897e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1274 | 0.99463 | 0.88902 | 1.1274 | 0.99463 | 0.88902 | 0.11846 | -130.8346 | 122.4502 | 0.11846 | -130.8346 | 122.4502
Line13_13_14 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0056559 | -0.041773 | 0.0016234 | 0.0057675 | 0.04238 | -0.00095251 | -0.026911 | -0.038174 | -0.053154 | 0.027134 | 0.039388 | 0.054496 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.1274 | 0.99463 | 0.88902 | 1.1373 | 1.0169 | 0.91117 | 0.11846 | -130.8346 | 122.4502 | -0.012245 | -130.3527 | 121.7021
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3977e-10 | -2.6737e-10 | -1.0433e-09 | -6.3977e-10 | 2.6737e-10 | 1.0433e-09 | -1.7948e-11 | 1.4396e-09 | -2.9264e-10 | 1.7948e-11 | -1.4396e-09 | 2.9264e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1274 | 0.99463 | 0.88902 | 1.1274 | 0.99463 | 0.88902 | 0.11846 | -130.8346 | 122.4502 | 0.11846 | -130.8346 | 122.4502
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1989e-10 | -1.3368e-10 | -5.2163e-10 | -3.1989e-10 | 1.3368e-10 | 5.2163e-10 | -8.974e-12 | 7.1981e-10 | -1.4632e-10 | 8.9739e-12 | -7.1981e-10 | 1.4632e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1274 | 0.99463 | 0.88902 | 1.1274 | 0.99463 | 0.88902 | 0.11846 | -130.8346 | 122.4502 | 0.11846 | -130.8346 | 122.4502
Line16_4_18 | 0 | 3.6866 | 3.6866 | 0 | 3.6866 | 3.6866 | 0 | 0.85139 | 0.85139 | 0 | 0.85139 | 0.85139 | 2.2277e-10 | 0.58108 | -0.30926 | -2.2277e-10 | -0.44517 | 0.44517 | -6.0249e-11 | 0.12002 | 0.42364 | 6.0249e-11 | 0.15181 | -0.15181 | 0 | -160.3584 | 19.6416 | 0 | 19.6416 | -160.3584 | 1.1049 | 0.69692 | 0.61606 | 1.1049 | 0.55244 | 0.55244 | 0.81154 | -148.6887 | 145.7714 | 0.81154 | -179.1885 | -179.1885
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5131e-10 | -3.884e-10 | -7.1297e-10 | -1.5131e-10 | 3.884e-10 | 7.1297e-10 | -4.8613e-11 | 7.8472e-10 | -3.1481e-10 | 4.8613e-11 | -7.8472e-10 | 3.1481e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0879 | 0.9062 | 0.80211 | 1.0879 | 0.9062 | 0.80211 | 0.66504 | -132.9982 | 125.851 | 0.66504 | -132.9982 | 125.851
Line1_1_3 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0052097 | -0.039345 | 0.0043071 | 0.0053213 | 0.039952 | -0.0036361 | -0.026019 | -0.033319 | -0.047787 | 0.026242 | 0.034532 | 0.049129 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.0879 | 0.9062 | 0.80211 | 1.0977 | 0.92818 | 0.82355 | 0.66504 | -132.9982 | 125.851 | 0.5247 | -132.4187 | 124.9337
Line2_1_4 | 0.17814 | 3.1133 | 3.1623 | 0.17814 | 3.1133 | 3.1623 | 0.041139 | 0.71898 | 0.7303 | 0.041139 | 0.71898 | 0.7303 | -0.026301 | 0.59177 | -0.16845 | 0.026618 | -0.49484 | 0.26845 | -0.03621 | 0.27262 | 0.56104 | 0.036845 | -0.078773 | -0.36104 | 126.6571 | -157.7336 | 19.1385 | -53.3429 | 22.2664 | -160.8615 | 1.0879 | 0.9062 | 0.80211 | 1.1049 | 0.69692 | 0.61606 | 0.66504 | -132.9982 | 125.851 | 0.81154 | -148.6887 | 145.7714
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0262e-10 | -7.7681e-10 | -1.4259e-09 | -3.0262e-10 | 7.7681e-10 | 1.4259e-09 | -9.7225e-11 | 1.5694e-09 | -6.2962e-10 | 9.7225e-11 | -1.5694e-09 | 6.2962e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0879 | 0.9062 | 0.80211 | 1.0879 | 0.9062 | 0.80211 | 0.66504 | -132.9982 | 125.851 | 0.66504 | -132.9982 | 125.851
Line4_2_6 | 0.12004 | 0.27826 | 0.2879 | 0.12004 | 0.27826 | 0.2879 | 0.027723 | 0.06426 | 0.066487 | 0.027723 | 0.06426 | 0.066487 | -0.0067797 | -0.044505 | 0.004532 | 0.0069238 | 0.045279 | -0.0037032 | -0.029708 | -0.040002 | -0.054718 | 0.029996 | 0.041551 | 0.056376 | 103.3755 | 5.6755 | -149.9183 | -76.6245 | -174.3245 | 30.0817 | 1.0992 | 0.93122 | 0.8258 | 1.1104 | 0.95634 | 0.84974 | 0.51995 | -132.3743 | 124.8165 | 0.37782 | -131.7831 | 123.8399
Line5_6_7 | 0.12004 | 0.27826 | 0.2879 | 0.12004 | 0.27826 | 0.2879 | 0.027723 | 0.06426 | 0.066487 | 0.027723 | 0.06426 | 0.066487 | -0.0069238 | -0.045279 | 0.0037032 | 0.0070679 | 0.046053 | -0.0028743 | -0.029996 | -0.041551 | -0.056376 | 0.030284 | 0.0431 | 0.058033 | 103.3755 | 5.6754 | -149.9183 | -76.6245 | -174.3246 | 30.0817 | 1.1104 | 0.95634 | 0.84974 | 1.1217 | 0.98156 | 0.87392 | 0.37782 | -131.7831 | 123.8399 | 0.23855 | -131.2223 | 122.9172
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8544e-10 | -5.2221e-10 | -1.6796e-09 | -8.8544e-10 | 5.2221e-10 | 1.6796e-09 | -5.3943e-11 | 2.2064e-09 | -5.137e-10 | 5.3943e-11 | -2.2064e-09 | 5.137e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1217 | 0.98156 | 0.87392 | 1.1217 | 0.98156 | 0.87392 | 0.23855 | -131.2223 | 122.9172 | 0.23855 | -131.2223 | 122.9172
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9515e-10 | -1.7407e-10 | -5.5987e-10 | -2.9515e-10 | 1.7407e-10 | 5.5987e-10 | -1.7981e-11 | 7.3545e-10 | -1.7123e-10 | 1.7981e-11 | -7.3545e-10 | 1.7123e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1217 | 0.98156 | 0.87392 | 1.1217 | 0.98156 | 0.87392 | 0.23855 | -131.2223 | 122.9172 | 0.23855 | -131.2223 | 122.9172
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9515e-10 | -1.7407e-10 | -5.5987e-10 | -2.9515e-10 | 1.7407e-10 | 5.5987e-10 | -1.7981e-11 | 7.3545e-10 | -1.7123e-10 | 1.7981e-11 | -7.3545e-10 | 1.7123e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1217 | 0.98156 | 0.87392 | 1.1217 | 0.98156 | 0.87392 | 0.23855 | -131.2223 | 122.9172 | 0.23855 | -131.2223 | 122.9172
Line9_3_11 | 0.10562 | 0.24636 | 0.25902 | 0.10562 | 0.24636 | 0.25902 | 0.024392 | 0.056894 | 0.059818 | 0.024392 | 0.056894 | 0.059818 | -0.0053213 | -0.039952 | 0.0036361 | 0.0054328 | 0.040559 | -0.0029652 | -0.026242 | -0.034532 | -0.049129 | 0.026465 | 0.035746 | 0.050471 | 101.9876 | 6.743 | -149.2992 | -78.0124 | -173.257 | 30.7008 | 1.0977 | 0.92818 | 0.82355 | 1.1076 | 0.95025 | 0.84519 | 0.5247 | -132.4187 | 124.9337 | 0.38687 | -131.8661 | 124.0632

## LL_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.12125 | 0.28676 | 0.29545 | 0.12125 | 0.28676 | 0.29545 | 0.028001 | 0.066224 | 0.068232 | 0.028001 | 0.066224 | 0.068232 | -0.0072796 | -0.047408 | 0.0062354 | 0.0074266 | 0.04823 | -0.0053624 | -0.031079 | -0.040686 | -0.056392 | 0.031373 | 0.04233 | 0.058138 | 103.86 | 5.8931 | -150.127 | -76.14 | -174.1069 | 29.873 | 1.14 | 0.94335 | 0.8315 | 1.1514 | 0.969 | 0.85567 | 0.67744 | -133.4704 | 126.1827 | 0.54223 | -132.8342 | 125.1429
Line10_11_12 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0059982 | -0.044121 | 0.0036669 | 0.0061128 | 0.044772 | -0.0029546 | -0.028047 | -0.038002 | -0.053845 | 0.028276 | 0.039303 | 0.05527 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.16 | 0.98872 | 0.87564 | 1.1701 | 1.0115 | 0.89801 | 0.41665 | -132.313 | 124.377 | 0.28961 | -131.7733 | 123.5412
Line11_12_13 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0061128 | -0.044772 | 0.0029546 | 0.0062274 | 0.045422 | -0.0022423 | -0.028276 | -0.039303 | -0.05527 | 0.028506 | 0.040604 | 0.056694 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.1701 | 1.0115 | 0.89801 | 1.1801 | 1.0345 | 0.92056 | 0.28961 | -131.7733 | 123.5412 | 0.16473 | -131.2575 | 122.7461
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0401e-09 | -5.0503e-10 | -1.8042e-09 | -1.0401e-09 | 5.0503e-10 | 1.8042e-09 | -4.1056e-11 | 2.4435e-09 | -5.3366e-10 | 4.1056e-11 | -2.4435e-09 | 5.3366e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1801 | 1.0345 | 0.92056 | 1.1801 | 1.0345 | 0.92056 | 0.16473 | -131.2575 | 122.7461 | 0.16473 | -131.2575 | 122.7461
Line13_13_14 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0062274 | -0.045422 | 0.0022423 | 0.006342 | 0.046072 | -0.00153 | -0.028506 | -0.040604 | -0.056694 | 0.028735 | 0.041904 | 0.058119 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.1801 | 1.0345 | 0.92056 | 1.1902 | 1.0574 | 0.94328 | 0.16473 | -131.2575 | 122.7461 | 0.041965 | -130.7641 | 121.9892
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9337e-10 | -3.3669e-10 | -1.2028e-09 | -6.9337e-10 | 3.3669e-10 | 1.2028e-09 | -2.737e-11 | 1.629e-09 | -3.5577e-10 | 2.737e-11 | -1.629e-09 | 3.5577e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1801 | 1.0345 | 0.92056 | 1.1801 | 1.0345 | 0.92056 | 0.16473 | -131.2575 | 122.7461 | 0.16473 | -131.2575 | 122.7461
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4669e-10 | -1.6834e-10 | -6.0141e-10 | -3.4669e-10 | 1.6834e-10 | 6.0141e-10 | -1.3685e-11 | 8.1451e-10 | -1.7789e-10 | 1.3685e-11 | -8.1451e-10 | 1.7789e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1801 | 1.0345 | 0.92056 | 1.1801 | 1.0345 | 0.92056 | 0.16473 | -131.2575 | 122.7461 | 0.16473 | -131.2575 | 122.7461
Line16_4_18 | 0 | 3.8016 | 3.8016 | 0 | 3.8016 | 3.8016 | 0 | 0.87794 | 0.87794 | 0 | 0.87794 | 0.87794 | 2.4252e-10 | 0.6258 | -0.33676 | -2.4252e-10 | -0.48128 | 0.48128 | -6.6499e-11 | 0.12673 | 0.45136 | 6.6499e-11 | 0.16231 | -0.16231 | 0 | -160.5465 | 19.4535 | 0 | 19.4535 | -160.5465 | 1.1571 | 0.72727 | 0.64143 | 1.1571 | 0.57853 | 0.57853 | 0.81646 | -149.0986 | 146.1801 | 0.81646 | -179.1835 | -179.1835
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.674e-10 | -4.3718e-10 | -7.991e-10 | -1.674e-10 | 4.3718e-10 | 7.991e-10 | -5.4362e-11 | 8.8631e-10 | -3.6119e-10 | 5.4362e-11 | -8.8631e-10 | 3.6119e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 0.94335 | 0.8315 | 1.14 | 0.94335 | 0.8315 | 0.67744 | -133.4704 | 126.1827 | 0.67744 | -133.4704 | 126.1827
Line1_1_3 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0057689 | -0.042821 | 0.0050915 | 0.0058836 | 0.043471 | -0.0043792 | -0.027589 | -0.035401 | -0.050996 | 0.027818 | 0.036701 | 0.052421 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.14 | 0.94335 | 0.8315 | 1.15 | 0.96598 | 0.85346 | 0.67744 | -133.4704 | 126.1827 | 0.54591 | -132.8781 | 125.2565
Line2_1_4 | 0.17875 | 3.2235 | 3.2732 | 0.17875 | 3.2235 | 3.2732 | 0.04128 | 0.74444 | 0.7559 | 0.04128 | 0.74444 | 0.7559 | -0.027594 | 0.63877 | -0.18623 | 0.027913 | -0.53486 | 0.29337 | -0.038119 | 0.29181 | 0.60031 | 0.038758 | -0.083991 | -0.38604 | 126.5778 | -158.0231 | 18.9477 | -53.4222 | 21.9769 | -161.0523 | 1.14 | 0.94335 | 0.8315 | 1.1571 | 0.72727 | 0.64143 | 0.67744 | -133.4704 | 126.1827 | 0.81646 | -149.0986 | 146.1801
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3479e-10 | -8.7436e-10 | -1.5982e-09 | -3.3479e-10 | 8.7436e-10 | 1.5982e-09 | -1.0872e-10 | 1.7726e-09 | -7.2239e-10 | 1.0872e-10 | -1.7726e-09 | 7.2239e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 0.94335 | 0.8315 | 1.14 | 0.94335 | 0.8315 | 0.67744 | -133.4704 | 126.1827 | 0.67744 | -133.4704 | 126.1827
Line4_2_6 | 0.12125 | 0.28676 | 0.29545 | 0.12125 | 0.28676 | 0.29545 | 0.028001 | 0.066224 | 0.068232 | 0.028001 | 0.066224 | 0.068232 | -0.0074266 | -0.04823 | 0.0053624 | 0.0075736 | 0.049052 | -0.0044895 | -0.031373 | -0.04233 | -0.058138 | 0.031667 | 0.043975 | 0.059883 | 103.86 | 5.8931 | -150.127 | -76.14 | -174.1069 | 29.873 | 1.1514 | 0.969 | 0.85567 | 1.1628 | 0.99477 | 0.8801 | 0.54223 | -132.8342 | 125.1429 | 0.40967 | -132.2309 | 124.1605
Line5_6_7 | 0.12125 | 0.28676 | 0.29545 | 0.12125 | 0.28676 | 0.29545 | 0.028001 | 0.066224 | 0.068232 | 0.028001 | 0.066224 | 0.068232 | -0.0075736 | -0.049052 | 0.0044895 | 0.0077206 | 0.049874 | -0.0036166 | -0.031667 | -0.043975 | -0.059883 | 0.031961 | 0.045619 | 0.061629 | 103.86 | 5.8931 | -150.127 | -76.14 | -174.1069 | 29.873 | 1.1628 | 0.99477 | 0.8801 | 1.1743 | 1.0206 | 0.90478 | 0.40967 | -132.2309 | 124.1605 | 0.2797 | -131.6582 | 123.2314
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5941e-10 | -6.3614e-10 | -1.9255e-09 | -9.5941e-10 | 6.3614e-10 | 1.9255e-09 | -6.9362e-11 | 2.4956e-09 | -6.1712e-10 | 6.9362e-11 | -2.4956e-09 | 6.1712e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1743 | 1.0206 | 0.90478 | 1.1743 | 1.0206 | 0.90478 | 0.2797 | -131.6582 | 123.2314 | 0.2797 | -131.6582 | 123.2314
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.198e-10 | -2.1205e-10 | -6.4184e-10 | -3.198e-10 | 2.1205e-10 | 6.4184e-10 | -2.3121e-11 | 8.3185e-10 | -2.0571e-10 | 2.3121e-11 | -8.3185e-10 | 2.0571e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1743 | 1.0206 | 0.90478 | 1.1743 | 1.0206 | 0.90478 | 0.2797 | -131.6582 | 123.2314 | 0.2797 | -131.6582 | 123.2314
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.198e-10 | -2.1205e-10 | -6.4184e-10 | -3.198e-10 | 2.1205e-10 | 6.4184e-10 | -2.3121e-11 | 8.3185e-10 | -2.0571e-10 | 2.312e-11 | -8.3185e-10 | 2.0571e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1743 | 1.0206 | 0.90478 | 1.1743 | 1.0206 | 0.90478 | 0.2797 | -131.6582 | 123.2314 | 0.2797 | -131.6582 | 123.2314
Line9_3_11 | 0.10706 | 0.25503 | 0.26689 | 0.10706 | 0.25503 | 0.26689 | 0.024725 | 0.058896 | 0.061635 | 0.024725 | 0.058896 | 0.061635 | -0.0058836 | -0.043471 | 0.0043792 | 0.0059982 | 0.044121 | -0.0036669 | -0.027818 | -0.036701 | -0.052421 | 0.028047 | 0.038002 | 0.053845 | 102.4881 | 6.9483 | -149.5188 | -77.5119 | -173.0517 | 30.4812 | 1.15 | 0.96598 | 0.85346 | 1.16 | 0.98872 | 0.87564 | 0.54591 | -132.8781 | 125.2565 | 0.41665 | -132.313 | 124.377

## LL_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11916 | 0.12006 | 0.12197 | 0.11916 | 0.12006 | 0.12197 | 0.027519 | 0.027727 | 0.028168 | 0.027519 | 0.027727 | 0.028168 | -0.0017278 | -0.0025535 | -0.0019426 | 0.0018698 | 0.0026977 | 0.0020913 | -0.029835 | -0.029959 | -0.030392 | 0.030119 | 0.030247 | 0.03069 | 93.44 | -25.2506 | -146.2691 | -86.56 | 154.7494 | 33.7309 | 1.086 | 1.0844 | 1.0812 | 1.0966 | 1.0952 | 1.092 | 0.12554 | -120.1223 | 120.0737 | -0.11242 | -120.3471 | 119.8325
Line10_11_12 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.00168 | -0.0024342 | -0.0019093 | 0.0017928 | 0.0025486 | 0.0020275 | -0.027055 | -0.027149 | -0.027575 | 0.027281 | 0.027378 | 0.027811 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.1049 | 1.1037 | 1.1006 | 1.1144 | 1.1133 | 1.1103 | -0.29874 | -120.5223 | 119.6447 | -0.50548 | -120.7171 | 119.4358
Line11_12_13 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.0017928 | -0.0025486 | -0.0020275 | 0.0019057 | 0.002663 | 0.0021458 | -0.027281 | -0.027378 | -0.027811 | 0.027506 | 0.027607 | 0.028048 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.1144 | 1.1133 | 1.1103 | 1.1239 | 1.123 | 1.12 | -0.50548 | -120.7171 | 119.4358 | -0.70873 | -120.9085 | 119.2306
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1428e-10 | 9.0327e-10 | 8.6406e-10 | -9.1428e-10 | -9.0327e-10 | -8.6406e-10 | 1.6056e-10 | 2.0566e-10 | 1.7371e-10 | -1.6056e-10 | -2.0566e-10 | -1.7371e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1239 | 1.123 | 1.12 | 1.1239 | 1.123 | 1.12 | -0.70873 | -120.9085 | 119.2306 | -0.70873 | -120.9085 | 119.2306
Line13_13_14 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.0019057 | -0.002663 | -0.0021458 | 0.0020185 | 0.0027774 | 0.0022641 | -0.027506 | -0.027607 | -0.028048 | 0.027732 | 0.027836 | 0.028285 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.1239 | 1.123 | 1.12 | 1.1334 | 1.1327 | 1.1298 | -0.70873 | -120.9085 | 119.2306 | -0.90857 | -121.0967 | 119.0289
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0952e-10 | 6.0218e-10 | 5.7604e-10 | -6.0952e-10 | -6.0218e-10 | -5.7604e-10 | 1.0704e-10 | 1.3711e-10 | 1.1581e-10 | -1.0704e-10 | -1.3711e-10 | -1.1581e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1239 | 1.123 | 1.12 | 1.1239 | 1.123 | 1.12 | -0.70873 | -120.9085 | 119.2306 | -0.70873 | -120.9085 | 119.2306
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0476e-10 | 3.0109e-10 | 2.8802e-10 | -3.0476e-10 | -3.0109e-10 | -2.8802e-10 | 5.3521e-11 | 6.8554e-11 | 5.7904e-11 | -5.3521e-11 | -6.8554e-11 | -5.7904e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1239 | 1.123 | 1.12 | 1.1239 | 1.123 | 1.12 | -0.70873 | -120.9085 | 119.2306 | -0.70873 | -120.9085 | 119.2306
Line16_4_18 | 0 | 0.06123 | 0.06123 | 0 | 0.06123 | 0.06123 | 0 | 0.01414 | 0.01414 | 0 | 0.01414 | 0.01414 | 1.9703e-10 | 0.014944 | 0.0038761 | -1.9703e-10 | -0.014907 | -0.0038386 | -1.0651e-12 | 0.0039945 | 0.014901 | 1.0651e-12 | -0.0039195 | -0.014826 | 0 | -135.4076 | 44.5924 | 0 | 44.5924 | -135.4076 | 1.0989 | 1.094 | 1.0888 | 1.0989 | 1.09 | 1.0831 | 0.014424 | -120.4428 | 120.0116 | 0.014424 | -120.6761 | 120.0768
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4339e-10 | 1.3695e-10 | 1.2351e-10 | -1.4339e-10 | -1.3695e-10 | -1.2351e-10 | -9.1614e-12 | 8.9118e-12 | -5.3514e-12 | 9.1614e-12 | -8.9118e-12 | 5.3514e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.086 | 1.0844 | 1.0812 | 1.086 | 1.0844 | 1.0812 | 0.12554 | -120.1223 | 120.0737 | 0.12554 | -120.1223 | 120.0737
Line1_1_3 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.0014543 | -0.0022055 | -0.0016727 | 0.0015671 | 0.0023199 | 0.001791 | -0.026604 | -0.026692 | -0.027102 | 0.026829 | 0.026921 | 0.027338 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.086 | 1.0844 | 1.0812 | 1.0955 | 1.0941 | 1.0909 | 0.12554 | -120.1223 | 120.0737 | -0.08843 | -120.324 | 119.8573
Line2_1_4 | 0.13494 | 0.1167 | 0.080388 | 0.13494 | 0.1167 | 0.080388 | 0.031163 | 0.026951 | 0.018565 | 0.031163 | 0.026951 | 0.018565 | -0.0099948 | 0.0031674 | -0.0061539 | 0.010177 | -0.0030312 | 0.0062186 | -0.032333 | -0.029054 | -0.019105 | 0.032698 | 0.029326 | 0.019234 | 107.3028 | -36.344 | -132.0717 | -72.6972 | 143.656 | 47.9283 | 1.086 | 1.0844 | 1.0812 | 1.0989 | 1.094 | 1.0888 | 0.12554 | -120.1223 | 120.0737 | 0.014424 | -120.4428 | 120.0116
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8677e-10 | 2.7389e-10 | 2.4702e-10 | -2.8677e-10 | -2.7389e-10 | -2.4702e-10 | -1.8323e-11 | 1.7824e-11 | -1.0703e-11 | 1.8323e-11 | -1.7824e-11 | 1.0703e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.086 | 1.0844 | 1.0812 | 1.086 | 1.0844 | 1.0812 | 0.12554 | -120.1223 | 120.0737 | 0.12554 | -120.1223 | 120.0737
Line4_2_6 | 0.11916 | 0.12006 | 0.12197 | 0.11916 | 0.12006 | 0.12197 | 0.027519 | 0.027727 | 0.028168 | 0.027519 | 0.027727 | 0.028168 | -0.0018698 | -0.0026977 | -0.0020913 | 0.0020118 | 0.0028418 | 0.0022401 | -0.030119 | -0.030247 | -0.03069 | 0.030403 | 0.030536 | 0.030987 | 93.44 | -25.2506 | -146.2691 | -86.56 | 154.7494 | 33.7309 | 1.0966 | 1.0952 | 1.092 | 1.1072 | 1.1061 | 1.103 | -0.11242 | -120.3471 | 119.8325 | -0.34582 | -120.5675 | 119.596
Line5_6_7 | 0.11916 | 0.12006 | 0.12197 | 0.11916 | 0.12006 | 0.12197 | 0.027519 | 0.027727 | 0.028168 | 0.027519 | 0.027727 | 0.028168 | -0.0020118 | -0.0028418 | -0.0022401 | 0.0021538 | 0.0029859 | 0.0023889 | -0.030403 | -0.030536 | -0.030987 | 0.030687 | 0.030824 | 0.031285 | 93.44 | -25.2506 | -146.2691 | -86.56 | 154.7494 | 33.7309 | 1.1072 | 1.1061 | 1.103 | 1.1179 | 1.1169 | 1.1139 | -0.34582 | -120.5675 | 119.596 | -0.57478 | -120.7836 | 119.3643
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3549e-10 | 8.2335e-10 | 7.8344e-10 | -8.3549e-10 | -8.2335e-10 | -7.8344e-10 | 1.2952e-10 | 1.7642e-10 | 1.4275e-10 | -1.2952e-10 | -1.7642e-10 | -1.4275e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.1169 | 1.1139 | 1.1179 | 1.1169 | 1.1139 | -0.57478 | -120.7836 | 119.3643 | -0.57478 | -120.7836 | 119.3643
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.785e-10 | 2.7445e-10 | 2.6115e-10 | -2.785e-10 | -2.7445e-10 | -2.6115e-10 | 4.3175e-11 | 5.8808e-11 | 4.7582e-11 | -4.3175e-11 | -5.8808e-11 | -4.7582e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.1169 | 1.1139 | 1.1179 | 1.1169 | 1.1139 | -0.57478 | -120.7836 | 119.3643 | -0.57478 | -120.7836 | 119.3643
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.785e-10 | 2.7445e-10 | 2.6115e-10 | -2.785e-10 | -2.7445e-10 | -2.6115e-10 | 4.3175e-11 | 5.8808e-11 | 4.7582e-11 | -4.3175e-11 | -5.8808e-11 | -4.7582e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1179 | 1.1169 | 1.1139 | 1.1179 | 1.1169 | 1.1139 | -0.57478 | -120.7836 | 119.3643 | -0.57478 | -120.7836 | 119.3643
Line9_3_11 | 0.10623 | 0.10694 | 0.10875 | 0.10623 | 0.10694 | 0.10875 | 0.024533 | 0.024698 | 0.025115 | 0.024533 | 0.024698 | 0.025115 | -0.0015671 | -0.0023199 | -0.001791 | 0.00168 | 0.0024342 | 0.0019093 | -0.026829 | -0.026921 | -0.027338 | 0.027055 | 0.027149 | 0.027575 | 93.2544 | -25.3988 | -146.3945 | -86.7456 | 154.6012 | 33.6055 | 1.0955 | 1.0941 | 1.0909 | 1.1049 | 1.1037 | 1.1006 | -0.08843 | -120.324 | 119.8573 | -0.29874 | -120.5223 | 119.6447

## LL_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11999 | 0.12096 | 0.12297 | 0.11999 | 0.12096 | 0.12297 | 0.027711 | 0.027934 | 0.028398 | 0.027711 | 0.027934 | 0.028398 | -0.0018547 | -0.0027674 | -0.0020891 | 0.0019987 | 0.0029137 | 0.0022403 | -0.03148 | -0.031619 | -0.032096 | 0.031768 | 0.031912 | 0.032399 | 93.4956 | -25.1341 | -146.2064 | -86.5044 | 154.8659 | 33.7936 | 1.138 | 1.1362 | 1.1326 | 1.1486 | 1.1471 | 1.1436 | 0.12371 | -120.136 | 120.0696 | -0.10453 | -120.351 | 119.838
Line10_11_12 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0018008 | -0.0026377 | -0.0020514 | 0.0019162 | 0.0027547 | 0.0021726 | -0.028646 | -0.028754 | -0.029224 | 0.028877 | 0.028988 | 0.029466 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.1571 | 1.1557 | 1.1523 | 1.1667 | 1.1655 | 1.1621 | -0.28496 | -120.5202 | 119.656 | -0.48427 | -120.7074 | 119.4545
Line11_12_13 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0019162 | -0.0027547 | -0.0021726 | 0.0020316 | 0.0028718 | 0.0022938 | -0.028877 | -0.028988 | -0.029466 | 0.029108 | 0.029222 | 0.029708 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.1667 | 1.1655 | 1.1621 | 1.1763 | 1.1753 | 1.172 | -0.48427 | -120.7074 | 119.4545 | -0.68033 | -120.8916 | 119.2563
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8776e-10 | 9.7474e-10 | 9.2953e-10 | -9.8776e-10 | -9.7474e-10 | -9.2953e-10 | 1.69e-10 | 2.2128e-10 | 1.8406e-10 | -1.69e-10 | -2.2128e-10 | -1.8406e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1763 | 1.1753 | 1.172 | 1.1763 | 1.1753 | 1.172 | -0.68033 | -120.8916 | 119.2563 | -0.68033 | -120.8916 | 119.2563
Line13_13_14 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0020316 | -0.0028718 | -0.0022938 | 0.002147 | 0.0029888 | 0.002415 | -0.029108 | -0.029222 | -0.029708 | 0.029338 | 0.029456 | 0.029951 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.1763 | 1.1753 | 1.172 | 1.1859 | 1.1851 | 1.1819 | -0.68033 | -120.8916 | 119.2563 | -0.87321 | -121.0727 | 119.0615
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.585e-10 | 6.4983e-10 | 6.1968e-10 | -6.585e-10 | -6.4983e-10 | -6.1968e-10 | 1.1266e-10 | 1.4752e-10 | 1.2271e-10 | -1.1266e-10 | -1.4752e-10 | -1.2271e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1763 | 1.1753 | 1.172 | 1.1763 | 1.1753 | 1.172 | -0.68033 | -120.8916 | 119.2563 | -0.68033 | -120.8916 | 119.2563
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2925e-10 | 3.2491e-10 | 3.0984e-10 | -3.2925e-10 | -3.2491e-10 | -3.0984e-10 | 5.6332e-11 | 7.3759e-11 | 6.1353e-11 | -5.6332e-11 | -7.3759e-11 | -6.1353e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1763 | 1.1753 | 1.172 | 1.1763 | 1.1753 | 1.172 | -0.68033 | -120.8916 | 119.2563 | -0.68033 | -120.8916 | 119.2563
Line16_4_18 | 0 | 0.064112 | 0.064112 | 0 | 0.064112 | 0.064112 | 0 | 0.014806 | 0.014806 | 0 | 0.014806 | 0.014806 | 2.1466e-10 | 0.016387 | 0.0042473 | -2.1466e-10 | -0.016346 | -0.0042062 | -1.1898e-12 | 0.0043792 | 0.016337 | 1.1898e-12 | -0.0042969 | -0.016255 | 0 | -135.4167 | 44.5833 | 0 | 44.5833 | -135.4167 | 1.1509 | 1.1456 | 1.1401 | 1.1509 | 1.1415 | 1.134 | 0.014686 | -120.4547 | 120.0101 | 0.014686 | -120.688 | 120.0753
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.584e-10 | 1.5097e-10 | 1.3552e-10 | -1.584e-10 | -1.5097e-10 | -1.3552e-10 | -9.9101e-12 | 1.0879e-11 | -5.547e-12 | 9.9101e-12 | -1.0879e-11 | 5.547e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.138 | 1.1362 | 1.1326 | 1.138 | 1.1362 | 1.1326 | 0.12371 | -120.136 | 120.0696 | 0.12371 | -120.136 | 120.0696
Line1_1_3 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0015701 | -0.0024036 | -0.001809 | 0.0016855 | 0.0025207 | 0.0019302 | -0.028185 | -0.028286 | -0.028739 | 0.028415 | 0.02852 | 0.028981 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.138 | 1.1362 | 1.1326 | 1.1475 | 1.146 | 1.1425 | 0.12371 | -120.136 | 120.0696 | -0.082328 | -120.3297 | 119.861
Line2_1_4 | 0.1352 | 0.11679 | 0.077932 | 0.1352 | 0.11679 | 0.077932 | 0.031223 | 0.026972 | 0.017998 | 0.031223 | 0.026972 | 0.017998 | -0.010349 | 0.0041229 | -0.006144 | 0.010532 | -0.0039865 | 0.0062047 | -0.03399 | -0.030368 | -0.019437 | 0.034355 | 0.03064 | 0.019558 | 107.0584 | -37.8676 | -132.3885 | -72.9416 | 142.1324 | 47.6115 | 1.138 | 1.1362 | 1.1326 | 1.1509 | 1.1456 | 1.1401 | 0.12371 | -120.136 | 120.0696 | 0.014686 | -120.4547 | 120.0101
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.168e-10 | 3.0194e-10 | 2.7104e-10 | -3.168e-10 | -3.0194e-10 | -2.7104e-10 | -1.982e-11 | 2.1759e-11 | -1.1094e-11 | 1.982e-11 | -2.1759e-11 | 1.1094e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.138 | 1.1362 | 1.1326 | 1.138 | 1.1362 | 1.1326 | 0.12371 | -120.136 | 120.0696 | 0.12371 | -120.136 | 120.0696
Line4_2_6 | 0.11999 | 0.12096 | 0.12297 | 0.11999 | 0.12096 | 0.12297 | 0.027711 | 0.027934 | 0.028398 | 0.027711 | 0.027934 | 0.028398 | -0.0019987 | -0.0029137 | -0.0022403 | 0.0021427 | 0.00306 | 0.0023915 | -0.031768 | -0.031912 | -0.032399 | 0.032055 | 0.032204 | 0.032701 | 93.4956 | -25.1341 | -146.2064 | -86.5044 | 154.8659 | 33.7936 | 1.1486 | 1.1471 | 1.1436 | 1.1594 | 1.1581 | 1.1546 | -0.10453 | -120.351 | 119.838 | -0.32855 | -120.5619 | 119.6109
Line5_6_7 | 0.11999 | 0.12096 | 0.12297 | 0.11999 | 0.12096 | 0.12297 | 0.027711 | 0.027934 | 0.028398 | 0.027711 | 0.027934 | 0.028398 | -0.0021427 | -0.00306 | -0.0023915 | 0.0022867 | 0.0032063 | 0.0025427 | -0.032055 | -0.032204 | -0.032701 | 0.032343 | 0.032497 | 0.033003 | 93.4956 | -25.1341 | -146.2064 | -86.5044 | 154.8659 | 33.7936 | 1.1594 | 1.1581 | 1.1546 | 1.1701 | 1.169 | 1.1656 | -0.32855 | -120.5619 | 119.6109 | -0.54848 | -120.7689 | 119.388
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0263e-10 | 8.883e-10 | 8.4233e-10 | -9.0263e-10 | -8.883e-10 | -8.4233e-10 | 1.3553e-10 | 1.8983e-10 | 1.5064e-10 | -1.3553e-10 | -1.8983e-10 | -1.5064e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1701 | 1.169 | 1.1656 | 1.1701 | 1.169 | 1.1656 | -0.54848 | -120.7689 | 119.388 | -0.54848 | -120.7689 | 119.388
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0088e-10 | 2.961e-10 | 2.8078e-10 | -3.0088e-10 | -2.961e-10 | -2.8078e-10 | 4.5176e-11 | 6.3275e-11 | 5.0214e-11 | -4.5176e-11 | -6.3275e-11 | -5.0214e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1701 | 1.169 | 1.1656 | 1.1701 | 1.169 | 1.1656 | -0.54848 | -120.7689 | 119.388 | -0.54848 | -120.7689 | 119.388
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0088e-10 | 2.961e-10 | 2.8078e-10 | -3.0088e-10 | -2.961e-10 | -2.8078e-10 | 4.5176e-11 | 6.3275e-11 | 5.0214e-11 | -4.5176e-11 | -6.3275e-11 | -5.0214e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1701 | 1.169 | 1.1656 | 1.1701 | 1.169 | 1.1656 | -0.54848 | -120.7689 | 119.388 | -0.54848 | -120.7689 | 119.388
Line9_3_11 | 0.10741 | 0.10818 | 0.11009 | 0.10741 | 0.10818 | 0.11009 | 0.024806 | 0.024984 | 0.025424 | 0.024806 | 0.024984 | 0.025424 | -0.0016855 | -0.0025207 | -0.0019302 | 0.0018008 | 0.0026377 | 0.0020514 | -0.028415 | -0.02852 | -0.028981 | 0.028646 | 0.028754 | 0.029224 | 93.3122 | -25.2789 | -146.3286 | -86.6878 | 154.7211 | 33.6714 | 1.1475 | 1.146 | 1.1425 | 1.1571 | 1.1557 | 1.1523 | -0.082328 | -120.3297 | 119.861 | -0.28496 | -120.5202 | 119.656

## LL_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00073134 | 0.0043194 | 0.0036537 | 0.00073134 | 0.0043194 | 0.0036537 | 0.0001689 | 0.00099752 | 0.00084379 | 0.0001689 | 0.00099752 | 0.00084379 | -0.00015686 | -0.00082368 | -8.0449e-05 | 0.00015687 | 0.00082404 | 8.0705e-05 | 3.3794e-05 | -0.00014813 | -0.00057528 | -3.3783e-05 | 0.00014851 | 0.00057555 | -167.8235 | 34.5522 | -141.0778 | 12.1765 | -145.4478 | 38.9222 | 0.95002 | 0.83898 | 0.68841 | 0.95006 | 0.8394 | 0.68877 | 0.018327 | -135.2526 | 120.9615 | 0.022833 | -135.2318 | 120.9401
Line10_11_12 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.00015579 | -0.00082213 | -8.1681e-05 | 0.0001558 | 0.00082249 | 8.1936e-05 | 3.422e-05 | -0.00014656 | -0.00057406 | -3.4209e-05 | 0.00014693 | 0.00057433 | -167.5846 | 34.6813 | -140.983 | 12.4154 | -145.3187 | 39.017 | 0.95011 | 0.83981 | 0.68912 | 0.95015 | 0.84023 | 0.68948 | 0.027308 | -135.211 | 120.919 | 0.031798 | -135.1903 | 120.8977
Line11_12_13 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.0001558 | -0.00082249 | -8.1935e-05 | 0.00015581 | 0.00082284 | 8.219e-05 | 3.4209e-05 | -0.00014693 | -0.00057432 | -3.4198e-05 | 0.0001473 | 0.00057459 | -167.5846 | 34.6812 | -140.9831 | 12.4154 | -145.3188 | 39.0169 | 0.95015 | 0.84023 | 0.68948 | 0.9502 | 0.84065 | 0.68983 | 0.031798 | -135.1903 | 120.8977 | 0.036287 | -135.1696 | 120.8765
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0919e-12 | -7.0508e-10 | -1.9734e-09 | -2.0919e-12 | 7.0508e-10 | 1.9734e-09 | -6.2887e-12 | 2.2988e-09 | -1.1028e-10 | 6.2887e-12 | -2.2988e-09 | 1.1028e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9502 | 0.84065 | 0.68983 | 0.9502 | 0.84065 | 0.68983 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line13_13_14 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.00015581 | -0.00082284 | -8.2187e-05 | 0.00015582 | 0.0008232 | 8.2442e-05 | 3.4198e-05 | -0.0001473 | -0.00057459 | -3.4188e-05 | 0.00014767 | 0.00057486 | -167.5846 | 34.681 | -140.9833 | 12.4154 | -145.319 | 39.0167 | 0.9502 | 0.84065 | 0.68983 | 0.95025 | 0.84107 | 0.69019 | 0.036287 | -135.1696 | 120.8765 | 0.040776 | -135.1488 | 120.8553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3946e-12 | -4.7005e-10 | -1.3156e-09 | -1.3946e-12 | 4.7005e-10 | 1.3156e-09 | -4.1924e-12 | 1.5325e-09 | -7.3518e-11 | 4.1924e-12 | -1.5325e-09 | 7.3518e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9502 | 0.84065 | 0.68983 | 0.9502 | 0.84065 | 0.68983 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9728e-13 | -2.3503e-10 | -6.5778e-10 | -6.9728e-13 | 2.3503e-10 | 6.5778e-10 | -2.0962e-12 | 7.6626e-10 | -3.6759e-11 | 2.0962e-12 | -7.6626e-10 | 3.6759e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9502 | 0.84065 | 0.68983 | 0.9502 | 0.84065 | 0.68983 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line16_4_18 | 0 | 2.5141 | 2.5141 | 0 | 2.5141 | 2.5141 | 0 | 0.58062 | 0.58062 | 0 | 0.58062 | 0.58062 | 5.6288e-13 | 0.35474 | -0.11202 | -5.6281e-13 | -0.23338 | 0.23338 | -1.4359e-12 | -0.020622 | 0.27346 | 1.4359e-12 | 0.14704 | -0.14704 | 0 | -147.7624 | 32.2376 | 0 | 32.2376 | -147.7624 | 0.95016 | 0.61201 | 0.50896 | 0.95016 | 0.47508 | 0.47508 | 0.024856 | -151.0894 | 144.5135 | 0.024856 | -179.9751 | -179.9751
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2313e-14 | -2.3859e-10 | -6.5996e-10 | -6.2313e-14 | 2.3859e-10 | 6.5996e-10 | -1.0585e-12 | 7.6882e-10 | -4.0238e-11 | 1.0585e-12 | -7.6882e-10 | 4.0238e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95002 | 0.83898 | 0.68841 | 0.95002 | 0.83898 | 0.68841 | 0.018327 | -135.2526 | 120.9615 | 0.018327 | -135.2526 | 120.9615
Line1_1_3 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.00015577 | -0.00082142 | -8.1172e-05 | 0.00015578 | 0.00082178 | 8.1427e-05 | 3.4241e-05 | -0.00014581 | -0.00057353 | -3.423e-05 | 0.00014619 | 0.00057379 | -167.5846 | 34.6814 | -140.9829 | 12.4154 | -145.3186 | 39.0171 | 0.95002 | 0.83898 | 0.68841 | 0.95006 | 0.8394 | 0.68877 | 0.018327 | -135.2526 | 120.9615 | 0.022818 | -135.2318 | 120.9402
Line2_1_4 | 0.0014981 | 2.5058 | 2.5069 | 0.0014981 | 2.5058 | 2.5069 | 0.00034597 | 0.57869 | 0.57895 | 0.00034597 | 0.57869 | 0.57895 | -0.00032449 | 0.4741 | 0.0091695 | 0.00032454 | -0.35354 | 0.1115 | -5.2275e-05 | 0.10463 | 0.39845 | 5.232e-05 | 0.020954 | -0.27276 | 170.8668 | -147.6976 | 32.2798 | -9.1332 | 32.3024 | -147.7202 | 0.95002 | 0.83898 | 0.68841 | 0.95016 | 0.61201 | 0.50896 | 0.018327 | -135.2526 | 120.9615 | 0.024856 | -151.0894 | 144.5135
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2469e-13 | -4.7718e-10 | -1.3199e-09 | -1.2471e-13 | 4.7718e-10 | 1.3199e-09 | -2.117e-12 | 1.5376e-09 | -8.0477e-11 | 2.117e-12 | -1.5376e-09 | 8.0477e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95002 | 0.83898 | 0.68841 | 0.95002 | 0.83898 | 0.68841 | 0.018327 | -135.2526 | 120.9615 | 0.018327 | -135.2526 | 120.9615
Line4_2_6 | 0.00073134 | 0.0043194 | 0.0036537 | 0.00073134 | 0.0043194 | 0.0036537 | 0.0001689 | 0.00099752 | 0.00084379 | 0.0001689 | 0.00099752 | 0.00084379 | -0.00015687 | -0.00082404 | -8.0704e-05 | 0.00015688 | 0.0008244 | 8.0961e-05 | 3.3783e-05 | -0.00014851 | -0.00057555 | -3.3772e-05 | 0.00014888 | 0.00057581 | -167.8235 | 34.5522 | -141.0778 | 12.1765 | -145.4478 | 38.9222 | 0.95006 | 0.8394 | 0.68877 | 0.95011 | 0.83982 | 0.68912 | 0.022833 | -135.2318 | 120.9401 | 0.027339 | -135.211 | 120.9187
Line5_6_7 | 0.00073134 | 0.0043194 | 0.0036537 | 0.00073134 | 0.0043194 | 0.0036537 | 0.0001689 | 0.00099752 | 0.00084379 | 0.0001689 | 0.00099752 | 0.00084379 | -0.00015688 | -0.0008244 | -8.096e-05 | 0.00015689 | 0.00082476 | 8.1216e-05 | 3.3772e-05 | -0.00014888 | -0.00057581 | -3.3762e-05 | 0.00014925 | 0.00057608 | -167.8235 | 34.5521 | -141.0779 | 12.1765 | -145.4479 | 38.9221 | 0.95011 | 0.83982 | 0.68912 | 0.95016 | 0.84024 | 0.68948 | 0.027339 | -135.211 | 120.9187 | 0.031844 | -135.1903 | 120.8974
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6338e-12 | -7.0771e-10 | -1.975e-09 | -1.6338e-12 | 7.0771e-10 | 1.975e-09 | -5.5183e-12 | 2.3007e-09 | -1.1285e-10 | 5.5183e-12 | -2.3007e-09 | 1.1285e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95016 | 0.84024 | 0.68948 | 0.95016 | 0.84024 | 0.68948 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4465e-13 | -2.359e-10 | -6.5833e-10 | -5.4462e-13 | 2.359e-10 | 6.5833e-10 | -1.8395e-12 | 7.669e-10 | -3.7615e-11 | 1.8395e-12 | -7.669e-10 | 3.7615e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95016 | 0.84024 | 0.68948 | 0.95016 | 0.84024 | 0.68948 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4458e-13 | -2.359e-10 | -6.5833e-10 | -5.4458e-13 | 2.359e-10 | 6.5833e-10 | -1.8395e-12 | 7.669e-10 | -3.7615e-11 | 1.8394e-12 | -7.669e-10 | 3.7615e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95016 | 0.84024 | 0.68948 | 0.95016 | 0.84024 | 0.68948 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line9_3_11 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00072696 | 0.0043058 | 0.0036435 | 0.00016788 | 0.00099438 | 0.00084142 | 0.00016788 | 0.00099438 | 0.00084142 | -0.00015578 | -0.00082178 | -8.1427e-05 | 0.00015579 | 0.00082213 | 8.1681e-05 | 3.423e-05 | -0.00014619 | -0.00057379 | -3.422e-05 | 0.00014656 | 0.00057406 | -167.5846 | 34.6813 | -140.9829 | 12.4154 | -145.3187 | 39.0171 | 0.95006 | 0.8394 | 0.68877 | 0.95011 | 0.83981 | 0.68912 | 0.022818 | -135.2318 | 120.9402 | 0.027308 | -135.211 | 120.919

## LL_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00016001 | 0.00094502 | 0.00079938 | 0.00016001 | 0.00094502 | 0.00079938 | -0.00014078 | -0.00073926 | -7.2203e-05 | 0.00014079 | 0.00073958 | 7.2433e-05 | 3.033e-05 | -0.00013295 | -0.00051632 | -3.032e-05 | 0.00013329 | 0.00051656 | -167.8235 | 34.5522 | -141.0778 | 12.1765 | -145.4478 | 38.9222 | 0.90002 | 0.79482 | 0.65218 | 0.90006 | 0.79522 | 0.65252 | 0.018327 | -135.2526 | 120.9615 | 0.022833 | -135.2318 | 120.9401
Line10_11_12 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013983 | -0.00073787 | -7.3309e-05 | 0.00013984 | 0.00073819 | 7.3538e-05 | 3.0712e-05 | -0.00013154 | -0.00051522 | -3.0703e-05 | 0.00013187 | 0.00051546 | -167.5846 | 34.6813 | -140.983 | 12.4154 | -145.3187 | 39.017 | 0.9001 | 0.79561 | 0.65285 | 0.90015 | 0.79601 | 0.65319 | 0.027308 | -135.211 | 120.919 | 0.031798 | -135.1903 | 120.8977
Line11_12_13 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013984 | -0.00073819 | -7.3537e-05 | 0.00013984 | 0.00073851 | 7.3766e-05 | 3.0703e-05 | -0.00013187 | -0.00051546 | -3.0693e-05 | 0.0001322 | 0.0005157 | -167.5846 | 34.6812 | -140.9831 | 12.4154 | -145.3188 | 39.0169 | 0.90015 | 0.79601 | 0.65319 | 0.90019 | 0.7964 | 0.65352 | 0.031798 | -135.1903 | 120.8977 | 0.036287 | -135.1696 | 120.8765
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8775e-12 | -6.3282e-10 | -1.7711e-09 | -1.8775e-12 | 6.3282e-10 | 1.7711e-09 | -5.6441e-12 | 2.0632e-09 | -9.8974e-11 | 5.6441e-12 | -2.0632e-09 | 9.8974e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90019 | 0.7964 | 0.65352 | 0.90019 | 0.7964 | 0.65352 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line13_13_14 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013984 | -0.00073851 | -7.3764e-05 | 0.00013985 | 0.00073883 | 7.3992e-05 | 3.0693e-05 | -0.00013221 | -0.0005157 | -3.0684e-05 | 0.00013254 | 0.00051594 | -167.5846 | 34.681 | -140.9833 | 12.4154 | -145.319 | 39.0167 | 0.90019 | 0.7964 | 0.65352 | 0.90023 | 0.7968 | 0.65386 | 0.036287 | -135.1696 | 120.8765 | 0.040776 | -135.1488 | 120.8553
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2516e-12 | -4.2188e-10 | -1.1807e-09 | -1.2516e-12 | 4.2188e-10 | 1.1807e-09 | -3.7627e-12 | 1.3754e-09 | -6.5983e-11 | 3.7627e-12 | -1.3754e-09 | 6.5983e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90019 | 0.7964 | 0.65352 | 0.90019 | 0.7964 | 0.65352 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2582e-13 | -2.1094e-10 | -5.9037e-10 | -6.2585e-13 | 2.1094e-10 | 5.9037e-10 | -1.8814e-12 | 6.8772e-10 | -3.2991e-11 | 1.8814e-12 | -6.8772e-10 | 3.2991e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90019 | 0.7964 | 0.65352 | 0.90019 | 0.7964 | 0.65352 | 0.036287 | -135.1696 | 120.8765 | 0.036287 | -135.1696 | 120.8765
Line16_4_18 | 0 | 2.3818 | 2.3818 | 0 | 2.3818 | 2.3818 | 0 | 0.55006 | 0.55006 | 0 | 0.55006 | 0.55006 | 5.0511e-13 | 0.31838 | -0.10054 | -5.0511e-13 | -0.20946 | 0.20946 | -1.2886e-12 | -0.018508 | 0.24543 | 1.2886e-12 | 0.13197 | -0.13197 | 0 | -147.7624 | 32.2376 | 0 | 32.2376 | -147.7624 | 0.90015 | 0.5798 | 0.48218 | 0.90015 | 0.45008 | 0.45008 | 0.024856 | -151.0894 | 144.5135 | 0.024856 | -179.9751 | -179.9751
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5935e-14 | -2.1414e-10 | -5.9232e-10 | -5.5935e-14 | 2.1414e-10 | 5.9232e-10 | -9.5001e-13 | 6.9002e-10 | -3.6114e-11 | 9.4999e-13 | -6.9002e-10 | 3.6114e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90002 | 0.79482 | 0.65218 | 0.90002 | 0.79482 | 0.65218 | 0.018327 | -135.2526 | 120.9615 | 0.018327 | -135.2526 | 120.9615
Line1_1_3 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013981 | -0.00073723 | -7.2853e-05 | 0.00013982 | 0.00073755 | 7.3082e-05 | 3.0731e-05 | -0.00013087 | -0.00051475 | -3.0722e-05 | 0.0001312 | 0.00051498 | -167.5846 | 34.6814 | -140.9829 | 12.4154 | -145.3186 | 39.0171 | 0.90002 | 0.79482 | 0.65218 | 0.90006 | 0.79522 | 0.65252 | 0.018327 | -135.2526 | 120.9615 | 0.022818 | -135.2318 | 120.9402
Line2_1_4 | 0.0014192 | 2.3739 | 2.375 | 0.0014192 | 2.3739 | 2.375 | 0.00032776 | 0.54824 | 0.54848 | 0.00032776 | 0.54824 | 0.54848 | -0.00029123 | 0.42551 | 0.0082297 | 0.00029127 | -0.31731 | 0.10007 | -4.6917e-05 | 0.093905 | 0.35761 | 4.6957e-05 | 0.018806 | -0.2448 | 170.8668 | -147.6976 | 32.2798 | -9.1332 | 32.3024 | -147.7202 | 0.90002 | 0.79482 | 0.65218 | 0.90015 | 0.5798 | 0.48218 | 0.018327 | -135.2526 | 120.9615 | 0.024856 | -151.0894 | 144.5135
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1192e-13 | -4.2827e-10 | -1.1846e-09 | -1.1191e-13 | 4.2827e-10 | 1.1846e-09 | -1.9e-12 | 1.38e-09 | -7.2228e-11 | 1.9e-12 | -1.38e-09 | 7.2228e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90002 | 0.79482 | 0.65218 | 0.90002 | 0.79482 | 0.65218 | 0.018327 | -135.2526 | 120.9615 | 0.018327 | -135.2526 | 120.9615
Line4_2_6 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00016001 | 0.00094502 | 0.00079938 | 0.00016001 | 0.00094502 | 0.00079938 | -0.00014079 | -0.00073958 | -7.2433e-05 | 0.0001408 | 0.0007399 | 7.2663e-05 | 3.032e-05 | -0.00013329 | -0.00051656 | -3.0311e-05 | 0.00013362 | 0.0005168 | -167.8235 | 34.5522 | -141.0778 | 12.1765 | -145.4478 | 38.9222 | 0.90006 | 0.79522 | 0.65252 | 0.9001 | 0.79562 | 0.65285 | 0.022833 | -135.2318 | 120.9401 | 0.027339 | -135.211 | 120.9187
Line5_6_7 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00069285 | 0.0040921 | 0.0034614 | 0.00016001 | 0.00094502 | 0.00079938 | 0.00016001 | 0.00094502 | 0.00079938 | -0.0001408 | -0.0007399 | -7.2662e-05 | 0.00014081 | 0.00074023 | 7.2892e-05 | 3.0311e-05 | -0.00013362 | -0.0005168 | -3.0301e-05 | 0.00013396 | 0.00051704 | -167.8235 | 34.5521 | -141.0779 | 12.1765 | -145.4479 | 38.9221 | 0.9001 | 0.79562 | 0.65285 | 0.90015 | 0.79601 | 0.65319 | 0.027339 | -135.211 | 120.9187 | 0.031844 | -135.1903 | 120.8974
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4664e-12 | -6.3518e-10 | -1.7726e-09 | -1.4664e-12 | 6.3518e-10 | 1.7726e-09 | -4.9528e-12 | 2.0649e-09 | -1.0128e-10 | 4.9528e-12 | -2.0649e-09 | 1.0128e-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90015 | 0.79601 | 0.65319 | 0.90015 | 0.79601 | 0.65319 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8877e-13 | -2.1173e-10 | -5.9085e-10 | -4.8877e-13 | 2.1173e-10 | 5.9085e-10 | -1.6509e-12 | 6.883e-10 | -3.376e-11 | 1.651e-12 | -6.883e-10 | 3.376e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90015 | 0.79601 | 0.65319 | 0.90015 | 0.79601 | 0.65319 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8877e-13 | -2.1173e-10 | -5.9085e-10 | -4.8876e-13 | 2.1173e-10 | 5.9085e-10 | -1.651e-12 | 6.883e-10 | -3.376e-11 | 1.6509e-12 | -6.883e-10 | 3.376e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90015 | 0.79601 | 0.65319 | 0.90015 | 0.79601 | 0.65319 | 0.031844 | -135.1903 | 120.8974 | 0.031844 | -135.1903 | 120.8974
Line9_3_11 | 0.0006887 | 0.0040792 | 0.0034517 | 0.0006887 | 0.0040792 | 0.0034517 | 0.00015905 | 0.00094204 | 0.00079714 | 0.00015905 | 0.00094204 | 0.00079714 | -0.00013982 | -0.00073755 | -7.3081e-05 | 0.00013983 | 0.00073787 | 7.331e-05 | 3.0722e-05 | -0.0001312 | -0.00051498 | -3.0712e-05 | 0.00013154 | 0.00051522 | -167.5846 | 34.6813 | -140.9829 | 12.4154 | -145.3187 | 39.0171 | 0.90006 | 0.79522 | 0.65252 | 0.9001 | 0.79561 | 0.65285 | 0.022818 | -135.2318 | 120.9402 | 0.027308 | -135.211 | 120.919

## LL_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | -3.0529e-06 | -1.9323e-05 | -6.1103e-06 | 3.0529e-06 | 1.9324e-05 | 6.1104e-06 | 1.4025e-06 | -4.3332e-06 | -1.553e-05 | -1.4024e-06 | 4.3334e-06 | 1.553e-05 | -155.3261 | 47.0496 | -128.5804 | 24.6739 | -132.9504 | 51.4196 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94815 | 0.94461 | 0.00037951 | -120.3111 | 119.9424 | 0.00048425 | -120.3108 | 119.9422
Line10_11_12 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9273e-05 | -6.119e-06 | 3.0287e-06 | 1.9273e-05 | 6.1191e-06 | 1.4067e-06 | -4.2765e-06 | -1.5477e-05 | -1.4067e-06 | 4.2766e-06 | 1.5477e-05 | -155.0872 | 47.1786 | -128.4856 | 24.9128 | -132.8214 | 51.5144 | 0.95 | 0.94816 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00058802 | -120.3104 | 119.942 | 0.00069228 | -120.3101 | 119.9418
Line11_12_13 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9273e-05 | -6.1191e-06 | 3.0287e-06 | 1.9273e-05 | 6.1192e-06 | 1.4067e-06 | -4.2767e-06 | -1.5477e-05 | -1.4067e-06 | 4.2768e-06 | 1.5477e-05 | -155.0872 | 47.1786 | -128.4857 | 24.9128 | -132.8214 | 51.5143 | 0.95 | 0.94817 | 0.94462 | 0.95 | 0.94818 | 0.94463 | 0.00069228 | -120.3101 | 119.9418 | 0.00079653 | -120.3097 | 119.9416
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4181e-14 | -1.8875e-11 | -5.5767e-11 | -1.4181e-14 | 1.8875e-11 | 5.5767e-11 | -1.3801e-13 | 5.3557e-11 | 1.0068e-11 | 1.3801e-13 | -5.3557e-11 | -1.0068e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94818 | 0.94463 | 0.95 | 0.94818 | 0.94463 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line13_13_14 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9273e-05 | -6.1191e-06 | 3.0287e-06 | 1.9273e-05 | 6.1192e-06 | 1.4067e-06 | -4.2769e-06 | -1.5477e-05 | -1.4067e-06 | 4.2771e-06 | 1.5477e-05 | -155.0872 | 47.1784 | -128.4859 | 24.9128 | -132.8216 | 51.5141 | 0.95 | 0.94818 | 0.94463 | 0.95 | 0.94819 | 0.94464 | 0.00079653 | -120.3097 | 119.9416 | 0.00090079 | -120.3093 | 119.9414
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4534e-15 | -1.2584e-11 | -3.7178e-11 | -9.4534e-15 | 1.2584e-11 | 3.7178e-11 | -9.2007e-14 | 3.5704e-11 | 6.7121e-12 | 9.2008e-14 | -3.5704e-11 | -6.7121e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94818 | 0.94463 | 0.95 | 0.94818 | 0.94463 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7264e-15 | -6.2918e-12 | -1.8589e-11 | -4.7264e-15 | 6.2918e-12 | 1.8589e-11 | -4.6004e-14 | 1.7852e-11 | 3.356e-12 | 4.6004e-14 | -1.7852e-11 | -3.356e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94818 | 0.94463 | 0.95 | 0.94818 | 0.94463 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line16_4_18 | 0 | 0.052642 | 0.052642 | 0 | 0.052642 | 0.052642 | 0 | 0.012157 | 0.012157 | 0 | 0.012157 | 0.012157 | 4.9838e-15 | 0.011083 | 0.002879 | -4.9838e-15 | -0.01103 | -0.0028258 | -3.1896e-14 | 0.0029191 | 0.011048 | 3.1896e-14 | -0.0028636 | -0.010992 | 0 | -135.265 | 44.735 | 0 | 44.735 | -135.265 | 0.95 | 0.94276 | 0.93909 | 0.95 | 0.93738 | 0.93358 | 0.0005523 | -120.5099 | 120.1288 | 0.0005523 | -120.7112 | 120.3181
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.5292e-15 | -6.4164e-12 | -1.8706e-11 | 3.5294e-15 | 6.4164e-12 | 1.8706e-11 | -2.1919e-14 | 1.7935e-11 | 3.3076e-12 | 2.1919e-14 | -1.7935e-11 | -3.3076e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94814 | 0.9446 | 0.00037951 | -120.3111 | 119.9424 | 0.00037951 | -120.3111 | 119.9424
Line1_1_3 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9272e-05 | -6.1188e-06 | 3.0287e-06 | 1.9272e-05 | 6.1189e-06 | 1.4067e-06 | -4.2761e-06 | -1.5476e-05 | -1.4067e-06 | 4.2763e-06 | 1.5476e-05 | -155.0872 | 47.1788 | -128.4855 | 24.9128 | -132.8212 | 51.5145 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94815 | 0.94461 | 0.00037951 | -120.3111 | 119.9424 | 0.00048377 | -120.3108 | 119.9422
Line2_1_4 | 3.1368e-05 | 0.052468 | 0.052491 | 3.1368e-05 | 0.052468 | 0.052491 | 7.244e-06 | 0.012117 | 0.012122 | 7.244e-06 | 0.012117 | 0.012122 | -6.87e-06 | 0.011103 | 0.0029318 | 6.87e-06 | -0.01105 | -0.0028789 | 4.038e-07 | 0.002952 | 0.011069 | -4.0378e-07 | -0.0028969 | -0.011014 | -176.6358 | -135.2002 | 44.7772 | 3.3642 | 44.7998 | -135.2228 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94276 | 0.93909 | 0.00037951 | -120.3111 | 119.9424 | 0.0005523 | -120.5099 | 120.1288
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.056e-15 | -1.2833e-11 | -3.7412e-11 | 7.0562e-15 | 1.2833e-11 | 3.7412e-11 | -4.3839e-14 | 3.587e-11 | 6.6152e-12 | 4.3839e-14 | -3.587e-11 | -6.6152e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94814 | 0.9446 | 0.95 | 0.94814 | 0.9446 | 0.00037951 | -120.3111 | 119.9424 | 0.00037951 | -120.3111 | 119.9424
Line4_2_6 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | -3.0529e-06 | -1.9324e-05 | -6.1104e-06 | 3.0529e-06 | 1.9324e-05 | 6.1105e-06 | 1.4024e-06 | -4.3334e-06 | -1.553e-05 | -1.4024e-06 | 4.3336e-06 | 1.553e-05 | -155.3261 | 47.0495 | -128.5804 | 24.6739 | -132.9505 | 51.4196 | 0.95 | 0.94815 | 0.94461 | 0.95 | 0.94816 | 0.94462 | 0.00048425 | -120.3108 | 119.9422 | 0.00058898 | -120.3104 | 119.942
Line5_6_7 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 1.5313e-05 | 9.0441e-05 | 7.6503e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | 3.5364e-06 | 2.0886e-05 | 1.7668e-05 | -3.0529e-06 | -1.9324e-05 | -6.1105e-06 | 3.0529e-06 | 1.9324e-05 | 6.1106e-06 | 1.4024e-06 | -4.3336e-06 | -1.553e-05 | -1.4024e-06 | 4.3337e-06 | 1.553e-05 | -155.3261 | 47.0495 | -128.5805 | 24.6739 | -132.9505 | 51.4195 | 0.95 | 0.94816 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00058898 | -120.3104 | 119.942 | 0.00069371 | -120.3101 | 119.9418
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3287e-15 | -1.8967e-11 | -5.5854e-11 | -8.3287e-15 | 1.8967e-11 | 5.5854e-11 | -1.2019e-13 | 5.3619e-11 | 1.0033e-11 | 1.2019e-13 | -5.3619e-11 | -1.0033e-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94817 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.776e-15 | -6.3225e-12 | -1.8618e-11 | -2.7759e-15 | 6.3225e-12 | 1.8618e-11 | -4.0066e-14 | 1.7873e-11 | 3.3442e-12 | 4.0066e-14 | -1.7873e-11 | -3.3442e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94817 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7756e-15 | -6.3225e-12 | -1.8618e-11 | -2.7756e-15 | 6.3225e-12 | 1.8618e-11 | -4.0066e-14 | 1.7873e-11 | 3.3442e-12 | 4.0066e-14 | -1.7873e-11 | -3.3442e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.94817 | 0.94462 | 0.95 | 0.94817 | 0.94462 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line9_3_11 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 1.5221e-05 | 9.0156e-05 | 7.6288e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | 3.5152e-06 | 2.0821e-05 | 1.7618e-05 | -3.0287e-06 | -1.9272e-05 | -6.1189e-06 | 3.0287e-06 | 1.9273e-05 | 6.119e-06 | 1.4067e-06 | -4.2763e-06 | -1.5476e-05 | -1.4067e-06 | 4.2765e-06 | 1.5477e-05 | -155.0872 | 47.1787 | -128.4856 | 24.9128 | -132.8213 | 51.5144 | 0.95 | 0.94815 | 0.94461 | 0.95 | 0.94816 | 0.94462 | 0.00048377 | -120.3108 | 119.9422 | 0.00058802 | -120.3104 | 119.942

## LL_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | -2.74e-06 | -1.7343e-05 | -5.4841e-06 | 2.74e-06 | 1.7343e-05 | 5.4842e-06 | 1.2587e-06 | -3.8891e-06 | -1.3938e-05 | -1.2587e-06 | 3.8892e-06 | 1.3938e-05 | -155.3261 | 47.0496 | -128.5804 | 24.6739 | -132.9504 | 51.4196 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89825 | 0.89489 | 0.00037951 | -120.3111 | 119.9424 | 0.00048425 | -120.3108 | 119.9422
Line10_11_12 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7297e-05 | -5.4918e-06 | 2.7183e-06 | 1.7297e-05 | 5.4919e-06 | 1.2625e-06 | -3.8382e-06 | -1.389e-05 | -1.2625e-06 | 3.8383e-06 | 1.389e-05 | -155.0872 | 47.1786 | -128.4856 | 24.9128 | -132.8214 | 51.5144 | 0.9 | 0.89826 | 0.8949 | 0.9 | 0.89826 | 0.89491 | 0.00058802 | -120.3104 | 119.942 | 0.00069228 | -120.3101 | 119.9418
Line11_12_13 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7297e-05 | -5.4919e-06 | 2.7183e-06 | 1.7298e-05 | 5.492e-06 | 1.2625e-06 | -3.8383e-06 | -1.389e-05 | -1.2625e-06 | 3.8385e-06 | 1.389e-05 | -155.0872 | 47.1786 | -128.4857 | 24.9128 | -132.8214 | 51.5143 | 0.9 | 0.89826 | 0.89491 | 0.9 | 0.89827 | 0.89492 | 0.00069228 | -120.3101 | 119.9418 | 0.00079653 | -120.3097 | 119.9416
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2727e-14 | -1.6941e-11 | -5.0052e-11 | -1.2727e-14 | 1.6941e-11 | 5.0052e-11 | -1.2387e-13 | 4.8067e-11 | 9.0362e-12 | 1.2387e-13 | -4.8067e-11 | -9.0362e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89827 | 0.89492 | 0.9 | 0.89827 | 0.89492 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line13_13_14 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7298e-05 | -5.4919e-06 | 2.7183e-06 | 1.7298e-05 | 5.492e-06 | 1.2625e-06 | -3.8385e-06 | -1.3891e-05 | -1.2625e-06 | 3.8387e-06 | 1.3891e-05 | -155.0872 | 47.1784 | -128.4859 | 24.9128 | -132.8216 | 51.5141 | 0.9 | 0.89827 | 0.89492 | 0.9 | 0.89828 | 0.89492 | 0.00079653 | -120.3097 | 119.9416 | 0.00090079 | -120.3093 | 119.9414
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4851e-15 | -1.1294e-11 | -3.3368e-11 | -8.485e-15 | 1.1294e-11 | 3.3368e-11 | -8.2578e-14 | 3.2045e-11 | 6.0241e-12 | 8.2578e-14 | -3.2045e-11 | -6.0241e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89827 | 0.89492 | 0.9 | 0.89827 | 0.89492 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.242e-15 | -5.6469e-12 | -1.6684e-11 | -4.242e-15 | 5.6469e-12 | 1.6684e-11 | -4.1289e-14 | 1.6022e-11 | 3.0121e-12 | 4.1288e-14 | -1.6022e-11 | -3.0121e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89827 | 0.89492 | 0.9 | 0.89827 | 0.89492 | 0.00079653 | -120.3097 | 119.9416 | 0.00079653 | -120.3097 | 119.9416
Line16_4_18 | 0 | 0.049871 | 0.049871 | 0 | 0.049871 | 0.049871 | 0 | 0.011517 | 0.011517 | 0 | 0.011517 | 0.011517 | 4.4738e-15 | 0.0099474 | 0.0025839 | -4.4738e-15 | -0.0098997 | -0.0025362 | -2.8628e-14 | 0.0026199 | 0.0099154 | 2.8627e-14 | -0.0025701 | -0.0098657 | 0 | -135.265 | 44.735 | 0 | 44.735 | -135.265 | 0.9 | 0.89314 | 0.88967 | 0.9 | 0.88804 | 0.88445 | 0.0005523 | -120.5099 | 120.1288 | 0.0005523 | -120.7112 | 120.3181
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1671e-15 | -5.7587e-12 | -1.6789e-11 | 3.1674e-15 | 5.7587e-12 | 1.6789e-11 | -1.9672e-14 | 1.6097e-11 | 2.9686e-12 | 1.9671e-14 | -1.6097e-11 | -2.9686e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89824 | 0.89488 | 0.00037951 | -120.3111 | 119.9424 | 0.00037951 | -120.3111 | 119.9424
Line1_1_3 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7297e-05 | -5.4916e-06 | 2.7183e-06 | 1.7297e-05 | 5.4917e-06 | 1.2625e-06 | -3.8378e-06 | -1.389e-05 | -1.2625e-06 | 3.838e-06 | 1.389e-05 | -155.0872 | 47.1788 | -128.4855 | 24.9128 | -132.8212 | 51.5145 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89825 | 0.89489 | 0.00037951 | -120.3111 | 119.9424 | 0.00048377 | -120.3108 | 119.9422
Line2_1_4 | 2.9717e-05 | 0.049706 | 0.049729 | 2.9717e-05 | 0.049706 | 0.049729 | 6.8628e-06 | 0.011479 | 0.011484 | 6.8628e-06 | 0.011479 | 0.011484 | -6.1658e-06 | 0.0099649 | 0.0026313 | 6.1659e-06 | -0.0099174 | -0.0025838 | 3.6241e-07 | 0.0026494 | 0.0099346 | -3.6239e-07 | -0.0026 | -0.0098851 | -176.6358 | -135.2002 | 44.7772 | 3.3642 | 44.7998 | -135.2228 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89314 | 0.88967 | 0.00037951 | -120.3111 | 119.9424 | 0.0005523 | -120.5099 | 120.1288
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3328e-15 | -1.1517e-11 | -3.3577e-11 | 6.3332e-15 | 1.1517e-11 | 3.3577e-11 | -3.9344e-14 | 3.2194e-11 | 5.9372e-12 | 3.9345e-14 | -3.2194e-11 | -5.9372e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89824 | 0.89488 | 0.9 | 0.89824 | 0.89488 | 0.00037951 | -120.3111 | 119.9424 | 0.00037951 | -120.3111 | 119.9424
Line4_2_6 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | -2.74e-06 | -1.7343e-05 | -5.4841e-06 | 2.74e-06 | 1.7343e-05 | 5.4842e-06 | 1.2587e-06 | -3.8892e-06 | -1.3938e-05 | -1.2587e-06 | 3.8894e-06 | 1.3939e-05 | -155.3261 | 47.0495 | -128.5804 | 24.6739 | -132.9505 | 51.4196 | 0.9 | 0.89825 | 0.89489 | 0.9 | 0.89826 | 0.8949 | 0.00048425 | -120.3108 | 119.9422 | 0.00058898 | -120.3104 | 119.942
Line5_6_7 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 1.4507e-05 | 8.5681e-05 | 7.2477e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | 3.3503e-06 | 1.9787e-05 | 1.6738e-05 | -2.74e-06 | -1.7343e-05 | -5.4842e-06 | 2.74e-06 | 1.7343e-05 | 5.4843e-06 | 1.2587e-06 | -3.8894e-06 | -1.3939e-05 | -1.2587e-06 | 3.8896e-06 | 1.3939e-05 | -155.3261 | 47.0495 | -128.5805 | 24.6739 | -132.9505 | 51.4195 | 0.9 | 0.89826 | 0.8949 | 0.9 | 0.89826 | 0.89491 | 0.00058898 | -120.3104 | 119.942 | 0.00069371 | -120.3101 | 119.9418
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4747e-15 | -1.7023e-11 | -5.013e-11 | -7.4747e-15 | 1.7023e-11 | 5.013e-11 | -1.0787e-13 | 4.8123e-11 | 9.0043e-12 | 1.0788e-13 | -4.8123e-11 | -9.0043e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89826 | 0.89491 | 0.9 | 0.89826 | 0.89491 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4913e-15 | -5.6745e-12 | -1.671e-11 | -2.4914e-15 | 5.6745e-12 | 1.671e-11 | -3.5959e-14 | 1.6041e-11 | 3.0014e-12 | 3.596e-14 | -1.6041e-11 | -3.0014e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89826 | 0.89491 | 0.9 | 0.89826 | 0.89491 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4917e-15 | -5.6745e-12 | -1.671e-11 | -2.492e-15 | 5.6745e-12 | 1.671e-11 | -3.5959e-14 | 1.6041e-11 | 3.0014e-12 | 3.596e-14 | -1.6041e-11 | -3.0014e-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.89826 | 0.89491 | 0.9 | 0.89826 | 0.89491 | 0.00069371 | -120.3101 | 119.9418 | 0.00069371 | -120.3101 | 119.9418
Line9_3_11 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 1.442e-05 | 8.5411e-05 | 7.2273e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | 3.3302e-06 | 1.9725e-05 | 1.6691e-05 | -2.7183e-06 | -1.7297e-05 | -5.4917e-06 | 2.7183e-06 | 1.7297e-05 | 5.4918e-06 | 1.2625e-06 | -3.838e-06 | -1.389e-05 | -1.2625e-06 | 3.8382e-06 | 1.389e-05 | -155.0872 | 47.1787 | -128.4856 | 24.9128 | -132.8213 | 51.5144 | 0.9 | 0.89825 | 0.89489 | 0.9 | 0.89826 | 0.8949 | 0.00048377 | -120.3108 | 119.9422 | 0.00058802 | -120.3104 | 119.942

## LG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.64353 | 0.28538 | 0.31637 | 0.64353 | 0.28538 | 0.31637 | 0.14862 | 0.065905 | 0.073063 | 0.14862 | 0.065905 | 0.073064 | -0.036877 | -0.068172 | 0.08628 | 0.039791 | 0.068827 | -0.086326 | -0.07397 | 0.047799 | 0.0063629 | 0.079627 | -0.047446 | -0.0053278 | 105.2482 | 87.3242 | 127.459 | -74.7518 | -92.6758 | -52.541 |  | 0.55615 | 1.2633 | 1.1841 | 0.59896 | 1.2684 | 1.1838 | -11.2496 | -127.7123 | 131.6768 | -11.3035 | -127.2562 | 130.9907
Line10_11_12 | 0.57915 | 0.25362 | 0.29215 | 0.57915 | 0.25362 | 0.29215 | 0.13375 | 0.058571 | 0.067469 | 0.13375 | 0.058571 | 0.067469 | -0.039863 | -0.059132 | 0.079843 | 0.042238 | 0.059629 | -0.079857 | -0.074697 | 0.045249 | 0.0016856 | 0.079258 | -0.044985 | -0.00079375 | 106.918 | 90.5035 | 129.1879 | -73.082 | -89.4965 | -50.8121 |  | 0.63303 | 1.2713 | 1.1837 | 0.67148 | 1.2753 | 1.1837 | -11.1691 | -126.9203 | 130.3973 | -11.1357 | -126.528 | 129.7573
Line11_12_13 | 0.57915 | 0.25362 | 0.29215 | 0.57915 | 0.25362 | 0.29215 | 0.13375 | 0.058571 | 0.067469 | 0.13375 | 0.058571 | 0.067469 | -0.042238 | -0.059629 | 0.079857 | 0.044612 | 0.060127 | -0.079872 | -0.079258 | 0.044985 | 0.00079375 | 0.083819 | -0.044722 | 9.8101e-05 | 106.918 | 90.5035 | 129.1879 | -73.082 | -89.4965 | -50.8122 |  | 0.67148 | 1.2753 | 1.1837 | 0.70992 | 1.2794 | 1.1838 | -11.1357 | -126.528 | 129.7573 | -11.1059 | -126.1382 | 129.1175
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1396e-08 | 5.7076e-08 | -7.5746e-08 | -1.343e-08 | -3.9155e-08 | 4.9859e-08 | 4.5665e-08 | -7.106e-08 | -3.3169e-08 | -3.097e-08 | 4.6847e-08 | 2.2835e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70992 | 1.2794 | 1.1838 | 0.70992 | 1.2794 | 1.1838 | -11.1059 | -126.1382 | 129.1175 | -11.1059 | -126.1382 | 129.1175
Line13_13_14 | 0.57915 | 0.25362 | 0.29215 | 0.57915 | 0.25362 | 0.29215 | 0.13375 | 0.058571 | 0.067469 | 0.13375 | 0.058571 | 0.067469 | -0.044612 | -0.060127 | 0.079872 | 0.046987 | 0.060624 | -0.079886 | -0.083819 | 0.044722 | -9.8067e-05 | 0.08838 | -0.044459 | 0.00098992 | 106.918 | 90.5035 | 129.1878 | -73.082 | -89.4964 | -50.8122 |  | 0.70992 | 1.2794 | 1.1838 | 0.74837 | 1.2836 | 1.1841 | -11.1059 | -126.1382 | 129.1175 | -11.0792 | -125.751 | 128.4779
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4264e-08 | 3.8051e-08 | -5.0497e-08 | -6.2979e-09 | -2.013e-08 | 2.461e-08 | 3.0443e-08 | -4.7373e-08 | -2.2113e-08 | -1.5748e-08 | 2.316e-08 | 1.1779e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70992 | 1.2794 | 1.1838 | 0.70992 | 1.2794 | 1.1838 | -11.1059 | -126.1382 | 129.1175 | -11.1059 | -126.1382 | 129.1175
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1319e-09 | 1.9025e-08 | -2.5249e-08 | 8.3405e-10 | -1.1044e-09 | -6.3848e-10 | 1.5222e-08 | -2.3687e-08 | -1.1056e-08 | -5.2648e-10 | -5.2669e-10 | 7.2221e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70992 | 1.2794 | 1.1838 | 0.70992 | 1.2794 | 1.1838 | -11.1059 | -126.1382 | 129.1175 | -11.1059 | -126.1382 | 129.1175
Line16_4_18 | 3.8658 | 0 | 0 | 3.8658 | 0 | 0 | 0.89276 | 0 | 0 | 0.89276 | 0 | 0 | 0.12453 | 3.1985e-08 | -3.3572e-08 | -1.8456e-14 | -7.8357e-10 | -2.1067e-10 | 0.24907 | -2.9278e-08 | -2.0476e-08 | 8.0331e-14 | -1.5289e-10 | 5.2981e-10 | -75.1978 | 0 | 0 | 104.8022 | 0 | 0 |  | 0.31192 | 1.2468 | 1.142 | 0 | 1.224 | 1.0942 | -11.7629 | -124.5523 | 129.2795 | 0 | -121.8591 | 127.2251
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5127e-09 | 2.4527e-08 | -2.9297e-08 | 9.6593e-10 | -1.0323e-09 | -6.7656e-10 | 1.5196e-08 | -2.7482e-08 | -1.7712e-08 | -4.1771e-10 | -6.5272e-10 | 9.2265e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.55615 | 1.2633 | 1.1841 | 0.55615 | 1.2633 | 1.1841 | -11.2496 | -127.7123 | 131.6768 | -11.2496 | -127.7123 | 131.6768
Line1_1_3 | 0.57915 | 0.25362 | 0.29215 | 0.57915 | 0.25362 | 0.29215 | 0.13375 | 0.058571 | 0.067469 | 0.13375 | 0.058571 | 0.067469 | -0.035113 | -0.058137 | 0.079815 | 0.037488 | 0.058634 | -0.079829 | -0.065575 | 0.045775 | 0.0034693 | 0.070136 | -0.045512 | -0.0025774 | 106.918 | 90.5035 | 129.1879 | -73.082 | -89.4965 | -50.8121 |  | 0.55615 | 1.2633 | 1.1841 | 0.59459 | 1.2673 | 1.1838 | -11.2496 | -127.7123 | 131.6768 | -11.2067 | -127.315 | 131.0371
Line2_1_4 | 2.9061 | 0.37422 | 0.2905 | 2.9061 | 0.37422 | 0.2905 | 0.67113 | 0.086423 | 0.067088 | 0.67113 | 0.086424 | 0.067088 | 0.17213 | -0.097093 | 0.079202 | -0.0982 | 0.098396 | -0.076565 | 0.33119 | 0.049938 | 0.0061353 | -0.18488 | -0.043928 | -0.0027168 | -73.7872 | 79.5058 | 127.2473 | 106.2128 | -100.4942 | -52.7527 |  | 0.55615 | 1.2633 | 1.1841 | 0.31192 | 1.2468 | 1.142 | -11.2496 | -127.7123 | 131.6768 | -11.7629 | -124.5523 | 129.2795
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1025e-08 | 4.9055e-08 | -5.8594e-08 | -4.5468e-09 | -2.556e-08 | 2.8621e-08 | 3.0392e-08 | -5.4963e-08 | -3.5423e-08 | -1.5614e-08 | 2.6829e-08 | 1.8634e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.55615 | 1.2633 | 1.1841 | 0.55615 | 1.2633 | 1.1841 | -11.2496 | -127.7123 | 131.6768 | -11.2496 | -127.7123 | 131.6768
Line4_2_6 | 0.64353 | 0.28538 | 0.31637 | 0.64353 | 0.28538 | 0.31637 | 0.14862 | 0.065905 | 0.073064 | 0.14862 | 0.065905 | 0.073064 | -0.039791 | -0.068827 | 0.086326 | 0.042704 | 0.069482 | -0.086371 | -0.079627 | 0.047446 | 0.0053278 | 0.085285 | -0.047092 | -0.0042928 | 105.2482 | 87.3242 | 127.459 | -74.7518 | -92.6758 | -52.541 |  | 0.59896 | 1.2684 | 1.1838 | 0.64178 | 1.2736 | 1.1836 | -11.3035 | -127.2562 | 130.9907 | -11.3501 | -126.8038 | 130.3043
Line5_6_7 | 0.64353 | 0.28538 | 0.31637 | 0.64353 | 0.28538 | 0.31637 | 0.14862 | 0.065905 | 0.073064 | 0.14862 | 0.065905 | 0.073064 | -0.042704 | -0.069482 | 0.086371 | 0.045618 | 0.070137 | -0.086417 | -0.085285 | 0.047092 | 0.0042928 | 0.090942 | -0.046739 | -0.0032577 | 105.2482 | 87.3242 | 127.459 | -74.7518 | -92.6758 | -52.541 |  | 0.64178 | 1.2736 | 1.1836 | 0.68459 | 1.2789 | 1.1836 | -11.3501 | -126.8038 | 130.3043 | -11.391 | -126.3551 | 129.6178
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1186e-08 | 5.9844e-08 | -7.8384e-08 | -1.3259e-08 | -4.1e-08 | 5.1612e-08 | 4.6016e-08 | -7.3688e-08 | -3.615e-08 | -3.1198e-08 | 4.858e-08 | 2.4861e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68459 | 1.2789 | 1.1836 | 0.68459 | 1.2789 | 1.1836 | -11.391 | -126.3551 | 129.6178 | -11.391 | -126.3551 | 129.6178
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0619e-09 | 1.9948e-08 | -2.6128e-08 | 8.6532e-10 | -1.1034e-09 | -6.4388e-10 | 1.5339e-08 | -2.4563e-08 | -1.205e-08 | -5.2056e-10 | -5.4499e-10 | 7.6134e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68459 | 1.2789 | 1.1836 | 0.68459 | 1.2789 | 1.1836 | -11.391 | -126.3551 | 129.6178 | -11.391 | -126.3551 | 129.6178
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0619e-09 | 1.9948e-08 | -2.6128e-08 | 8.6532e-10 | -1.1034e-09 | -6.4388e-10 | 1.5339e-08 | -2.4563e-08 | -1.205e-08 | -5.2056e-10 | -5.4499e-10 | 7.6134e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.68459 | 1.2789 | 1.1836 | 0.68459 | 1.2789 | 1.1836 | -11.391 | -126.3551 | 129.6178 | -11.391 | -126.3551 | 129.6178
Line9_3_11 | 0.57915 | 0.25362 | 0.29215 | 0.57915 | 0.25362 | 0.29215 | 0.13375 | 0.058571 | 0.067469 | 0.13375 | 0.058571 | 0.067469 | -0.037488 | -0.058634 | 0.079829 | 0.039863 | 0.059132 | -0.079843 | -0.070136 | 0.045512 | 0.0025774 | 0.074697 | -0.045249 | -0.0016856 | 106.918 | 90.5035 | 129.1879 | -73.082 | -89.4965 | -50.8121 |  | 0.59459 | 1.2673 | 1.1838 | 0.63303 | 1.2713 | 1.1837 | -11.2067 | -127.315 | 131.0371 | -11.1691 | -126.9203 | 130.3973

## LG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.65948 | 0.29459 | 0.32341 | 0.65948 | 0.29459 | 0.32341 | 0.1523 | 0.068033 | 0.074688 | 0.1523 | 0.068033 | 0.074688 | -0.038817 | -0.073802 | 0.092502 | 0.041869 | 0.074493 | -0.092549 | -0.077726 | 0.051973 | 0.0082163 | 0.083664 | -0.051588 | -0.0071459 | 105.0126 | 87.3079 | 126.7661 | -74.9874 | -92.6921 | -53.2339 |  | 0.57045 | 1.3268 | 1.2434 | 0.61429 | 1.3319 | 1.2428 | -11.5251 | -127.8459 | 131.842 | -11.5726 | -127.3953 | 131.1813
Line10_11_12 | 0.59589 | 0.26302 | 0.2996 | 0.59589 | 0.26302 | 0.2996 | 0.13762 | 0.060742 | 0.06919 | 0.13762 | 0.060742 | 0.06919 | -0.042068 | -0.064369 | 0.08591 | 0.044575 | 0.064899 | -0.085925 | -0.078861 | 0.049293 | 0.0032196 | 0.083687 | -0.049002 | -0.0022913 | 106.6397 | 90.385 | 128.4592 | -73.3603 | -89.615 | -51.5408 |  | 0.64949 | 1.3347 | 1.2425 | 0.68901 | 1.3388 | 1.2423 | -11.4378 | -127.0592 | 130.6054 | -11.4017 | -126.6694 | 129.9867
Line11_12_13 | 0.59589 | 0.26302 | 0.2996 | 0.59589 | 0.26302 | 0.2996 | 0.13762 | 0.060742 | 0.06919 | 0.13762 | 0.060742 | 0.06919 | -0.044575 | -0.064899 | 0.085925 | 0.047082 | 0.06543 | -0.08594 | -0.083687 | 0.049002 | 0.0022913 | 0.088514 | -0.048711 | -0.0013629 | 106.6397 | 90.385 | 128.4592 | -73.3603 | -89.6149 | -51.5408 |  | 0.68901 | 1.3388 | 1.2423 | 0.72853 | 1.3429 | 1.2422 | -11.4017 | -126.6694 | 129.9867 | -11.3695 | -126.282 | 129.3678
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3549e-08 | 6.4745e-08 | -8.5268e-08 | -1.4764e-08 | -4.4392e-08 | 5.613e-08 | 5.05e-08 | -8.014e-08 | -3.8385e-08 | -3.4246e-08 | 5.2834e-08 | 2.6405e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72853 | 1.3429 | 1.2422 | 0.72853 | 1.3429 | 1.2422 | -11.3695 | -126.282 | 129.3678 | -11.3695 | -126.282 | 129.3678
Line13_13_14 | 0.59589 | 0.26302 | 0.2996 | 0.59589 | 0.26302 | 0.2996 | 0.13762 | 0.060742 | 0.06919 | 0.13762 | 0.060742 | 0.06919 | -0.047082 | -0.06543 | 0.08594 | 0.049589 | 0.065961 | -0.085955 | -0.088514 | 0.048712 | 0.0013629 | 0.093341 | -0.048421 | -0.00043457 | 106.6397 | 90.3851 | 128.4592 | -73.3603 | -89.6149 | -51.5408 |  | 0.72853 | 1.3429 | 1.2422 | 0.76805 | 1.3471 | 1.2423 | -11.3695 | -126.282 | 129.3678 | -11.3406 | -125.8969 | 128.7488
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5699e-08 | 4.3163e-08 | -5.6845e-08 | -6.9149e-09 | -2.281e-08 | 2.7708e-08 | 3.3667e-08 | -5.3427e-08 | -2.559e-08 | -1.7413e-08 | 2.6121e-08 | 1.361e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72853 | 1.3429 | 1.2422 | 0.72853 | 1.3429 | 1.2422 | -11.3695 | -126.282 | 129.3678 | -11.3695 | -126.282 | 129.3678
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8495e-09 | 2.1582e-08 | -2.8423e-08 | 9.3464e-10 | -1.2286e-09 | -7.1467e-10 | 1.6833e-08 | -2.6713e-08 | -1.2795e-08 | -5.7926e-10 | -5.9267e-10 | 8.1554e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.72853 | 1.3429 | 1.2422 | 0.72853 | 1.3429 | 1.2422 | -11.3695 | -126.282 | 129.3678 | -11.3695 | -126.282 | 129.3678
Line16_4_18 | 3.9575 | 0 | 0 | 3.9575 | 0 | 0 | 0.91395 | 0 | 0 | 0.91395 | 0 | 0 | 0.13052 | 3.5595e-08 | -3.7286e-08 | 3.0969e-14 | -8.8246e-10 | -2.5145e-10 | 0.26103 | -3.2701e-08 | -2.3056e-08 | -2.8796e-14 | -1.9352e-10 | 6.0898e-10 | -75.4484 | 0 | 0 | 104.5516 | 0 | 0 |  | 0.31932 | 1.3097 | 1.1994 | 0 | 1.2863 | 1.1501 | -12.0134 | -124.7619 | 129.523 | 0 | -122.1377 | 127.5436
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0648e-09 | 2.7534e-08 | -3.2746e-08 | 1.0612e-09 | -1.1535e-09 | -7.6046e-10 | 1.6639e-08 | -3.0811e-08 | -2.006e-08 | -4.597e-10 | -7.3052e-10 | 1.0291e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.57045 | 1.3268 | 1.2434 | 0.57045 | 1.3268 | 1.2434 | -11.5251 | -127.8459 | 131.842 | -11.5251 | -127.8459 | 131.842
Line1_1_3 | 0.59589 | 0.26302 | 0.2996 | 0.59589 | 0.26302 | 0.2996 | 0.13762 | 0.060742 | 0.06919 | 0.13762 | 0.060742 | 0.06919 | -0.037054 | -0.063308 | 0.085881 | 0.039561 | 0.063838 | -0.085895 | -0.069207 | 0.049874 | 0.0050763 | 0.074034 | -0.049583 | -0.004148 | 106.6397 | 90.385 | 128.4592 | -73.3603 | -89.615 | -51.5408 |  | 0.57045 | 1.3268 | 1.2434 | 0.60997 | 1.3307 | 1.2429 | -11.5251 | -127.8459 | 131.842 | -11.4786 | -127.4514 | 131.2239
Line2_1_4 | 2.9884 | 0.38167 | 0.29788 | 2.9884 | 0.38167 | 0.29788 | 0.69014 | 0.088142 | 0.068792 | 0.69014 | 0.088142 | 0.068792 | 0.1813 | -0.10364 | 0.085158 | -0.10315 | 0.10503 | -0.082393 | 0.34946 | 0.054174 | 0.008023 | -0.19475 | -0.047893 | -0.0044091 | -74.1052 | 79.7502 | 126.4599 | 105.8948 | -100.2498 | -53.5402 |  | 0.57045 | 1.3268 | 1.2434 | 0.31932 | 1.3097 | 1.1994 | -11.5251 | -127.8459 | 131.842 | -12.0134 | -124.7619 | 129.523
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.213e-08 | 5.5068e-08 | -6.5492e-08 | -5.0035e-09 | -2.8687e-08 | 3.1986e-08 | 3.3278e-08 | -6.1622e-08 | -4.0121e-08 | -1.7098e-08 | 3.008e-08 | 2.109e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.57045 | 1.3268 | 1.2434 | 0.57045 | 1.3268 | 1.2434 | -11.5251 | -127.8459 | 131.842 | -11.5251 | -127.8459 | 131.842
Line4_2_6 | 0.65948 | 0.29459 | 0.32341 | 0.65948 | 0.29459 | 0.32341 | 0.1523 | 0.068033 | 0.074688 | 0.1523 | 0.068033 | 0.074688 | -0.041869 | -0.074493 | 0.092549 | 0.044921 | 0.075184 | -0.092595 | -0.083664 | 0.051588 | 0.0071459 | 0.089602 | -0.051203 | -0.0060756 | 105.0126 | 87.3079 | 126.7661 | -74.9874 | -92.6921 | -53.2339 |  | 0.61429 | 1.3319 | 1.2428 | 0.65812 | 1.3371 | 1.2424 | -11.5726 | -127.3953 | 131.1813 | -11.6138 | -126.9483 | 130.5202
Line5_6_7 | 0.65948 | 0.29459 | 0.32341 | 0.65948 | 0.29459 | 0.32341 | 0.1523 | 0.068033 | 0.074688 | 0.1523 | 0.068033 | 0.074688 | -0.044921 | -0.075184 | 0.092595 | 0.047973 | 0.075875 | -0.092642 | -0.089602 | 0.051203 | 0.0060756 | 0.09554 | -0.050818 | -0.0050052 | 105.0126 | 87.3079 | 126.7661 | -74.9874 | -92.6921 | -53.2339 |  | 0.65812 | 1.3371 | 1.2424 | 0.70196 | 1.3423 | 1.2422 | -11.6138 | -126.9483 | 130.5202 | -11.6498 | -126.5047 | 129.8587
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3261e-08 | 6.7807e-08 | -8.8119e-08 | -1.4541e-08 | -4.6432e-08 | 5.8025e-08 | 5.079e-08 | -8.2995e-08 | -4.1733e-08 | -3.4432e-08 | 5.4716e-08 | 2.868e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70196 | 1.3423 | 1.2422 | 0.70196 | 1.3423 | 1.2422 | -11.6498 | -126.5047 | 129.8587 | -11.6498 | -126.5047 | 129.8587
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7538e-09 | 2.2602e-08 | -2.9373e-08 | 9.6618e-10 | -1.2275e-09 | -7.2161e-10 | 1.693e-08 | -2.7665e-08 | -1.3911e-08 | -5.7171e-10 | -6.1332e-10 | 8.5783e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70196 | 1.3423 | 1.2422 | 0.70196 | 1.3423 | 1.2422 | -11.6498 | -126.5047 | 129.8587 | -11.6498 | -126.5047 | 129.8587
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7538e-09 | 2.2602e-08 | -2.9373e-08 | 9.6618e-10 | -1.2275e-09 | -7.2161e-10 | 1.693e-08 | -2.7665e-08 | -1.3911e-08 | -5.7171e-10 | -6.1332e-10 | 8.5783e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.70196 | 1.3423 | 1.2422 | 0.70196 | 1.3423 | 1.2422 | -11.6498 | -126.5047 | 129.8587 | -11.6498 | -126.5047 | 129.8587
Line9_3_11 | 0.59589 | 0.26302 | 0.2996 | 0.59589 | 0.26302 | 0.2996 | 0.13762 | 0.060742 | 0.06919 | 0.13762 | 0.060742 | 0.06919 | -0.039561 | -0.063838 | 0.085895 | 0.042068 | 0.064369 | -0.08591 | -0.074034 | 0.049583 | 0.004148 | 0.078861 | -0.049293 | -0.0032196 | 106.6397 | 90.385 | 128.4592 | -73.3603 | -89.615 | -51.5408 |  | 0.60997 | 1.3307 | 1.2429 | 0.64949 | 1.3347 | 1.2425 | -11.4786 | -127.4514 | 131.2239 | -11.4378 | -127.0592 | 130.6054

## LG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.12283 | 0.11625 | 0.12004 | 0.12283 | 0.11625 | 0.12004 | 0.028367 | 0.026847 | 0.027722 | 0.028367 | 0.026847 | 0.027722 | -0.0026453 | -0.0018847 | -0.00086312 | 0.0027976 | 0.0020232 | 0.0010023 | -0.030585 | -0.029153 | -0.030082 | 0.030882 | 0.029427 | 0.030371 | 94.882 | -26.2166 | -148.122 | -85.118 | 153.7834 | 31.878 |  | 1.0822 | 1.0882 | 1.0856 | 1.0931 | 1.0987 | 1.0961 | -0.061278 | -119.9157 | 120.2345 | -0.29422 | -120.1498 | 119.9878
Line10_11_12 | 0.10943 | 0.10356 | 0.10714 | 0.10943 | 0.10356 | 0.10714 | 0.025272 | 0.023917 | 0.024743 | 0.025272 | 0.023917 | 0.024743 | -0.0025618 | -0.0017963 | -0.00091052 | 0.0026828 | 0.0019061 | 0.0010213 | -0.027723 | -0.026413 | -0.027312 | 0.027958 | 0.02663 | 0.027542 | 94.8045 | -26.4425 | -148.2959 | -85.1955 | 153.5575 | 31.7041 |  | 1.1017 | 1.1069 | 1.1044 | 1.1114 | 1.1163 | 1.1139 | -0.47521 | -120.3331 | 119.7947 | -0.67674 | -120.5366 | 119.5804
Line11_12_13 | 0.10943 | 0.10356 | 0.10714 | 0.10943 | 0.10356 | 0.10714 | 0.025272 | 0.023917 | 0.024743 | 0.025272 | 0.023917 | 0.024743 | -0.0026828 | -0.0019061 | -0.0010213 | 0.0028038 | 0.002016 | 0.0011322 | -0.027958 | -0.02663 | -0.027542 | 0.028194 | 0.026848 | 0.027772 | 94.8045 | -26.4425 | -148.2959 | -85.1955 | 153.5575 | 31.7041 |  | 1.1114 | 1.1163 | 1.1139 | 1.1211 | 1.1257 | 1.1234 | -0.67674 | -120.5366 | 119.5804 | -0.87478 | -120.7366 | 119.3697
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4222e-09 | 1.0903e-09 | 2.118e-10 | -1.2411e-09 | -1.0396e-09 | -4.4359e-10 | 6.842e-10 | -5.4925e-10 | 3.6757e-10 | -5.2204e-10 | 3.1044e-10 | -2.9262e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1211 | 1.1257 | 1.1234 | 1.1211 | 1.1257 | 1.1234 | -0.87478 | -120.7366 | 119.3697 | -0.87478 | -120.7366 | 119.3697
Line13_13_14 | 0.10943 | 0.10356 | 0.10714 | 0.10943 | 0.10356 | 0.10714 | 0.025272 | 0.023917 | 0.024743 | 0.025272 | 0.023917 | 0.024743 | -0.0028038 | -0.002016 | -0.0011322 | 0.0029248 | 0.0021258 | 0.001243 | -0.028194 | -0.026848 | -0.027772 | 0.028429 | 0.027065 | 0.028003 | 94.8045 | -26.4424 | -148.2959 | -85.1955 | 153.5576 | 31.7041 |  | 1.1211 | 1.1257 | 1.1234 | 1.1309 | 1.1351 | 1.1328 | -0.87478 | -120.7366 | 119.3697 | -1.0694 | -120.9334 | 119.1625
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4813e-10 | 7.2685e-10 | 1.412e-10 | -7.6699e-10 | -6.762e-10 | -3.7299e-10 | 4.5614e-10 | -3.6616e-10 | 2.4505e-10 | -2.9397e-10 | 1.2736e-10 | -1.701e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1211 | 1.1257 | 1.1234 | 1.1211 | 1.1257 | 1.1234 | -0.87478 | -120.7366 | 119.3697 | -0.87478 | -120.7366 | 119.3697
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7407e-10 | 3.6343e-10 | 7.0601e-11 | -2.9293e-10 | -3.1277e-10 | -3.0239e-10 | 2.2807e-10 | -1.8308e-10 | 1.2252e-10 | -6.5899e-11 | -5.5719e-11 | -4.7577e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1211 | 1.1257 | 1.1234 | 1.1211 | 1.1257 | 1.1234 | -0.87478 | -120.7366 | 119.3697 | -0.87478 | -120.7366 | 119.3697
Line16_4_18 | 0.035604 | 0 | 0 | 0.035604 | 0 | 0 | 0.0082225 | 0 | 0 | 0.0082225 | 0 | 0 | 0.006349 | 3.287e-10 | -1.4971e-10 | -0.0063384 | -2.0207e-10 | -1.9401e-10 | 0.0063595 | -3.2562e-10 | 4.8154e-11 | -0.0063384 | 9.8203e-13 | 3.9911e-12 | -45.2654 | 0 | 0 | 134.7346 | 0 | 0 |  | 1.0929 | 1.1005 | 1.0983 | 1.0902 | 1.1001 | 1.0982 | -0.2178 | -120.0067 | 120.0834 | -0.26543 | -119.9867 | 120.0541
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2303e-10 | 2.4083e-10 | -1.4206e-10 | -1.2796e-10 | -1.5228e-10 | -1.4156e-10 | 2.1796e-10 | -2.8314e-10 | 4.38e-11 | -4.4562e-12 | 6.1675e-12 | 1.7108e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0822 | 1.0882 | 1.0856 | 1.0822 | 1.0882 | 1.0856 | -0.061278 | -119.9157 | 120.2345 | -0.061278 | -119.9157 | 120.2345
Line1_1_3 | 0.10943 | 0.10356 | 0.10714 | 0.10943 | 0.10356 | 0.10714 | 0.025272 | 0.023917 | 0.024743 | 0.025272 | 0.023917 | 0.024743 | -0.0023199 | -0.0015767 | -0.00068887 | 0.0024409 | 0.0016865 | 0.00079969 | -0.027251 | -0.025978 | -0.026851 | 0.027487 | 0.026195 | 0.027082 | 94.8045 | -26.4425 | -148.2959 | -85.1955 | 153.5575 | 31.7041 |  | 1.0822 | 1.0882 | 1.0856 | 1.0919 | 1.0975 | 1.095 | -0.061278 | -119.9157 | 120.2345 | -0.27008 | -120.1262 | 120.0127
Line2_1_4 | 0.1113 | 0.13195 | 0.13476 | 0.1113 | 0.13195 | 0.13476 | 0.025704 | 0.030473 | 0.03112 | 0.025704 | 0.030473 | 0.03112 | -0.0047325 | -0.010096 | -0.0088884 | 0.0048546 | 0.010261 | 0.0090797 | -0.027413 | -0.031585 | -0.032593 | 0.027669 | 0.031927 | 0.032952 | 99.7335 | -12.1895 | -134.5112 | -80.2665 | 167.8105 | 45.4888 |  | 1.0822 | 1.0882 | 1.0856 | 1.0929 | 1.1005 | 1.0983 | -0.061278 | -119.9157 | 120.2345 | -0.2178 | -120.0067 | 120.0834
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4605e-10 | 4.8166e-10 | -2.8412e-10 | -4.5098e-10 | -3.9311e-10 | 5.0484e-13 | 4.3593e-10 | -5.6628e-10 | 8.7599e-11 | -2.2242e-10 | 2.8931e-10 | -2.6691e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0822 | 1.0882 | 1.0856 | 1.0822 | 1.0882 | 1.0856 | -0.061278 | -119.9157 | 120.2345 | -0.061278 | -119.9157 | 120.2345
Line4_2_6 | 0.12283 | 0.11625 | 0.12004 | 0.12283 | 0.11625 | 0.12004 | 0.028367 | 0.026847 | 0.027722 | 0.028367 | 0.026847 | 0.027722 | -0.0027976 | -0.0020232 | -0.0010023 | 0.0029498 | 0.0021617 | 0.0011416 | -0.030882 | -0.029427 | -0.030371 | 0.031179 | 0.0297 | 0.03066 | 94.882 | -26.2166 | -148.122 | -85.118 | 153.7834 | 31.878 |  | 1.0931 | 1.0987 | 1.0961 | 1.1041 | 1.1092 | 1.1067 | -0.29422 | -120.1498 | 119.9878 | -0.52256 | -120.3794 | 119.7457
Line5_6_7 | 0.12283 | 0.11625 | 0.12004 | 0.12283 | 0.11625 | 0.12004 | 0.028367 | 0.026847 | 0.027722 | 0.028367 | 0.026847 | 0.027722 | -0.0029498 | -0.0021617 | -0.0011416 | 0.003102 | 0.0023001 | 0.0012808 | -0.031179 | -0.0297 | -0.03066 | 0.031476 | 0.029974 | 0.030949 | 94.882 | -26.2166 | -148.122 | -85.118 | 153.7834 | 31.878 |  | 1.1041 | 1.1092 | 1.1067 | 1.115 | 1.1198 | 1.1174 | -0.52256 | -120.3794 | 119.7457 | -0.74643 | -120.6048 | 119.5083
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3551e-09 | 1.0272e-09 | 1.0436e-10 | -1.1695e-09 | -9.7153e-10 | -3.4571e-10 | 6.7933e-10 | -6.0439e-10 | 3.3459e-10 | -5.0881e-10 | 3.5742e-10 | -2.5998e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.115 | 1.1198 | 1.1174 | 1.115 | 1.1198 | 1.1174 | -0.74643 | -120.6048 | 119.5083 | -0.74643 | -120.6048 | 119.5083
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5171e-10 | 3.4241e-10 | 3.4786e-11 | -2.6605e-10 | -2.8671e-10 | -2.7614e-10 | 2.2644e-10 | -2.0146e-10 | 1.1153e-10 | -5.5922e-11 | -4.5503e-11 | -3.6917e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.115 | 1.1198 | 1.1174 | 1.115 | 1.1198 | 1.1174 | -0.74643 | -120.6048 | 119.5083 | -0.74643 | -120.6048 | 119.5083
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5171e-10 | 3.4241e-10 | 3.4786e-11 | -2.6605e-10 | -2.8671e-10 | -2.7614e-10 | 2.2644e-10 | -2.0146e-10 | 1.1153e-10 | -5.5922e-11 | -4.5503e-11 | -3.6917e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.115 | 1.1198 | 1.1174 | 1.115 | 1.1198 | 1.1174 | -0.74643 | -120.6048 | 119.5083 | -0.74643 | -120.6048 | 119.5083
Line9_3_11 | 0.10943 | 0.10356 | 0.10714 | 0.10943 | 0.10356 | 0.10714 | 0.025272 | 0.023917 | 0.024743 | 0.025272 | 0.023917 | 0.024743 | -0.0024409 | -0.0016865 | -0.00079969 | 0.0025618 | 0.0017963 | 0.00091052 | -0.027487 | -0.026195 | -0.027082 | 0.027723 | 0.026413 | 0.027312 | 94.8045 | -26.4425 | -148.2959 | -85.1955 | 153.5575 | 31.7041 |  | 1.0919 | 1.0975 | 1.095 | 1.1017 | 1.1069 | 1.1044 | -0.27008 | -120.1262 | 120.0127 | -0.47521 | -120.3331 | 119.7947

## LG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.12387 | 0.11694 | 0.12091 | 0.12387 | 0.11694 | 0.12091 | 0.028606 | 0.027007 | 0.027924 | 0.028606 | 0.027007 | 0.027924 | -0.0028626 | -0.002027 | -0.00090245 | 0.0030174 | 0.0021673 | 0.0010435 | -0.032308 | -0.030729 | -0.031749 | 0.032609 | 0.031006 | 0.032043 | 94.9918 | -26.1449 | -148.1348 | -85.0082 | 153.8551 | 31.8652 |  | 1.1338 | 1.1403 | 1.1375 | 1.1448 | 1.1509 | 1.1481 | -0.071565 | -119.9189 | 120.237 | -0.29481 | -120.1433 | 120
Line10_11_12 | 0.1108 | 0.10461 | 0.10836 | 0.1108 | 0.10461 | 0.10836 | 0.025589 | 0.024158 | 0.025025 | 0.025589 | 0.024158 | 0.025025 | -0.0027719 | -0.00193 | -0.00094987 | 0.002896 | 0.0020422 | 0.0010631 | -0.029387 | -0.027939 | -0.028928 | 0.029628 | 0.02816 | 0.029163 | 94.9185 | -26.3689 | -148.3066 | -85.0815 | 153.6311 | 31.6934 |  | 1.1535 | 1.1593 | 1.1565 | 1.1634 | 1.1688 | 1.1661 | -0.46992 | -120.3207 | 119.8127 | -0.66405 | -120.5168 | 119.6058
Line11_12_13 | 0.1108 | 0.10461 | 0.10836 | 0.1108 | 0.10461 | 0.10836 | 0.025589 | 0.024158 | 0.025025 | 0.025589 | 0.024158 | 0.025025 | -0.002896 | -0.0020422 | -0.0010631 | 0.00302 | 0.0021544 | 0.0011763 | -0.029628 | -0.02816 | -0.029163 | 0.02987 | 0.028382 | 0.029399 | 94.9185 | -26.3689 | -148.3066 | -85.0815 | 153.6311 | 31.6934 |  | 1.1634 | 1.1688 | 1.1661 | 1.1732 | 1.1783 | 1.1757 | -0.66405 | -120.5168 | 119.6058 | -0.85491 | -120.7097 | 119.4022
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.572e-09 | 1.1924e-09 | 1.7726e-10 | -1.3635e-09 | -1.1334e-09 | -4.4472e-10 | 7.7396e-10 | -6.4917e-10 | 4.059e-10 | -5.8657e-10 | 3.7392e-10 | -3.2008e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1732 | 1.1783 | 1.1757 | 1.1732 | 1.1783 | 1.1757 | -0.85491 | -120.7097 | 119.4022 | -0.85491 | -120.7097 | 119.4022
Line13_13_14 | 0.1108 | 0.10461 | 0.10836 | 0.1108 | 0.10461 | 0.10836 | 0.025589 | 0.024158 | 0.025025 | 0.025589 | 0.024158 | 0.025025 | -0.00302 | -0.0021544 | -0.0011763 | 0.0031441 | 0.0022665 | 0.0012895 | -0.02987 | -0.028382 | -0.029399 | 0.030111 | 0.028604 | 0.029634 | 94.9185 | -26.3689 | -148.3066 | -85.0815 | 153.6311 | 31.6934 |  | 1.1732 | 1.1783 | 1.1757 | 1.1831 | 1.1878 | 1.1853 | -0.85491 | -120.7097 | 119.4022 | -1.0426 | -120.8994 | 119.2019
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.048e-09 | 7.949e-10 | 1.1817e-10 | -8.3954e-10 | -7.3591e-10 | -3.8563e-10 | 5.1597e-10 | -4.3278e-10 | 2.706e-10 | -3.2859e-10 | 1.5753e-10 | -1.8478e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1732 | 1.1783 | 1.1757 | 1.1732 | 1.1783 | 1.1757 | -0.85491 | -120.7097 | 119.4022 | -0.85491 | -120.7097 | 119.4022
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.24e-10 | 3.9745e-10 | 5.9087e-11 | -3.1554e-10 | -3.3846e-10 | -3.2654e-10 | 2.5799e-10 | -2.1639e-10 | 1.353e-10 | -7.0603e-11 | -5.886e-11 | -4.9476e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1732 | 1.1783 | 1.1757 | 1.1732 | 1.1783 | 1.1757 | -0.85491 | -120.7097 | 119.4022 | -0.85491 | -120.7097 | 119.4022
Line16_4_18 | 0.037282 | 0 | 0 | 0.037282 | 0 | 0 | 0.00861 | 0 | 0 | 0.00861 | 0 | 0 | 0.0069615 | 3.6352e-10 | -1.7941e-10 | -0.0069499 | -2.2061e-10 | -2.1124e-10 | 0.006973 | -3.7057e-10 | 5.5635e-11 | -0.0069499 | 9.9359e-13 | 4.7545e-12 | -45.2735 | 0 | 0 | 134.7265 | 0 | 0 |  | 1.1444 | 1.1527 | 1.1502 | 1.1415 | 1.1522 | 1.1501 | -0.22591 | -120.0077 | 120.0881 | -0.27353 | -119.9878 | 120.0587
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6432e-10 | 2.6957e-10 | -1.6832e-10 | -1.4071e-10 | -1.6857e-10 | -1.5629e-10 | 2.4981e-10 | -3.2374e-10 | 5.1107e-11 | -5.7121e-12 | 6.5101e-12 | 1.898e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1338 | 1.1403 | 1.1375 | 1.1338 | 1.1403 | 1.1375 | -0.071565 | -119.9189 | 120.237 | -0.071565 | -119.9189 | 120.237
Line1_1_3 | 0.1108 | 0.10461 | 0.10836 | 0.1108 | 0.10461 | 0.10836 | 0.025589 | 0.024158 | 0.025025 | 0.025589 | 0.024158 | 0.025025 | -0.0025237 | -0.0017057 | -0.00072347 | 0.0026478 | 0.0018179 | 0.00083667 | -0.028904 | -0.027495 | -0.028456 | 0.029145 | 0.027717 | 0.028692 | 94.9185 | -26.3689 | -148.3066 | -85.0815 | 153.6311 | 31.6934 |  | 1.1338 | 1.1403 | 1.1375 | 1.1437 | 1.1498 | 1.147 | -0.071565 | -119.9189 | 120.237 | -0.27246 | -120.1215 | 120.0231
Line2_1_4 | 0.11049 | 0.13207 | 0.13503 | 0.11049 | 0.13207 | 0.13503 | 0.025515 | 0.030501 | 0.031184 | 0.025515 | 0.030501 | 0.031184 | -0.0045708 | -0.010463 | -0.0091423 | 0.0046909 | 0.010628 | 0.0093349 | -0.028567 | -0.03317 | -0.034273 | 0.02882 | 0.033513 | 0.034633 | 99.0188 | -12.4118 | -134.827 | -80.9812 | 167.5882 | 45.173 |  | 1.1338 | 1.1403 | 1.1375 | 1.1444 | 1.1527 | 1.1502 | -0.071565 | -119.9189 | 120.237 | -0.22591 | -120.0077 | 120.0881
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2864e-10 | 5.3914e-10 | -3.3664e-10 | -5.0503e-10 | -4.3814e-10 | 1.2026e-11 | 4.9961e-10 | -6.4749e-10 | 1.0221e-10 | -2.5552e-10 | 3.3025e-10 | -3.2127e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1338 | 1.1403 | 1.1375 | 1.1338 | 1.1403 | 1.1375 | -0.071565 | -119.9189 | 120.237 | -0.071565 | -119.9189 | 120.237
Line4_2_6 | 0.12387 | 0.11694 | 0.12091 | 0.12387 | 0.11694 | 0.12091 | 0.028606 | 0.027007 | 0.027924 | 0.028606 | 0.027007 | 0.027924 | -0.0030174 | -0.0021673 | -0.0010435 | 0.0031722 | 0.0023076 | 0.0011845 | -0.032609 | -0.031006 | -0.032043 | 0.032911 | 0.031284 | 0.032336 | 94.9918 | -26.1449 | -148.1348 | -85.0082 | 153.8551 | 31.8652 |  | 1.1448 | 1.1509 | 1.1481 | 1.1558 | 1.1615 | 1.1588 | -0.29481 | -120.1433 | 120 | -0.51381 | -120.3636 | 119.7673
Line5_6_7 | 0.12387 | 0.11694 | 0.12091 | 0.12387 | 0.11694 | 0.12091 | 0.028606 | 0.027007 | 0.027924 | 0.028606 | 0.027007 | 0.027924 | -0.0031722 | -0.0023076 | -0.0011845 | 0.0033271 | 0.0024479 | 0.0013256 | -0.032911 | -0.031284 | -0.032336 | 0.033213 | 0.031561 | 0.03263 | 94.9918 | -26.1449 | -148.1348 | -85.0082 | 153.8551 | 31.8652 |  | 1.1558 | 1.1615 | 1.1588 | 1.1669 | 1.1721 | 1.1695 | -0.51381 | -120.3636 | 119.7673 | -0.72867 | -120.5799 | 119.5388
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4996e-09 | 1.1252e-09 | 6.0034e-11 | -1.2862e-09 | -1.0605e-09 | -3.382e-10 | 7.7e-10 | -7.0941e-10 | 3.6977e-10 | -5.7318e-10 | 4.2509e-10 | -2.8448e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1669 | 1.1721 | 1.1695 | 1.1669 | 1.1721 | 1.1695 | -0.72867 | -120.5799 | 119.5388 | -0.72867 | -120.5799 | 119.5388
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9986e-10 | 3.7508e-10 | 2.0011e-11 | -2.8647e-10 | -3.103e-10 | -2.9818e-10 | 2.5667e-10 | -2.3647e-10 | 1.2326e-10 | -5.9852e-11 | -4.785e-11 | -3.7967e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1669 | 1.1721 | 1.1695 | 1.1669 | 1.1721 | 1.1695 | -0.72867 | -120.5799 | 119.5388 | -0.72867 | -120.5799 | 119.5388
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9986e-10 | 3.7508e-10 | 2.0011e-11 | -2.8647e-10 | -3.103e-10 | -2.9818e-10 | 2.5667e-10 | -2.3647e-10 | 1.2326e-10 | -5.9852e-11 | -4.785e-11 | -3.7967e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1669 | 1.1721 | 1.1695 | 1.1669 | 1.1721 | 1.1695 | -0.72867 | -120.5799 | 119.5388 | -0.72867 | -120.5799 | 119.5388
Line9_3_11 | 0.1108 | 0.10461 | 0.10836 | 0.1108 | 0.10461 | 0.10836 | 0.025589 | 0.024158 | 0.025025 | 0.025589 | 0.024158 | 0.025025 | -0.0026478 | -0.0018179 | -0.00083667 | 0.0027719 | 0.00193 | 0.00094987 | -0.029145 | -0.027717 | -0.028692 | 0.029387 | 0.027939 | 0.028928 | 94.9185 | -26.3689 | -148.3066 | -85.0815 | 153.6311 | 31.6934 |  | 1.1437 | 1.1498 | 1.147 | 1.1535 | 1.1593 | 1.1565 | -0.27246 | -120.1215 | 120.0231 | -0.46992 | -120.3207 | 119.8127

## LG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.026146 | 0.025809 | 0.025745 | 0.026146 | 0.025809 | 0.025745 | 0.0060381 | 0.0059602 | 0.0059455 | 0.0060382 | 0.0059603 | 0.0059456 | -0.00018898 | -0.0047848 | 0.0050106 | 0.0001956 | 0.0047912 | -0.0050044 | -0.00019632 | 0.0083301 | 0.0079436 | 0.00020322 | -0.0083235 | -0.0079371 | 92.2039 | 92.1176 | 92.1696 | -87.7961 | -87.8824 | -87.8304 |  | 0.045129 | 1.6118 | 1.5797 | 0.046713 | 1.6113 | 1.5782 | -41.7048 | -148.0093 | 149.9266 | -41.7008 | -147.9566 | 149.9378
Line10_11_12 | 0.02608 | 0.025744 | 0.025681 | 0.026081 | 0.025744 | 0.025681 | 0.006023 | 0.0059453 | 0.0059307 | 0.0060231 | 0.0059454 | 0.0059308 | -0.00020214 | -0.0047657 | 0.0050044 | 0.00020873 | 0.0047721 | -0.0049982 | -0.00020912 | 0.0083074 | 0.0078988 | 0.00021599 | -0.0083009 | -0.0078923 | 92.3398 | 92.2541 | 92.3056 | -87.6602 | -87.7459 | -87.6944 |  | 0.048289 | 1.6109 | 1.5767 | 0.049869 | 1.6105 | 1.5752 | -41.6882 | -147.9042 | 149.9487 | -41.6808 | -147.8516 | 149.9598
Line11_12_13 | 0.026081 | 0.025744 | 0.025681 | 0.026081 | 0.025745 | 0.025681 | 0.0060231 | 0.0059454 | 0.0059308 | 0.0060232 | 0.0059455 | 0.0059308 | -0.00020873 | -0.0047721 | 0.0049982 | 0.00021532 | 0.0047786 | -0.0049919 | -0.00021599 | 0.0083009 | 0.0078923 | 0.00022286 | -0.0082944 | -0.0078859 | 92.3398 | 92.254 | 92.3056 | -87.6602 | -87.746 | -87.6944 |  | 0.049869 | 1.6105 | 1.5752 | 0.051449 | 1.61 | 1.5737 | -41.6808 | -147.8516 | 149.9598 | -41.6737 | -147.799 | 149.9709
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6632e-09 | 1.9478e-07 | -1.7619e-07 | -4.9846e-09 | -1.3439e-07 | 1.1313e-07 | 8.7063e-09 | -3.0629e-07 | -3.0793e-07 | -5.9234e-09 | 2.0158e-07 | 2.0802e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.051449 | 1.61 | 1.5737 | 0.051449 | 1.61 | 1.5737 | -41.6737 | -147.799 | 149.9709 | -41.6737 | -147.799 | 149.9709
Line13_13_14 | 0.026082 | 0.025746 | 0.025682 | 0.026082 | 0.025746 | 0.025683 | 0.0060234 | 0.0059457 | 0.0059311 | 0.0060235 | 0.0059458 | 0.0059311 | -0.00021533 | -0.0047788 | 0.0049921 | 0.00022192 | 0.0047852 | -0.0049859 | -0.00022287 | 0.0082947 | 0.0078862 | 0.00022975 | -0.0082882 | -0.0078797 | 92.3397 | 92.2539 | 92.3054 | -87.6603 | -87.7461 | -87.6946 |  | 0.051449 | 1.61 | 1.5737 | 0.05303 | 1.6096 | 1.5722 | -41.6737 | -147.799 | 149.9709 | -41.6671 | -147.7464 | 149.982
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1088e-09 | 1.2985e-07 | -1.1746e-07 | -2.4302e-09 | -6.9469e-08 | 5.4397e-08 | 5.8042e-09 | -2.0419e-07 | -2.0529e-07 | -3.0213e-09 | 9.948e-08 | 1.0538e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.051449 | 1.61 | 1.5737 | 0.051449 | 1.61 | 1.5737 | -41.6737 | -147.799 | 149.9709 | -41.6737 | -147.799 | 149.9709
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5544e-09 | 6.4925e-08 | -5.8729e-08 | 1.2416e-10 | -4.5438e-09 | -4.3315e-09 | 2.9021e-09 | -1.021e-07 | -1.0264e-07 | -1.1916e-10 | -2.6155e-09 | 2.7384e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.051449 | 1.61 | 1.5737 | 0.051449 | 1.61 | 1.5737 | -41.6737 | -147.799 | 149.9709 | -41.6737 | -147.799 | 149.9709
Line16_4_18 | 0.23366 | 0 | 0 | 0.23366 | 0 | 0 | 0.053961 | 0 | 0 | 0.053961 | 0 | 0 | 0.00087353 | 6.643e-08 | -5.8443e-08 | 4.2388e-15 | -4.5252e-09 | -4.2937e-09 | 0.00090993 | -1.0256e-07 | -1.0415e-07 | 7.0224e-16 | -2.5994e-09 | 2.7332e-09 | -87.9055 | 0 | 0 | 92.0945 | 0 | 0 |  | 0.023375 | 1.61 | 1.5736 | 0 | 1.6087 | 1.569 | -41.7363 | -147.7969 | 149.9721 | 0 | -147.6369 | 150.0067
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.241e-09 | 6.5433e-08 | -5.8834e-08 | 1.0989e-10 | -4.5685e-09 | -4.3807e-09 | 2.5678e-09 | -1.0265e-07 | -1.0379e-07 | -1.0458e-10 | -2.6366e-09 | 2.7451e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.045129 | 1.6118 | 1.5797 | 0.045129 | 1.6118 | 1.5797 | -41.7048 | -148.0093 | 149.9266 | -41.7048 | -148.0093 | 149.9266
Line1_1_3 | 0.02608 | 0.025743 | 0.02568 | 0.02608 | 0.025744 | 0.02568 | 0.0060229 | 0.0059452 | 0.0059305 | 0.006023 | 0.0059453 | 0.0059306 | -0.00018896 | -0.0047529 | 0.0050169 | 0.00019555 | 0.0047593 | -0.0050106 | -0.00019537 | 0.0083204 | 0.0079117 | 0.00020224 | -0.0083139 | -0.0079052 | 92.3399 | 92.2541 | 92.3057 | -87.6601 | -87.7459 | -87.6943 |  | 0.045129 | 1.6118 | 1.5797 | 0.046709 | 1.6113 | 1.5782 | -41.7048 | -148.0093 | 149.9266 | -41.6962 | -147.9568 | 149.9377
Line2_1_4 | 0.20711 | 0.025875 | 0.02577 | 0.20711 | 0.025875 | 0.025771 | 0.047831 | 0.0059756 | 0.0059514 | 0.047831 | 0.0059757 | 0.0059515 | 0.001496 | -0.0048319 | 0.0050036 | -0.00077534 | 0.0048576 | -0.0049781 | 0.001556 | 0.0083315 | 0.0079591 | -0.00080555 | -0.0083047 | -0.0079325 | -87.8311 | 91.8789 | 92.0826 | 92.1689 | -88.1211 | -87.9174 |  | 0.045129 | 1.6118 | 1.5797 | 0.023375 | 1.61 | 1.5736 | -41.7048 | -148.0093 | 149.9266 | -41.7363 | -147.7969 | 149.9721
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4819e-09 | 1.3087e-07 | -1.1767e-07 | -2.1311e-09 | -7.0001e-08 | 5.4454e-08 | 5.1356e-09 | -2.0529e-07 | -2.0757e-07 | -2.6724e-09 | 1.0001e-07 | 1.0653e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.045129 | 1.6118 | 1.5797 | 0.045129 | 1.6118 | 1.5797 | -41.7048 | -148.0093 | 149.9266 | -41.7048 | -148.0093 | 149.9266
Line4_2_6 | 0.026146 | 0.025809 | 0.025745 | 0.026146 | 0.025809 | 0.025745 | 0.0060382 | 0.0059603 | 0.0059456 | 0.0060383 | 0.0059604 | 0.0059456 | -0.0001956 | -0.0047912 | 0.0050044 | 0.00020222 | 0.0047977 | -0.0049981 | -0.00020322 | 0.0083235 | 0.0079371 | 0.00021013 | -0.008317 | -0.0079306 | 92.2039 | 92.1176 | 92.1695 | -87.7961 | -87.8824 | -87.8305 |  | 0.046713 | 1.6113 | 1.5782 | 0.048297 | 1.6109 | 1.5767 | -41.7008 | -147.9566 | 149.9378 | -41.6971 | -147.9039 | 149.949
Line5_6_7 | 0.026146 | 0.025809 | 0.025745 | 0.026147 | 0.02581 | 0.025746 | 0.0060383 | 0.0059604 | 0.0059456 | 0.0060384 | 0.0059605 | 0.0059457 | -0.00020222 | -0.0047977 | 0.0049981 | 0.00020884 | 0.0048041 | -0.0049919 | -0.00021013 | 0.008317 | 0.0079306 | 0.00021704 | -0.0083105 | -0.0079241 | 92.2039 | 92.1175 | 92.1695 | -87.7961 | -87.8825 | -87.8305 |  | 0.048297 | 1.6109 | 1.5767 | 0.049881 | 1.6105 | 1.5751 | -41.6971 | -147.9039 | 149.949 | -41.6936 | -147.8511 | 149.9603
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4318e-09 | 1.9515e-07 | -1.7627e-07 | -4.8339e-09 | -1.3465e-07 | 1.1317e-07 | 8.4577e-09 | -3.067e-07 | -3.0878e-07 | -5.754e-09 | 2.0185e-07 | 2.0859e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.049881 | 1.6105 | 1.5751 | 0.049881 | 1.6105 | 1.5751 | -41.6936 | -147.8511 | 149.9603 | -41.6936 | -147.8511 | 149.9603
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4773e-09 | 6.5051e-08 | -5.8756e-08 | 1.2062e-10 | -4.5499e-09 | -4.3437e-09 | 2.8192e-09 | -1.0223e-07 | -1.0293e-07 | -1.1557e-10 | -2.6208e-09 | 2.7401e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.049881 | 1.6105 | 1.5751 | 0.049881 | 1.6105 | 1.5751 | -41.6936 | -147.8511 | 149.9603 | -41.6936 | -147.8511 | 149.9603
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4773e-09 | 6.5051e-08 | -5.8756e-08 | 1.2062e-10 | -4.5499e-09 | -4.3437e-09 | 2.8192e-09 | -1.0223e-07 | -1.0293e-07 | -1.1557e-10 | -2.6208e-09 | 2.7401e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.049881 | 1.6105 | 1.5751 | 0.049881 | 1.6105 | 1.5751 | -41.6936 | -147.8511 | 149.9603 | -41.6936 | -147.8511 | 149.9603
Line9_3_11 | 0.02608 | 0.025744 | 0.02568 | 0.02608 | 0.025744 | 0.025681 | 0.006023 | 0.0059453 | 0.0059306 | 0.006023 | 0.0059453 | 0.0059307 | -0.00019555 | -0.0047593 | 0.0050106 | 0.00020214 | 0.0047657 | -0.0050044 | -0.00020225 | 0.0083139 | 0.0079052 | 0.00020912 | -0.0083074 | -0.0078988 | 92.3399 | 92.2541 | 92.3056 | -87.6601 | -87.7459 | -87.6944 |  | 0.046709 | 1.6113 | 1.5782 | 0.048289 | 1.6109 | 1.5767 | -41.6962 | -147.9568 | 149.9377 | -41.6882 | -147.9042 | 149.9487

## LG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.02477 | 0.02445 | 0.02439 | 0.02477 | 0.024451 | 0.02439 | 0.0057203 | 0.0056465 | 0.0056326 | 0.0057204 | 0.0056466 | 0.0056326 | -0.00016961 | -0.0042944 | 0.0044971 | 0.00017555 | 0.0043002 | -0.0044915 | -0.00017619 | 0.0074763 | 0.0071294 | 0.00018239 | -0.0074704 | -0.0071236 | 92.2039 | 92.1176 | 92.1696 | -87.7961 | -87.8824 | -87.8304 |  | 0.042753 | 1.5269 | 1.4965 | 0.044254 | 1.5265 | 1.4951 | -41.7048 | -148.0093 | 149.9266 | -41.7008 | -147.9566 | 149.9378
Line10_11_12 | 0.024708 | 0.024389 | 0.024329 | 0.024708 | 0.024389 | 0.024329 | 0.005706 | 0.0056324 | 0.0056185 | 0.0057061 | 0.0056325 | 0.0056186 | -0.00018142 | -0.0042773 | 0.0044915 | 0.00018734 | 0.004283 | -0.0044859 | -0.00018768 | 0.007456 | 0.0070892 | 0.00019385 | -0.0074501 | -0.0070834 | 92.3398 | 92.2541 | 92.3056 | -87.6602 | -87.7459 | -87.6944 |  | 0.045747 | 1.5261 | 1.4937 | 0.047245 | 1.5257 | 1.4923 | -41.6882 | -147.9042 | 149.9487 | -41.6808 | -147.8516 | 149.9598
Line11_12_13 | 0.024708 | 0.024389 | 0.024329 | 0.024708 | 0.02439 | 0.02433 | 0.0057061 | 0.0056325 | 0.0056186 | 0.0057062 | 0.0056326 | 0.0056187 | -0.00018734 | -0.004283 | 0.0044859 | 0.00019325 | 0.0042888 | -0.0044803 | -0.00019385 | 0.0074501 | 0.0070834 | 0.00020002 | -0.0074443 | -0.0070776 | 92.3398 | 92.254 | 92.3056 | -87.6602 | -87.746 | -87.6944 |  | 0.047245 | 1.5257 | 1.4923 | 0.048742 | 1.5253 | 1.4908 | -41.6808 | -147.8516 | 149.9598 | -41.6737 | -147.799 | 149.9709
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8777e-09 | 1.7481e-07 | -1.5813e-07 | -4.4737e-09 | -1.2062e-07 | 1.0153e-07 | 7.814e-09 | -2.7489e-07 | -2.7637e-07 | -5.3163e-09 | 1.8092e-07 | 1.867e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.048742 | 1.5253 | 1.4908 | 0.048742 | 1.5253 | 1.4908 | -41.6737 | -147.799 | 149.9709 | -41.6737 | -147.799 | 149.9709
Line13_13_14 | 0.024709 | 0.024391 | 0.024331 | 0.02471 | 0.024391 | 0.024331 | 0.0057064 | 0.0056328 | 0.0056189 | 0.0057065 | 0.0056329 | 0.005619 | -0.00019326 | -0.004289 | 0.0044804 | 0.00019917 | 0.0042947 | -0.0044748 | -0.00020003 | 0.0074446 | 0.0070779 | 0.0002062 | -0.0074387 | -0.0070721 | 92.3397 | 92.2539 | 92.3054 | -87.6603 | -87.7461 | -87.6946 |  | 0.048742 | 1.5253 | 1.4908 | 0.050239 | 1.5249 | 1.4894 | -41.6737 | -147.799 | 149.9709 | -41.6671 | -147.7464 | 149.982
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5851e-09 | 1.1654e-07 | -1.0542e-07 | -2.1811e-09 | -6.2349e-08 | 4.8822e-08 | 5.2093e-09 | -1.8326e-07 | -1.8425e-07 | -2.7116e-09 | 8.9284e-08 | 9.458e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.048742 | 1.5253 | 1.4908 | 0.048742 | 1.5253 | 1.4908 | -41.6737 | -147.799 | 149.9709 | -41.6737 | -147.799 | 149.9709
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2926e-09 | 5.8271e-08 | -5.2709e-08 | 1.1143e-10 | -4.078e-09 | -3.8876e-09 | 2.6047e-09 | -9.1631e-08 | -9.2123e-08 | -1.0695e-10 | -2.3475e-09 | 2.4577e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.048742 | 1.5253 | 1.4908 | 0.048741 | 1.5253 | 1.4908 | -41.6737 | -147.799 | 149.9709 | -41.6737 | -147.799 | 149.9709
Line16_4_18 | 0.22136 | 0 | 0 | 0.22136 | 0 | 0 | 0.051121 | 0 | 0 | 0.051121 | 0 | 0 | 0.000784 | 5.9622e-08 | -5.2453e-08 | 3.7979e-15 | -4.0614e-09 | -3.8536e-09 | 0.00081667 | -9.2047e-08 | -9.3475e-08 | 6.3349e-16 | -2.333e-09 | 2.4531e-09 | -87.9055 | 0 | 0 | 92.0945 | 0 | 0 |  | 0.022145 | 1.5253 | 1.4908 | 0 | 1.5241 | 1.4864 | -41.7363 | -147.7969 | 149.9721 | 0 | -147.6369 | 150.0067
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0113e-09 | 5.8726e-08 | -5.2804e-08 | 9.863e-11 | -4.1002e-09 | -3.9317e-09 | 2.3046e-09 | -9.2125e-08 | -9.3149e-08 | -9.3864e-11 | -2.3663e-09 | 2.4638e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.042753 | 1.5269 | 1.4965 | 0.042753 | 1.5269 | 1.4965 | -41.7048 | -148.0093 | 149.9266 | -41.7048 | -148.0093 | 149.9266
Line1_1_3 | 0.024707 | 0.024389 | 0.024328 | 0.024708 | 0.024389 | 0.024329 | 0.0057059 | 0.0056323 | 0.0056184 | 0.005706 | 0.0056324 | 0.0056185 | -0.0001696 | -0.0042658 | 0.0045027 | 0.00017551 | 0.0042715 | -0.0044971 | -0.00017535 | 0.0074676 | 0.0071008 | 0.00018152 | -0.0074618 | -0.007095 | 92.3399 | 92.2541 | 92.3057 | -87.6601 | -87.7459 | -87.6943 |  | 0.042753 | 1.5269 | 1.4965 | 0.04425 | 1.5265 | 1.4951 | -41.7048 | -148.0093 | 149.9266 | -41.6962 | -147.9568 | 149.9377
Line2_1_4 | 0.19621 | 0.024513 | 0.024414 | 0.19621 | 0.024514 | 0.024414 | 0.045313 | 0.0056611 | 0.0056382 | 0.045313 | 0.0056612 | 0.0056383 | 0.0013427 | -0.0043366 | 0.0044907 | -0.00069587 | 0.0043597 | -0.0044679 | 0.0013965 | 0.0074776 | 0.0071433 | -0.00072299 | -0.0074535 | -0.0071195 | -87.8311 | 91.8789 | 92.0826 | 92.1689 | -88.1211 | -87.9174 |  | 0.042753 | 1.5269 | 1.4965 | 0.022145 | 1.5253 | 1.4908 | -41.7048 | -148.0093 | 149.9266 | -41.7363 | -147.7969 | 149.9721
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0226e-09 | 1.1745e-07 | -1.0561e-07 | -1.9127e-09 | -6.2827e-08 | 4.8873e-08 | 4.6092e-09 | -1.8425e-07 | -1.863e-07 | -2.3985e-09 | 8.9759e-08 | 9.5613e-08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.042753 | 1.5269 | 1.4965 | 0.042753 | 1.5269 | 1.4965 | -41.7048 | -148.0093 | 149.9266 | -41.7048 | -148.0093 | 149.9266
Line4_2_6 | 0.02477 | 0.024451 | 0.02439 | 0.02477 | 0.024451 | 0.02439 | 0.0057204 | 0.0056466 | 0.0056326 | 0.0057205 | 0.0056467 | 0.0056327 | -0.00017555 | -0.0043002 | 0.0044915 | 0.00018149 | 0.0043059 | -0.0044859 | -0.00018239 | 0.0074704 | 0.0071236 | 0.00018859 | -0.0074646 | -0.0071178 | 92.2039 | 92.1176 | 92.1695 | -87.7961 | -87.8824 | -87.8305 |  | 0.044254 | 1.5265 | 1.4951 | 0.045755 | 1.5261 | 1.4937 | -41.7008 | -147.9566 | 149.9378 | -41.6971 | -147.9039 | 149.949
Line5_6_7 | 0.02477 | 0.024451 | 0.02439 | 0.024771 | 0.024451 | 0.024391 | 0.0057205 | 0.0056467 | 0.0056327 | 0.0057205 | 0.0056467 | 0.0056328 | -0.00018149 | -0.004306 | 0.0044858 | 0.00018744 | 0.0043117 | -0.0044802 | -0.00018859 | 0.0074646 | 0.0071178 | 0.00019479 | -0.0074587 | -0.0071119 | 92.2039 | 92.1175 | 92.1695 | -87.7961 | -87.8825 | -87.8305 |  | 0.045755 | 1.5261 | 1.4937 | 0.047256 | 1.5257 | 1.4922 | -41.6971 | -147.9039 | 149.949 | -41.6936 | -147.8511 | 149.9603
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6701e-09 | 1.7515e-07 | -1.582e-07 | -4.3385e-09 | -1.2085e-07 | 1.0157e-07 | 7.5908e-09 | -2.7527e-07 | -2.7713e-07 | -5.1643e-09 | 1.8116e-07 | 1.8721e-07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.047256 | 1.5257 | 1.4922 | 0.047256 | 1.5257 | 1.4922 | -41.6936 | -147.8511 | 149.9603 | -41.6936 | -147.8511 | 149.9603
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2234e-09 | 5.8384e-08 | -5.2734e-08 | 1.0826e-10 | -4.0836e-09 | -3.8985e-09 | 2.5303e-09 | -9.1755e-08 | -9.2378e-08 | -1.0373e-10 | -2.3522e-09 | 2.4592e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.047256 | 1.5257 | 1.4922 | 0.047256 | 1.5257 | 1.4922 | -41.6936 | -147.8511 | 149.9603 | -41.6936 | -147.8511 | 149.9603
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2234e-09 | 5.8384e-08 | -5.2734e-08 | 1.0826e-10 | -4.0836e-09 | -3.8985e-09 | 2.5303e-09 | -9.1755e-08 | -9.2378e-08 | -1.0373e-10 | -2.3522e-09 | 2.4592e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.047256 | 1.5257 | 1.4922 | 0.047256 | 1.5257 | 1.4922 | -41.6936 | -147.8511 | 149.9603 | -41.6936 | -147.8511 | 149.9603
Line9_3_11 | 0.024708 | 0.024389 | 0.024329 | 0.024708 | 0.024389 | 0.024329 | 0.005706 | 0.0056324 | 0.0056185 | 0.005706 | 0.0056324 | 0.0056185 | -0.00017551 | -0.0042715 | 0.0044971 | 0.00018142 | 0.0042773 | -0.0044915 | -0.00018152 | 0.0074618 | 0.007095 | 0.00018768 | -0.007456 | -0.0070892 | 92.3399 | 92.2541 | 92.3056 | -87.6601 | -87.7459 | -87.6944 |  | 0.04425 | 1.5265 | 1.4951 | 0.045747 | 1.5261 | 1.4937 | -41.6962 | -147.9568 | 149.9377 | -41.6882 | -147.9042 | 149.9487

## LG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0031534 | 0.0031127 | 0.003105 | 0.0031535 | 0.0031128 | 0.0031051 | 0.00072825 | 0.00071886 | 0.00071708 | 0.00072826 | 0.00071887 | 0.00071709 | -0.00044793 | -0.0002299 | 0.00067034 | 0.00044803 | 0.00023 | -0.00067025 | -0.00044634 | 0.00072038 | -4.5374e-05 | 0.00044645 | -0.00072029 | 4.547e-05 | 130.3996 | 130.3133 | 130.3652 | -49.6004 | -49.6867 | -49.6348 |  | 0.86831 | 1.0519 | 0.93696 | 0.8685 | 1.0518 | 0.93684 | -4.7023 | -121.9869 | 126.4929 | -4.702 | -121.978 | 126.4842
Line10_11_12 | 0.0031455 | 0.003105 | 0.0030973 | 0.0031456 | 0.003105 | 0.0030973 | 0.00072643 | 0.00071706 | 0.00071529 | 0.00072644 | 0.00071707 | 0.0007153 | -0.00044806 | -0.0002278 | 0.00066838 | 0.00044816 | 0.00022789 | -0.00066829 | -0.00044436 | 0.00071893 | -4.7039e-05 | 0.00044447 | -0.00071885 | 4.7135e-05 | 130.5355 | 130.4497 | 130.5012 | -49.4645 | -49.5503 | -49.4988 |  | 0.86869 | 1.0517 | 0.93672 | 0.86888 | 1.0516 | 0.9366 | -4.7017 | -121.9691 | 126.4755 | -4.7013 | -121.9602 | 126.4668
Line11_12_13 | 0.0031456 | 0.003105 | 0.0030973 | 0.0031456 | 0.003105 | 0.0030974 | 0.00072644 | 0.00071707 | 0.0007153 | 0.00072645 | 0.00071708 | 0.00071531 | -0.00044816 | -0.00022789 | 0.00066829 | 0.00044826 | 0.00022799 | -0.00066821 | -0.00044447 | 0.00071885 | -4.7135e-05 | 0.00044457 | -0.00071876 | 4.723e-05 | 130.5355 | 130.4497 | 130.5012 | -49.4645 | -49.5503 | -49.4988 |  | 0.86888 | 1.0516 | 0.9366 | 0.86907 | 1.0516 | 0.93648 | -4.7013 | -121.9602 | 126.4668 | -4.701 | -121.9514 | 126.4581
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5987e-08 | 9.8286e-09 | -2.5455e-08 | -1.041e-08 | -6.9461e-09 | 1.6996e-08 | 1.74e-08 | -2.685e-08 | 6.599e-10 | -1.1848e-08 | 1.7775e-08 | -7.3021e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86907 | 1.0516 | 0.93648 | 0.86907 | 1.0516 | 0.93648 | -4.701 | -121.9514 | 126.4581 | -4.701 | -121.9514 | 126.4581
Line13_13_14 | 0.0031457 | 0.0031052 | 0.0030975 | 0.0031458 | 0.0031052 | 0.0030975 | 0.00072648 | 0.00071711 | 0.00071534 | 0.00072649 | 0.00071712 | 0.00071535 | -0.00044828 | -0.000228 | 0.00066823 | 0.00044838 | 0.00022809 | -0.00066815 | -0.00044459 | 0.00071879 | -4.7231e-05 | 0.0004447 | -0.0007187 | 4.7327e-05 | 130.5353 | 130.4496 | 130.5011 | -49.4647 | -49.5504 | -49.4989 |  | 0.86907 | 1.0516 | 0.93648 | 0.86926 | 1.0515 | 0.93636 | -4.701 | -121.9514 | 126.4581 | -4.7007 | -121.9425 | 126.4494
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0658e-08 | 6.5524e-09 | -1.697e-08 | -5.0813e-09 | -3.6699e-09 | 8.5107e-09 | 1.16e-08 | -1.79e-08 | 4.3993e-10 | -6.0481e-09 | 8.8253e-09 | 1.4694e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86907 | 1.0516 | 0.93648 | 0.86907 | 1.0516 | 0.93648 | -4.701 | -121.9514 | 126.4581 | -4.701 | -121.9514 | 126.4581
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.329e-09 | 3.2762e-09 | -8.4849e-09 | 2.4771e-10 | -3.9371e-10 | 2.5717e-11 | 5.8e-09 | -8.95e-09 | 2.1997e-10 | -2.481e-10 | -1.2473e-10 | 3.6691e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86907 | 1.0516 | 0.93648 | 0.86907 | 1.0516 | 0.93648 | -4.701 | -121.9514 | 126.4581 | -4.701 | -121.9514 | 126.4581
Line16_4_18 | 0.028181 | 0 | 0 | 0.028181 | 0 | 0 | 0.0065082 | 0 | 0 | 0.0065081 | 0 | 0 | 0.0039836 | 3.3839e-09 | -8.5708e-09 | -0.0039709 | -3.9251e-10 | 2.7147e-11 | 0.0039841 | -9.0111e-09 | 1.5087e-10 | -0.0039709 | -1.2294e-10 | 3.6525e-10 | -49.7098 | 0 | 0 | 130.2902 | 0 | 0 |  | 0.86568 | 1.0516 | 0.93647 | 0.86287 | 1.0513 | 0.93611 | -4.706 | -121.951 | 126.4578 | -4.7098 | -121.9239 | 126.4314
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3234e-09 | 3.331e-09 | -8.5328e-09 | 2.4991e-10 | -3.9529e-10 | 2.3881e-11 | 5.8493e-09 | -8.9842e-09 | 1.7537e-10 | -2.4795e-10 | -1.2704e-10 | 3.6906e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86831 | 1.0519 | 0.93696 | 0.86831 | 1.0519 | 0.93696 | -4.7023 | -121.9869 | 126.4929 | -4.7023 | -121.9869 | 126.4929
Line1_1_3 | 0.0031455 | 0.0031049 | 0.0030972 | 0.0031455 | 0.0031049 | 0.0030973 | 0.00072641 | 0.00071704 | 0.00071528 | 0.00072642 | 0.00071705 | 0.00071528 | -0.00044786 | -0.00022761 | 0.00066854 | 0.00044796 | 0.0002277 | -0.00066846 | -0.00044415 | 0.00071911 | -4.6848e-05 | 0.00044426 | -0.00071902 | 4.6944e-05 | 130.5356 | 130.4498 | 130.5013 | -49.4644 | -49.5502 | -49.4987 |  | 0.86831 | 1.0519 | 0.93696 | 0.8685 | 1.0518 | 0.93684 | -4.7023 | -121.9869 | 126.4929 | -4.702 | -121.978 | 126.4842
Line2_1_4 | 0.02498 | 0.0031208 | 0.0031081 | 0.02498 | 0.0031208 | 0.0031082 | 0.0057688 | 0.00072071 | 0.00071779 | 0.0057688 | 0.00072072 | 0.0007178 | 0.0035461 | -0.0002335 | 0.00067107 | -0.0035356 | 0.00023388 | -0.00067071 | 0.0035378 | 0.00072127 | -4.4401e-05 | -0.0035269 | -0.00072089 | 4.479e-05 | -49.6354 | 130.0746 | 130.2783 | 130.3646 | -49.9254 | -49.7217 |  | 0.86831 | 1.0519 | 0.93696 | 0.86568 | 1.0516 | 0.93647 | -4.7023 | -121.9869 | 126.4929 | -4.706 | -121.951 | 126.4578
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0647e-08 | 6.6619e-09 | -1.7066e-08 | -5.0734e-09 | -3.7263e-09 | 8.5567e-09 | 1.1699e-08 | -1.7968e-08 | 3.5073e-10 | -6.0972e-09 | 8.8571e-09 | 1.9369e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86831 | 1.0519 | 0.93696 | 0.86831 | 1.0519 | 0.93696 | -4.7023 | -121.9869 | 126.4929 | -4.7023 | -121.9869 | 126.4929
Line4_2_6 | 0.0031535 | 0.0031128 | 0.0031051 | 0.0031535 | 0.0031128 | 0.0031051 | 0.00072826 | 0.00071887 | 0.00071709 | 0.00072827 | 0.00071887 | 0.0007171 | -0.00044803 | -0.00023 | 0.00067025 | 0.00044813 | 0.00023009 | -0.00067017 | -0.00044645 | 0.00072029 | -4.547e-05 | 0.00044655 | -0.0007202 | 4.5566e-05 | 130.3995 | 130.3132 | 130.3652 | -49.6005 | -49.6868 | -49.6348 |  | 0.8685 | 1.0518 | 0.93684 | 0.86869 | 1.0517 | 0.93672 | -4.702 | -121.978 | 126.4842 | -4.7017 | -121.9691 | 126.4755
Line5_6_7 | 0.0031535 | 0.0031128 | 0.0031051 | 0.0031535 | 0.0031129 | 0.0031052 | 0.00072827 | 0.00071887 | 0.0007171 | 0.00072828 | 0.00071888 | 0.00071711 | -0.00044813 | -0.00023009 | 0.00067017 | 0.00044824 | 0.00023019 | -0.00067009 | -0.00044655 | 0.0007202 | -4.5566e-05 | 0.00044666 | -0.00072012 | 4.5662e-05 | 130.3995 | 130.3132 | 130.3651 | -49.6005 | -49.6868 | -49.6349 |  | 0.86869 | 1.0517 | 0.93672 | 0.86888 | 1.0516 | 0.9366 | -4.7017 | -121.9691 | 126.4755 | -4.7014 | -121.9601 | 126.4668
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5983e-08 | 9.8692e-09 | -2.5491e-08 | -1.0407e-08 | -6.9736e-09 | 1.7019e-08 | 1.7437e-08 | -2.6876e-08 | 6.2694e-10 | -1.1873e-08 | 1.7792e-08 | -5.0511e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86888 | 1.0516 | 0.9366 | 0.86888 | 1.0516 | 0.9366 | -4.7014 | -121.9601 | 126.4668 | -4.7014 | -121.9601 | 126.4668
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3277e-09 | 3.2897e-09 | -8.4969e-09 | 2.4825e-10 | -3.941e-10 | 2.5265e-11 | 5.8122e-09 | -8.9586e-09 | 2.0898e-10 | -2.4807e-10 | -1.253e-10 | 3.6745e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86888 | 1.0516 | 0.9366 | 0.86888 | 1.0516 | 0.9366 | -4.7014 | -121.9601 | 126.4668 | -4.7014 | -121.9601 | 126.4668
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3277e-09 | 3.2897e-09 | -8.4969e-09 | 2.4825e-10 | -3.941e-10 | 2.5265e-11 | 5.8122e-09 | -8.9586e-09 | 2.0898e-10 | -2.4807e-10 | -1.253e-10 | 3.6745e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.86888 | 1.0516 | 0.9366 | 0.86888 | 1.0516 | 0.9366 | -4.7014 | -121.9601 | 126.4668 | -4.7014 | -121.9601 | 126.4668
Line9_3_11 | 0.0031455 | 0.0031049 | 0.0030973 | 0.0031455 | 0.003105 | 0.0030973 | 0.00072642 | 0.00071705 | 0.00071528 | 0.00072643 | 0.00071706 | 0.00071529 | -0.00044796 | -0.0002277 | 0.00066846 | 0.00044806 | 0.0002278 | -0.00066838 | -0.00044426 | 0.00071902 | -4.6943e-05 | 0.00044436 | -0.00071893 | 4.7039e-05 | 130.5355 | 130.4498 | 130.5013 | -49.4645 | -49.5502 | -49.4987 |  | 0.8685 | 1.0518 | 0.93684 | 0.86869 | 1.0517 | 0.93672 | -4.702 | -121.978 | 126.4842 | -4.7017 | -121.9691 | 126.4755

## LG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0029875 | 0.0029489 | 0.0029416 | 0.0029875 | 0.0029489 | 0.0029417 | 0.00068992 | 0.00068102 | 0.00067934 | 0.00068993 | 0.00068103 | 0.00067935 | -0.00040202 | -0.00020634 | 0.00060163 | 0.00040211 | 0.00020642 | -0.00060156 | -0.00040059 | 0.00064655 | -4.0723e-05 | 0.00040069 | -0.00064647 | 4.081e-05 | 130.3996 | 130.3133 | 130.3652 | -49.6004 | -49.6867 | -49.6348 |  | 0.82261 | 0.99655 | 0.88764 | 0.82279 | 0.99647 | 0.88753 | -4.7023 | -121.9869 | 126.4929 | -4.702 | -121.978 | 126.4842
Line10_11_12 | 0.00298 | 0.0029415 | 0.0029343 | 0.00298 | 0.0029416 | 0.0029343 | 0.0006882 | 0.00067932 | 0.00067765 | 0.00068821 | 0.00067933 | 0.00067765 | -0.00040213 | -0.00020445 | 0.00059987 | 0.00040223 | 0.00020454 | -0.0005998 | -0.00039882 | 0.00064525 | -4.2218e-05 | 0.00039891 | -0.00064517 | 4.2304e-05 | 130.5355 | 130.4497 | 130.5012 | -49.4645 | -49.5503 | -49.4988 |  | 0.82297 | 0.99638 | 0.88742 | 0.82315 | 0.9963 | 0.88731 | -4.7017 | -121.9691 | 126.4755 | -4.7013 | -121.9602 | 126.4668
Line11_12_13 | 0.00298 | 0.0029416 | 0.0029343 | 0.0029801 | 0.0029416 | 0.0029344 | 0.00068821 | 0.00067933 | 0.00067765 | 0.00068821 | 0.00067934 | 0.00067766 | -0.00040223 | -0.00020454 | 0.0005998 | 0.00040232 | 0.00020462 | -0.00059972 | -0.00039891 | 0.00064517 | -4.2304e-05 | 0.00039901 | -0.00064509 | 4.239e-05 | 130.5355 | 130.4497 | 130.5012 | -49.4645 | -49.5503 | -49.4988 |  | 0.82315 | 0.9963 | 0.88731 | 0.82333 | 0.99621 | 0.88719 | -4.7013 | -121.9602 | 126.4668 | -4.701 | -121.9514 | 126.4581
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4349e-08 | 8.8212e-09 | -2.2846e-08 | -9.3434e-09 | -6.2342e-09 | 1.5254e-08 | 1.5617e-08 | -2.4098e-08 | 5.9226e-10 | -1.0634e-08 | 1.5953e-08 | -6.5537e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82333 | 0.99621 | 0.88719 | 0.82333 | 0.99621 | 0.88719 | -4.701 | -121.9514 | 126.4581 | -4.701 | -121.9514 | 126.4581
Line13_13_14 | 0.0029802 | 0.0029417 | 0.0029345 | 0.0029802 | 0.0029418 | 0.0029345 | 0.00068824 | 0.00067936 | 0.00067769 | 0.00068825 | 0.00067937 | 0.0006777 | -0.00040233 | -0.00020463 | 0.00059975 | 0.00040242 | 0.00020472 | -0.00059967 | -0.00039902 | 0.00064511 | -4.239e-05 | 0.00039912 | -0.00064504 | 4.2476e-05 | 130.5353 | 130.4496 | 130.5011 | -49.4647 | -49.5504 | -49.4989 |  | 0.82333 | 0.99621 | 0.88719 | 0.82351 | 0.99613 | 0.88708 | -4.701 | -121.9514 | 126.4581 | -4.7007 | -121.9425 | 126.4494
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5657e-09 | 5.8808e-09 | -1.5231e-08 | -4.5605e-09 | -3.2938e-09 | 7.6384e-09 | 1.0411e-08 | -1.6065e-08 | 3.9484e-10 | -5.4282e-09 | 7.9208e-09 | 1.3188e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82333 | 0.99621 | 0.88719 | 0.82333 | 0.99621 | 0.88719 | -4.701 | -121.9514 | 126.4581 | -4.701 | -121.9514 | 126.4581
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7828e-09 | 2.9404e-09 | -7.6153e-09 | 2.2232e-10 | -3.5335e-10 | 2.3081e-11 | 5.2056e-09 | -8.0327e-09 | 1.9742e-10 | -2.2267e-10 | -1.1194e-10 | 3.293e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82333 | 0.99621 | 0.88719 | 0.82333 | 0.99621 | 0.88719 | -4.701 | -121.9514 | 126.4581 | -4.701 | -121.9514 | 126.4581
Line16_4_18 | 0.026698 | 0 | 0 | 0.026698 | 0 | 0 | 0.0061656 | 0 | 0 | 0.0061656 | 0 | 0 | 0.0035753 | 3.0371e-09 | -7.6923e-09 | -0.0035639 | -3.5228e-10 | 2.4364e-11 | 0.0035758 | -8.0875e-09 | 1.3541e-10 | -0.0035639 | -1.1034e-10 | 3.2781e-10 | -49.7098 | 0 | 0 | 130.2902 | 0 | 0 |  | 0.82012 | 0.99621 | 0.88719 | 0.81745 | 0.99596 | 0.88684 | -4.706 | -121.951 | 126.4578 | -4.7098 | -121.9239 | 126.4314
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7777e-09 | 2.9896e-09 | -7.6583e-09 | 2.243e-10 | -3.5477e-10 | 2.1433e-11 | 5.2498e-09 | -8.0634e-09 | 1.5739e-10 | -2.2254e-10 | -1.1402e-10 | 3.3124e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82261 | 0.99655 | 0.88764 | 0.82261 | 0.99655 | 0.88764 | -4.7023 | -121.9869 | 126.4929 | -4.7023 | -121.9869 | 126.4929
Line1_1_3 | 0.0029799 | 0.0029415 | 0.0029342 | 0.0029799 | 0.0029415 | 0.0029343 | 0.00068818 | 0.0006793 | 0.00067763 | 0.00068819 | 0.00067931 | 0.00067764 | -0.00040195 | -0.00020428 | 0.00060002 | 0.00040204 | 0.00020436 | -0.00059995 | -0.00039863 | 0.0006454 | -4.2046e-05 | 0.00039872 | -0.00064533 | 4.2132e-05 | 130.5356 | 130.4498 | 130.5013 | -49.4644 | -49.5502 | -49.4987 |  | 0.82261 | 0.99655 | 0.88764 | 0.82279 | 0.99647 | 0.88753 | -4.7023 | -121.9869 | 126.4929 | -4.702 | -121.978 | 126.4842
Line2_1_4 | 0.023665 | 0.0029565 | 0.0029446 | 0.023665 | 0.0029565 | 0.0029446 | 0.0054652 | 0.00068278 | 0.00068002 | 0.0054652 | 0.00068279 | 0.00068002 | 0.0031826 | -0.00020957 | 0.00060229 | -0.0031732 | 0.0002099 | -0.00060197 | 0.0031752 | 0.00064734 | -3.985e-05 | -0.0031654 | -0.000647 | 4.0199e-05 | -49.6354 | 130.0746 | 130.2783 | 130.3646 | -49.9254 | -49.7217 |  | 0.82261 | 0.99655 | 0.88764 | 0.82012 | 0.99621 | 0.88719 | -4.7023 | -121.9869 | 126.4929 | -4.706 | -121.951 | 126.4578
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5555e-09 | 5.9791e-09 | -1.5317e-08 | -4.5535e-09 | -3.3443e-09 | 7.6797e-09 | 1.05e-08 | -1.6127e-08 | 3.1479e-10 | -5.4723e-09 | 7.9493e-09 | 1.7384e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82261 | 0.99655 | 0.88764 | 0.82261 | 0.99655 | 0.88764 | -4.7023 | -121.9869 | 126.4929 | -4.7023 | -121.9869 | 126.4929
Line4_2_6 | 0.0029875 | 0.0029489 | 0.0029417 | 0.0029875 | 0.002949 | 0.0029417 | 0.00068993 | 0.00068103 | 0.00067935 | 0.00068994 | 0.00068104 | 0.00067935 | -0.00040211 | -0.00020642 | 0.00060156 | 0.0004022 | 0.00020651 | -0.00060148 | -0.00040069 | 0.00064647 | -4.0809e-05 | 0.00040078 | -0.00064639 | 4.0896e-05 | 130.3995 | 130.3132 | 130.3652 | -49.6005 | -49.6868 | -49.6348 |  | 0.82279 | 0.99647 | 0.88753 | 0.82297 | 0.99638 | 0.88742 | -4.702 | -121.978 | 126.4842 | -4.7017 | -121.9691 | 126.4755
Line5_6_7 | 0.0029875 | 0.002949 | 0.0029417 | 0.0029876 | 0.002949 | 0.0029417 | 0.00068994 | 0.00068104 | 0.00067935 | 0.00068995 | 0.00068105 | 0.00067936 | -0.0004022 | -0.00020651 | 0.00060148 | 0.00040229 | 0.0002066 | -0.00060141 | -0.00040078 | 0.00064639 | -4.0896e-05 | 0.00040088 | -0.00064631 | 4.0982e-05 | 130.3995 | 130.3132 | 130.3651 | -49.6005 | -49.6868 | -49.6349 |  | 0.82297 | 0.99638 | 0.88742 | 0.82315 | 0.9963 | 0.8873 | -4.7017 | -121.9691 | 126.4755 | -4.7014 | -121.9601 | 126.4668
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4345e-08 | 8.8577e-09 | -2.2878e-08 | -9.3405e-09 | -6.2588e-09 | 1.5275e-08 | 1.565e-08 | -2.4121e-08 | 5.6268e-10 | -1.0656e-08 | 1.5968e-08 | -4.5334e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82315 | 0.9963 | 0.8873 | 0.82315 | 0.9963 | 0.8873 | -4.7014 | -121.9601 | 126.4668 | -4.7014 | -121.9601 | 126.4668
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7817e-09 | 2.9526e-09 | -7.626e-09 | 2.2281e-10 | -3.5371e-10 | 2.2675e-11 | 5.2165e-09 | -8.0404e-09 | 1.8756e-10 | -2.2265e-10 | -1.1246e-10 | 3.2979e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82315 | 0.9963 | 0.8873 | 0.82315 | 0.9963 | 0.8873 | -4.7014 | -121.9601 | 126.4668 | -4.7014 | -121.9601 | 126.4668
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7817e-09 | 2.9526e-09 | -7.626e-09 | 2.2281e-10 | -3.5371e-10 | 2.2675e-11 | 5.2165e-09 | -8.0404e-09 | 1.8756e-10 | -2.2265e-10 | -1.1246e-10 | 3.2979e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.82315 | 0.9963 | 0.8873 | 0.82315 | 0.9963 | 0.8873 | -4.7014 | -121.9601 | 126.4668 | -4.7014 | -121.9601 | 126.4668
Line9_3_11 | 0.0029799 | 0.0029415 | 0.0029343 | 0.00298 | 0.0029415 | 0.0029343 | 0.00068819 | 0.00067931 | 0.00067764 | 0.0006882 | 0.00067932 | 0.00067765 | -0.00040204 | -0.00020436 | 0.00059995 | 0.00040213 | 0.00020445 | -0.00059987 | -0.00039872 | 0.00064533 | -4.2132e-05 | 0.00039882 | -0.00064525 | 4.2218e-05 | 130.5355 | 130.4498 | 130.5013 | -49.4645 | -49.5502 | -49.4987 |  | 0.82279 | 0.99647 | 0.88753 | 0.82297 | 0.99638 | 0.88742 | -4.702 | -121.978 | 126.4842 | -4.7017 | -121.9691 | 126.4755

## LLG_max_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.19197 | 0.5129 | 0.55737 | 0.19197 | 0.5129 | 0.55737 | 0.044333 | 0.11845 | 0.12872 | 0.044333 | 0.11845 | 0.12872 | 0.0099756 | 0.027243 | -0.083559 | -0.009944 | -0.026437 | 0.086786 | 0.057142 | -0.07313 | -0.038851 | -0.057121 | 0.077321 | 0.042768 | -77.8128 | -43.3904 | -106.0008 | 102.1872 | 136.6096 | 73.9992 |  | 1.3084 | 0.65885 | 0.7159 | 1.3078 | 0.68989 | 0.75165 | 2.2845 | -112.9588 | 98.9354 | 2.3118 | -114.5144 | 100.2336
Line10_11_12 | 0.17724 | 0.46435 | 0.49764 | 0.17724 | 0.46435 | 0.49764 | 0.040933 | 0.10724 | 0.11492 | 0.040933 | 0.10724 | 0.11492 | 0.013395 | 0.02191 | -0.080777 | -0.013387 | -0.021233 | 0.083367 | 0.051767 | -0.073533 | -0.038668 | -0.051725 | 0.076943 | 0.041768 | -73.2141 | -42.1826 | -104.3093 | 106.7859 | 137.8174 | 75.6908 |  | 1.3063 | 0.71549 | 0.77925 | 1.3053 | 0.74432 | 0.81136 | 2.2785 | -115.591 | 101.2716 | 2.2755 | -116.7557 | 102.302
Line11_12_13 | 0.17724 | 0.46435 | 0.49764 | 0.17724 | 0.46435 | 0.49764 | 0.040933 | 0.10724 | 0.11492 | 0.040933 | 0.10724 | 0.11492 | 0.013387 | 0.021233 | -0.083367 | -0.013379 | -0.020556 | 0.085958 | 0.051725 | -0.076943 | -0.041768 | -0.051683 | 0.080353 | 0.044867 | -73.2141 | -42.1826 | -104.3092 | 106.7859 | 137.8174 | 75.6908 |  | 1.3053 | 0.74432 | 0.81136 | 1.3042 | 0.77342 | 0.84371 | 2.2755 | -116.7557 | 102.302 | 2.2724 | -117.8331 | 103.2536
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3732e-08 | -3.9527e-08 | 5.307e-08 | 7.9347e-09 | 2.7134e-08 | -3.488e-08 | -8.3156e-08 | 3.3141e-08 | 1.9368e-09 | 5.5636e-08 | -2.1981e-08 | -2.2271e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3042 | 0.77342 | 0.84371 | 1.3042 | 0.77342 | 0.84371 | 2.2724 | -117.8331 | 103.2536 | 2.2724 | -117.8331 | 103.2536
Line13_13_14 | 0.17724 | 0.46435 | 0.49764 | 0.17724 | 0.46435 | 0.49764 | 0.040933 | 0.10724 | 0.11492 | 0.040933 | 0.10724 | 0.11492 | 0.013379 | 0.020556 | -0.085958 | -0.013371 | -0.019879 | 0.088548 | 0.051683 | -0.080353 | -0.044867 | -0.051641 | 0.083763 | 0.047966 | -73.2141 | -42.1827 | -104.3092 | 106.7859 | 137.8173 | 75.6908 |  | 1.3042 | 0.77342 | 0.84371 | 1.3032 | 0.80278 | 0.87627 | 2.2724 | -117.8331 | 103.2536 | 2.2694 | -118.8321 | 104.1348
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.1545e-09 | -2.6351e-08 | 3.538e-08 | 3.3574e-09 | 1.3958e-08 | -1.719e-08 | -5.5437e-08 | 2.2094e-08 | 1.2912e-09 | 2.7918e-08 | -1.0934e-08 | -1.5815e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3042 | 0.77342 | 0.84371 | 1.3042 | 0.77342 | 0.84371 | 2.2724 | -117.8331 | 103.2536 | 2.2724 | -117.8331 | 103.2536
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5773e-09 | -1.3176e-08 | 1.769e-08 | -1.2198e-09 | 7.8221e-10 | 5.0043e-10 | -2.7719e-08 | 1.1047e-08 | 6.456e-10 | 1.991e-10 | 1.1259e-10 | -9.3594e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3042 | 0.77342 | 0.84371 | 1.3042 | 0.77342 | 0.84371 | 2.2724 | -117.8331 | 103.2536 | 2.2724 | -117.8331 | 103.2536
Line16_4_18 | 0 | 3.8608 | 4.319 | 0 | 3.8608 | 4.319 | 0 | 0.89161 | 0.99743 | 0 | 0.89161 | 0.99743 | -8.3872e-10 | 0.098591 | 0.21611 | -7.1085e-10 | 7.9389e-14 | 3.4093e-14 | -4.005e-08 | 0.30504 | 0.32437 | 3.3634e-10 | 8.936e-15 | 9.9657e-15 | 0 | 172.8679 | 43.7836 | 0 | -7.1321 | -136.2164 |  | 1.2619 | 0.35955 | 0.39077 | 1.2078 | 0 | 0 | 3.2992 | -115.0432 | 100.1095 | 4.148 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9634e-09 | -1.5741e-08 | 1.8329e-08 | -1.2437e-09 | 9.258e-10 | 6.9283e-10 | -3.4711e-08 | 9.0162e-09 | 8.9117e-10 | 2.008e-10 | 3.1094e-10 | -9.9063e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3084 | 0.65885 | 0.7159 | 1.3084 | 0.65885 | 0.7159 | 2.2845 | -112.9588 | 98.9354 | 2.2845 | -112.9588 | 98.9354
Line1_1_3 | 0.17724 | 0.46435 | 0.49764 | 0.17724 | 0.46435 | 0.49764 | 0.040933 | 0.10724 | 0.11492 | 0.040933 | 0.10724 | 0.11492 | 0.013411 | 0.023263 | -0.075596 | -0.013403 | -0.022586 | 0.078186 | 0.05185 | -0.066714 | -0.03247 | -0.051808 | 0.070124 | 0.035569 | -73.2141 | -42.1826 | -104.3093 | 106.7859 | 137.8174 | 75.6907 |  | 1.3084 | 0.65885 | 0.7159 | 1.3074 | 0.68699 | 0.74742 | 2.2845 | -112.9588 | 98.9354 | 2.2815 | -114.3291 | 100.153
Line2_1_4 | 0.20252 | 3.1676 | 3.4926 | 0.20252 | 3.1676 | 3.4926 | 0.04677 | 0.73154 | 0.80658 | 0.04677 | 0.73154 | 0.80658 | -0.019853 | 0.18652 | 0.2939 | 0.020133 | -0.11055 | -0.15483 | 0.057884 | 0.44442 | 0.49703 | -0.055478 | -0.23867 | -0.27454 | -106.647 | 179.8094 | 39.5316 | 73.3531 | -0.19062 | -140.4684 |  | 1.3084 | 0.65885 | 0.7159 | 1.2619 | 0.35955 | 0.39077 | 2.2845 | -112.9588 | 98.9354 | 3.2992 | -115.0432 | 100.1095
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.9268e-09 | -3.1481e-08 | 3.6658e-08 | 1.7197e-09 | 1.6666e-08 | -1.7636e-08 | -6.9423e-08 | 1.8032e-08 | 1.7823e-09 | 3.4912e-08 | -8.7053e-09 | -1.8818e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3084 | 0.65885 | 0.7159 | 1.3084 | 0.65885 | 0.7159 | 2.2845 | -112.9588 | 98.9354 | 2.2845 | -112.9588 | 98.9354
Line4_2_6 | 0.19197 | 0.5129 | 0.55737 | 0.19197 | 0.5129 | 0.55737 | 0.044333 | 0.11845 | 0.12872 | 0.044333 | 0.11845 | 0.12872 | 0.009944 | 0.026437 | -0.086786 | -0.0099124 | -0.025631 | 0.090013 | 0.057121 | -0.077321 | -0.042768 | -0.057101 | 0.081512 | 0.046686 | -77.8128 | -43.3904 | -106.0008 | 102.1872 | 136.6096 | 73.9993 |  | 1.3078 | 0.68989 | 0.75165 | 1.3073 | 0.72139 | 0.78776 | 2.3118 | -114.5144 | 100.2336 | 2.3391 | -115.9351 | 101.4133
Line5_6_7 | 0.19197 | 0.5129 | 0.55737 | 0.19197 | 0.5129 | 0.55737 | 0.044333 | 0.11845 | 0.12872 | 0.044333 | 0.11845 | 0.12872 | 0.0099124 | 0.025631 | -0.090013 | -0.0098808 | -0.024825 | 0.09324 | 0.057101 | -0.081512 | -0.046686 | -0.05708 | 0.085703 | 0.050604 | -77.8128 | -43.3904 | -106.0007 | 102.1872 | 136.6096 | 73.9993 |  | 1.3073 | 0.72139 | 0.78776 | 1.3067 | 0.75329 | 0.82418 | 2.3391 | -115.9351 | 101.4133 | 2.3664 | -117.2363 | 102.4891
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3416e-08 | -4.0905e-08 | 5.3969e-08 | 7.7102e-09 | 2.8086e-08 | -3.5444e-08 | -8.707e-08 | 3.2779e-08 | 1.8183e-09 | 5.8254e-08 | -2.1713e-08 | -2.1669e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3067 | 0.75329 | 0.82418 | 1.3067 | 0.75329 | 0.82418 | 2.3664 | -117.2363 | 102.4891 | 2.3664 | -117.2363 | 102.4891
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4721e-09 | -1.3635e-08 | 1.799e-08 | -1.234e-09 | 8.1615e-10 | 5.3539e-10 | -2.9023e-08 | 1.0926e-08 | 6.0609e-10 | 2.0771e-10 | 1.3984e-10 | -9.5474e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3067 | 0.75329 | 0.82418 | 1.3067 | 0.75329 | 0.82418 | 2.3664 | -117.2363 | 102.4891 | 2.3664 | -117.2363 | 102.4891
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4721e-09 | -1.3635e-08 | 1.799e-08 | -1.234e-09 | 8.1615e-10 | 5.3539e-10 | -2.9023e-08 | 1.0926e-08 | 6.0609e-10 | 2.0771e-10 | 1.3984e-10 | -9.5474e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3067 | 0.75329 | 0.82418 | 1.3067 | 0.75329 | 0.82418 | 2.3664 | -117.2363 | 102.4891 | 2.3664 | -117.2363 | 102.4891
Line9_3_11 | 0.17724 | 0.46435 | 0.49764 | 0.17724 | 0.46435 | 0.49764 | 0.040933 | 0.10724 | 0.11492 | 0.040933 | 0.10724 | 0.11492 | 0.013403 | 0.022586 | -0.078186 | -0.013395 | -0.02191 | 0.080777 | 0.051808 | -0.070124 | -0.035569 | -0.051767 | 0.073533 | 0.038668 | -73.2141 | -42.1826 | -104.3093 | 106.7859 | 137.8174 | 75.6907 |  | 1.3074 | 0.68699 | 0.74742 | 1.3063 | 0.71549 | 0.77925 | 2.2815 | -114.3291 | 100.153 | 2.2785 | -115.591 | 101.2716

## LLG_max_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.1969 | 0.52329 | 0.57076 | 0.1969 | 0.52329 | 0.57076 | 0.045472 | 0.12085 | 0.13181 | 0.045472 | 0.12085 | 0.13181 | 0.0098437 | 0.028576 | -0.088294 | -0.0098023 | -0.027746 | 0.09168 | 0.061683 | -0.077064 | -0.041052 | -0.061661 | 0.08144 | 0.045168 | -78.6429 | -43.3035 | -106.3944 | 101.3571 | 136.6964 | 73.6056 |  | 1.3737 | 0.68012 | 0.73871 | 1.373 | 0.71194 | 0.77537 | 2.29 | -112.9582 | 98.5415 | 2.3243 | -114.49 | 99.8338
Line10_11_12 | 0.18229 | 0.47553 | 0.51176 | 0.18229 | 0.47553 | 0.51176 | 0.042098 | 0.10982 | 0.11819 | 0.042098 | 0.10982 | 0.11819 | 0.013512 | 0.023127 | -0.08567 | -0.013496 | -0.022425 | 0.088411 | 0.056133 | -0.077721 | -0.041094 | -0.05609 | 0.081308 | 0.044379 | -74.1659 | -42.1321 | -104.7523 | 105.8341 | 137.8679 | 75.2477 |  | 1.3715 | 0.73839 | 0.80396 | 1.3704 | 0.76804 | 0.83703 | 2.2998 | -115.5609 | 100.8738 | 2.3047 | -116.713 | 101.9028
Line11_12_13 | 0.18229 | 0.47553 | 0.51176 | 0.18229 | 0.47553 | 0.51176 | 0.042098 | 0.10982 | 0.11819 | 0.042098 | 0.10982 | 0.11819 | 0.013496 | 0.022425 | -0.088411 | -0.013481 | -0.021723 | 0.091151 | 0.05609 | -0.081308 | -0.044379 | -0.056046 | 0.084896 | 0.047664 | -74.1659 | -42.1321 | -104.7523 | 105.8341 | 137.8679 | 75.2477 |  | 1.3704 | 0.76804 | 0.83703 | 1.3693 | 0.79797 | 0.87034 | 2.3047 | -116.713 | 101.9028 | 2.3097 | -117.7791 | 102.8533
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4882e-08 | -4.3957e-08 | 5.8534e-08 | 8.5646e-09 | 3.0186e-08 | -3.8446e-08 | -9.3581e-08 | 3.6327e-08 | 2.0691e-09 | 6.261e-08 | -2.4094e-08 | -2.4143e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3693 | 0.79797 | 0.87034 | 1.3693 | 0.79797 | 0.87034 | 2.3097 | -117.7791 | 102.8533 | 2.3097 | -117.7791 | 102.8533
Line13_13_14 | 0.18229 | 0.47553 | 0.51176 | 0.18229 | 0.47553 | 0.51176 | 0.042099 | 0.10982 | 0.11819 | 0.042099 | 0.10982 | 0.11819 | 0.013481 | 0.021723 | -0.091151 | -0.013465 | -0.021022 | 0.093892 | 0.056046 | -0.084896 | -0.047664 | -0.056002 | 0.088483 | 0.050949 | -74.1659 | -42.1321 | -104.7523 | 105.8341 | 137.8679 | 75.2477 |  | 1.3693 | 0.79797 | 0.87034 | 1.3682 | 0.82815 | 0.90387 | 2.3097 | -117.7791 | 102.8533 | 2.3147 | -118.7677 | 103.7334
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.9211e-09 | -2.9305e-08 | 3.9022e-08 | 3.6041e-09 | 1.5534e-08 | -1.8934e-08 | -6.2387e-08 | 2.4218e-08 | 1.3794e-09 | 3.1416e-08 | -1.1984e-08 | -1.7246e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3693 | 0.79797 | 0.87034 | 1.3693 | 0.79797 | 0.87034 | 2.3097 | -117.7791 | 102.8533 | 2.3097 | -117.7791 | 102.8533
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9605e-09 | -1.4652e-08 | 1.9511e-08 | -1.3564e-09 | 8.813e-10 | 5.7688e-10 | -3.1194e-08 | 1.2109e-08 | 6.8969e-10 | 2.2257e-10 | 1.2473e-10 | -1.0349e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3693 | 0.79797 | 0.87034 | 1.3693 | 0.79797 | 0.87034 | 2.3097 | -117.7791 | 102.8533 | 2.3097 | -117.7791 | 102.8533
Line16_4_18 | 0 | 3.9717 | 4.4421 | 0 | 3.9717 | 4.4421 | 0 | 0.91723 | 1.0259 | 0 | 0.91723 | 1.0259 | -8.6577e-10 | 0.10497 | 0.22847 | -8.1051e-10 | 1.3283e-13 | 9.4074e-14 | -4.4397e-08 | 0.32309 | 0.3438 | 3.6787e-10 | -4.4839e-14 | -3.7363e-14 | 0 | 173.0002 | 43.3189 | 0 | -6.9998 | -136.6811 |  | 1.3261 | 0.37037 | 0.40238 | 1.2711 | 0 | 0 | 3.2843 | -114.9984 | 99.7124 | 4.1149 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1889e-09 | -1.7293e-08 | 2.0066e-08 | -1.3828e-09 | 1.0264e-09 | 7.7205e-10 | -3.8701e-08 | 9.8373e-09 | 8.9944e-10 | 2.2138e-10 | 3.3629e-10 | -1.09e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3737 | 0.68012 | 0.73871 | 1.3737 | 0.68012 | 0.73871 | 2.29 | -112.9582 | 98.5415 | 2.29 | -112.9582 | 98.5415
Line1_1_3 | 0.18229 | 0.47553 | 0.51176 | 0.18229 | 0.47553 | 0.51176 | 0.042098 | 0.10982 | 0.11819 | 0.042098 | 0.10982 | 0.11819 | 0.013543 | 0.024531 | -0.080189 | -0.013528 | -0.023829 | 0.082929 | 0.05622 | -0.070546 | -0.034524 | -0.056177 | 0.074133 | 0.037809 | -74.1659 | -42.1321 | -104.7523 | 105.8341 | 137.8679 | 75.2477 |  | 1.3737 | 0.68012 | 0.73871 | 1.3726 | 0.70907 | 0.77118 | 2.29 | -112.9582 | 98.5415 | 2.2949 | -114.313 | 99.757
Line2_1_4 | 0.20721 | 3.275 | 3.6111 | 0.20721 | 3.275 | 3.6111 | 0.047853 | 0.75633 | 0.83394 | 0.047853 | 0.75633 | 0.83394 | -0.021039 | 0.19908 | 0.3131 | 0.02135 | -0.11754 | -0.16461 | 0.062275 | 0.47431 | 0.53055 | -0.059757 | -0.25427 | -0.29242 | -106.3769 | 179.8105 | 39.0881 | 73.6231 | -0.18947 | -140.9119 |  | 1.3737 | 0.68012 | 0.73871 | 1.3261 | 0.37037 | 0.40238 | 2.29 | -112.9582 | 98.5415 | 3.2843 | -114.9984 | 99.7124
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.3777e-09 | -3.4585e-08 | 4.0132e-08 | 1.8061e-09 | 1.8319e-08 | -1.9294e-08 | -7.7402e-08 | 1.9675e-08 | 1.7989e-09 | 3.8922e-08 | -9.501e-09 | -1.9894e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3737 | 0.68012 | 0.73871 | 1.3737 | 0.68012 | 0.73871 | 2.29 | -112.9582 | 98.5415 | 2.29 | -112.9582 | 98.5415
Line4_2_6 | 0.1969 | 0.52329 | 0.57076 | 0.1969 | 0.52329 | 0.57076 | 0.045472 | 0.12085 | 0.13181 | 0.045472 | 0.12085 | 0.13181 | 0.0098023 | 0.027746 | -0.09168 | -0.0097608 | -0.026916 | 0.095066 | 0.061661 | -0.08144 | -0.045168 | -0.061638 | 0.085817 | 0.049284 | -78.6429 | -43.3036 | -106.3944 | 101.3571 | 136.6964 | 73.6056 |  | 1.373 | 0.71194 | 0.77537 | 1.3724 | 0.74422 | 0.81239 | 2.3243 | -114.49 | 99.8338 | 2.3587 | -115.8898 | 101.0089
Line5_6_7 | 0.1969 | 0.52329 | 0.57076 | 0.1969 | 0.52329 | 0.57076 | 0.045472 | 0.12085 | 0.13181 | 0.045473 | 0.12085 | 0.13181 | 0.0097608 | 0.026916 | -0.095066 | -0.0097193 | -0.026086 | 0.098452 | 0.061638 | -0.085817 | -0.049284 | -0.061616 | 0.090193 | 0.053401 | -78.6429 | -43.3036 | -106.3944 | 101.3571 | 136.6964 | 73.6056 |  | 1.3724 | 0.74422 | 0.81239 | 1.3718 | 0.77692 | 0.84971 | 2.3587 | -115.8898 | 101.0089 | 2.3931 | -117.1726 | 102.0812
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4483e-08 | -4.5414e-08 | 5.9422e-08 | 8.2839e-09 | 3.1192e-08 | -3.9001e-08 | -9.7851e-08 | 3.5849e-08 | 1.9348e-09 | 6.5465e-08 | -2.3745e-08 | -2.3443e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3718 | 0.77692 | 0.84971 | 1.3718 | 0.77692 | 0.84971 | 2.3931 | -117.1726 | 102.0812 | 2.3931 | -117.1726 | 102.0812
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8278e-09 | -1.5138e-08 | 1.9807e-08 | -1.3718e-09 | 9.1655e-10 | 6.1356e-10 | -3.2617e-08 | 1.195e-08 | 6.4492e-10 | 2.3102e-10 | 1.5457e-10 | -1.0544e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3718 | 0.77692 | 0.84971 | 1.3718 | 0.77692 | 0.84971 | 2.3931 | -117.1726 | 102.0812 | 2.3931 | -117.1726 | 102.0812
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8278e-09 | -1.5138e-08 | 1.9807e-08 | -1.3718e-09 | 9.1655e-10 | 6.1356e-10 | -3.2617e-08 | 1.195e-08 | 6.4492e-10 | 2.3102e-10 | 1.5457e-10 | -1.0544e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3718 | 0.77692 | 0.84971 | 1.3718 | 0.77692 | 0.84971 | 2.3931 | -117.1726 | 102.0812 | 2.3931 | -117.1726 | 102.0812
Line9_3_11 | 0.18229 | 0.47553 | 0.51176 | 0.18229 | 0.47553 | 0.51176 | 0.042098 | 0.10982 | 0.11819 | 0.042098 | 0.10982 | 0.11819 | 0.013528 | 0.023829 | -0.082929 | -0.013512 | -0.023127 | 0.08567 | 0.056177 | -0.074133 | -0.037809 | -0.056133 | 0.077721 | 0.041094 | -74.1659 | -42.1321 | -104.7523 | 105.8341 | 137.8679 | 75.2477 |  | 1.3726 | 0.70907 | 0.77118 | 1.3715 | 0.73839 | 0.80396 | 2.2949 | -114.313 | 99.757 | 2.2998 | -115.5609 | 100.8738

## LLG_max_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11694 | 0.12346 | 0.11979 | 0.11694 | 0.12346 | 0.11979 | 0.027007 | 0.028512 | 0.027664 | 0.027007 | 0.028512 | 0.027664 | -0.0010913 | -0.0018514 | -0.0028719 | 0.0012266 | 0.0020004 | 0.0030202 | -0.029354 | -0.030787 | -0.02986 | 0.029632 | 0.031088 | 0.030146 | 92.331 | -26.5015 | -144.5997 | -87.669 | 153.4985 | 35.4003 |  | 1.0877 | 1.0817 | 1.0844 | 1.0982 | 1.0926 | 1.0952 | 0.20191 | -119.943 | 119.9066 | -0.039291 | -120.1831 | 119.6792
Line10_11_12 | 0.10431 | 0.11011 | 0.10664 | 0.10431 | 0.11011 | 0.10664 | 0.024089 | 0.025429 | 0.024629 | 0.024089 | 0.025429 | 0.024629 | -0.0010788 | -0.0018438 | -0.0027289 | 0.0011863 | 0.0019623 | 0.0028465 | -0.026629 | -0.02794 | -0.027043 | 0.026851 | 0.028179 | 0.027269 | 92.0915 | -26.5944 | -144.7358 | -87.9085 | 153.4056 | 35.2642 |  | 1.1064 | 1.1011 | 1.1036 | 1.1157 | 1.1108 | 1.1132 | -0.22849 | -120.37 | 119.502 | -0.43827 | -120.5779 | 119.305
Line11_12_13 | 0.10431 | 0.11011 | 0.10664 | 0.10431 | 0.11011 | 0.10664 | 0.024089 | 0.025429 | 0.024629 | 0.024089 | 0.025429 | 0.024629 | -0.0011863 | -0.0019623 | -0.0028465 | 0.0012938 | 0.0020809 | 0.0029641 | -0.026851 | -0.028179 | -0.027269 | 0.027072 | 0.028419 | 0.027496 | 92.0915 | -26.5944 | -144.7358 | -87.9085 | 153.4056 | 35.2642 |  | 1.1157 | 1.1108 | 1.1132 | 1.1251 | 1.1205 | 1.1229 | -0.43827 | -120.5779 | 119.305 | -0.64456 | -120.7823 | 119.1113
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8759e-10 | 7.1945e-10 | 1.5958e-09 | -5.6849e-10 | -7.6988e-10 | -1.3644e-09 | -3.4453e-10 | 8.895e-10 | -2.599e-11 | 1.8095e-10 | -6.519e-10 | -4.9726e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1251 | 1.1205 | 1.1229 | 1.1251 | 1.1205 | 1.1229 | -0.64456 | -120.7823 | 119.1113 | -0.64456 | -120.7823 | 119.1113
Line13_13_14 | 0.10431 | 0.11011 | 0.10664 | 0.10431 | 0.11011 | 0.10664 | 0.024089 | 0.025429 | 0.024629 | 0.024089 | 0.025429 | 0.024629 | -0.0012938 | -0.0020809 | -0.0029641 | 0.0014012 | 0.0021994 | 0.0030818 | -0.027072 | -0.028419 | -0.027496 | 0.027293 | 0.028658 | 0.027722 | 92.0915 | -26.5944 | -144.7358 | -87.9085 | 153.4056 | 35.2642 |  | 1.1251 | 1.1205 | 1.1229 | 1.1345 | 1.1303 | 1.1325 | -0.64456 | -120.7823 | 119.1113 | -0.84744 | -120.9831 | 118.9209
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.584e-10 | 4.7963e-10 | 1.0638e-09 | -4.3929e-10 | -5.3006e-10 | -8.3252e-10 | -2.2968e-10 | 5.93e-10 | -1.7327e-11 | 6.6113e-11 | -3.554e-10 | -5.8389e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1251 | 1.1205 | 1.1229 | 1.1251 | 1.1205 | 1.1229 | -0.64456 | -120.7823 | 119.1113 | -0.64456 | -120.7823 | 119.1113
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.292e-10 | 2.3982e-10 | 5.3192e-10 | -3.101e-10 | -2.9025e-10 | -3.006e-10 | -1.1484e-10 | 2.965e-10 | -8.6632e-12 | -4.8729e-11 | -5.8898e-11 | -6.7052e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1251 | 1.1205 | 1.1229 | 1.1251 | 1.1205 | 1.1229 | -0.64456 | -120.7823 | 119.1113 | -0.64456 | -120.7823 | 119.1113
Line16_4_18 | 0 | 0.035581 | 0.035643 | 0 | 0.035581 | 0.035643 | 0 | 0.008217 | 0.0082313 | 0 | 0.008217 | 0.0082313 | -1.7891e-11 | 0.0063378 | 0.0063673 | -1.9896e-10 | -0.0063299 | -0.006352 | -2.7707e-10 | 0.0063549 | 0.0063734 | 4.9698e-12 | -0.0063299 | -0.006352 | 0 | -165.2113 | 74.7479 | 0 | 14.7887 | -105.2521 |  | 1.0999 | 1.0923 | 1.0945 | 1.0994 | 1.0894 | 1.0913 | 0.076546 | -120.1341 | 119.7756 | 0.067276 | -120.2113 | 119.7479
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4534e-11 | 3.7802e-11 | 4.1949e-10 | -1.5024e-10 | -1.2592e-10 | -1.366e-10 | -2.3032e-10 | 2.7104e-10 | -5.5367e-11 | 1.4757e-11 | 4.145e-12 | -6.8073e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0877 | 1.0817 | 1.0844 | 1.0877 | 1.0817 | 1.0844 | 0.20191 | -119.943 | 119.9066 | 0.20191 | -119.943 | 119.9066
Line1_1_3 | 0.10431 | 0.11011 | 0.10664 | 0.10431 | 0.11011 | 0.10664 | 0.024089 | 0.025429 | 0.024629 | 0.024089 | 0.025429 | 0.024629 | -0.00086394 | -0.0016068 | -0.0024936 | 0.00097139 | 0.0017253 | 0.0026112 | -0.026187 | -0.027461 | -0.026589 | 0.026408 | 0.0277 | 0.026816 | 92.0915 | -26.5944 | -144.7358 | -87.9085 | 153.4056 | 35.2642 |  | 1.0877 | 1.0817 | 1.0844 | 1.097 | 1.0914 | 1.094 | 0.20191 | -119.943 | 119.9066 | -0.015121 | -120.1584 | 119.7025
Line2_1_4 | 0.13179 | 0.11162 | 0.10811 | 0.13179 | 0.11162 | 0.10811 | 0.030435 | 0.025778 | 0.024966 | 0.030435 | 0.025778 | 0.024966 | -0.0092639 | -0.003913 | -0.0050828 | 0.0094384 | 0.004044 | 0.0051916 | -0.03178 | -0.027609 | -0.026591 | 0.032117 | 0.027864 | 0.026827 | 106.4532 | -21.8762 | -139.2719 | -73.5468 | 158.1238 | 40.7281 |  | 1.0877 | 1.0817 | 1.0844 | 1.0999 | 1.0923 | 1.0945 | 0.20191 | -119.943 | 119.9066 | 0.076546 | -120.1341 | 119.7756
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.9068e-11 | 7.5605e-11 | 8.3898e-10 | -1.0571e-10 | -1.6372e-10 | -5.5609e-10 | -4.6064e-10 | 5.4208e-10 | -1.1073e-10 | 2.4508e-10 | -2.6689e-10 | 4.856e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0877 | 1.0817 | 1.0844 | 1.0877 | 1.0817 | 1.0844 | 0.20191 | -119.943 | 119.9066 | 0.20191 | -119.943 | 119.9066
Line4_2_6 | 0.11694 | 0.12346 | 0.11979 | 0.11694 | 0.12346 | 0.11979 | 0.027007 | 0.028512 | 0.027664 | 0.027007 | 0.028512 | 0.027664 | -0.0012266 | -0.0020004 | -0.0030202 | 0.0013619 | 0.0021493 | 0.0031685 | -0.029632 | -0.031088 | -0.030146 | 0.02991 | 0.03139 | 0.030432 | 92.331 | -26.5015 | -144.5997 | -87.669 | 153.4985 | 35.4003 |  | 1.0982 | 1.0926 | 1.0952 | 1.1087 | 1.1035 | 1.106 | -0.039291 | -120.1831 | 119.6792 | -0.27593 | -120.4185 | 119.4562
Line5_6_7 | 0.11694 | 0.12346 | 0.11979 | 0.11694 | 0.12346 | 0.11979 | 0.027007 | 0.028512 | 0.027664 | 0.027007 | 0.028512 | 0.027664 | -0.0013619 | -0.0021493 | -0.0031685 | 0.0014971 | 0.0022982 | 0.0033168 | -0.02991 | -0.03139 | -0.030432 | 0.030188 | 0.031691 | 0.030717 | 92.331 | -26.5015 | -144.5997 | -87.669 | 153.4985 | 35.4003 |  | 1.1087 | 1.1035 | 1.106 | 1.1192 | 1.1144 | 1.1168 | -0.27593 | -120.4185 | 119.4562 | -0.50812 | -120.6493 | 119.2375
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9602e-10 | 6.2393e-10 | 1.5444e-09 | -4.8143e-10 | -6.7937e-10 | -1.3036e-09 | -4.0147e-10 | 8.8287e-10 | -5.4731e-11 | 2.2944e-10 | -6.372e-10 | -2.073e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1192 | 1.1144 | 1.1168 | 1.1192 | 1.1144 | 1.1168 | -0.50812 | -120.6493 | 119.2375 | -0.50812 | -120.6493 | 119.2375
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8674e-11 | 2.0798e-10 | 5.148e-10 | -2.8408e-10 | -2.6342e-10 | -2.7396e-10 | -1.3382e-10 | 2.9429e-10 | -1.8244e-11 | -3.8212e-11 | -4.862e-11 | -5.7218e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1192 | 1.1144 | 1.1168 | 1.1192 | 1.1144 | 1.1168 | -0.50812 | -120.6493 | 119.2375 | -0.50812 | -120.6493 | 119.2375
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8674e-11 | 2.0798e-10 | 5.148e-10 | -2.8408e-10 | -2.6342e-10 | -2.7396e-10 | -1.3382e-10 | 2.9429e-10 | -1.8244e-11 | -3.8212e-11 | -4.862e-11 | -5.7218e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1192 | 1.1144 | 1.1168 | 1.1192 | 1.1144 | 1.1168 | -0.50812 | -120.6493 | 119.2375 | -0.50812 | -120.6493 | 119.2375
Line9_3_11 | 0.10431 | 0.11011 | 0.10664 | 0.10431 | 0.11011 | 0.10664 | 0.024089 | 0.025429 | 0.024629 | 0.024089 | 0.025429 | 0.024629 | -0.00097139 | -0.0017253 | -0.0026112 | 0.0010788 | 0.0018438 | 0.0027289 | -0.026408 | -0.0277 | -0.026816 | 0.026629 | 0.02794 | 0.027043 | 92.0915 | -26.5944 | -144.7358 | -87.9085 | 153.4056 | 35.2642 |  | 1.097 | 1.0914 | 1.094 | 1.1064 | 1.1011 | 1.1036 | -0.015121 | -120.1584 | 119.7025 | -0.22849 | -120.37 | 119.502

## LLG_max_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.11766 | 0.12452 | 0.12068 | 0.11766 | 0.12452 | 0.12068 | 0.027173 | 0.028756 | 0.02787 | 0.027173 | 0.028756 | 0.02787 | -0.0011551 | -0.0019901 | -0.0031133 | 0.001292 | 0.0021414 | 0.003264 | -0.030949 | -0.032528 | -0.031511 | 0.031231 | 0.032835 | 0.031801 | 92.3408 | -26.4476 | -144.4622 | -87.6592 | 153.5524 | 35.5378 |  | 1.1398 | 1.1333 | 1.1361 | 1.1503 | 1.1443 | 1.147 | 0.20333 | -119.9485 | 119.8953 | -0.028157 | -120.179 | 119.6776
Line10_11_12 | 0.10538 | 0.11151 | 0.10788 | 0.10538 | 0.11151 | 0.10788 | 0.024337 | 0.025752 | 0.024913 | 0.024337 | 0.025752 | 0.024913 | -0.0011385 | -0.0019796 | -0.0029589 | 0.0012481 | 0.0021011 | 0.0030794 | -0.028175 | -0.029624 | -0.028637 | 0.028401 | 0.02987 | 0.028869 | 92.1024 | -26.5369 | -144.5946 | -87.8976 | 153.4631 | 35.4054 |  | 1.1587 | 1.1529 | 1.1556 | 1.1681 | 1.1627 | 1.1654 | -0.21149 | -120.36 | 119.5063 | -0.41386 | -120.5606 | 119.3167
Line11_12_13 | 0.10538 | 0.11151 | 0.10788 | 0.10538 | 0.11151 | 0.10788 | 0.024337 | 0.025752 | 0.024913 | 0.024337 | 0.025752 | 0.024913 | -0.0012481 | -0.0021011 | -0.0030794 | 0.0013577 | 0.0022225 | 0.0032 | -0.028401 | -0.02987 | -0.028869 | 0.028627 | 0.030115 | 0.029101 | 92.1024 | -26.5369 | -144.5946 | -87.8976 | 153.4631 | 35.4054 |  | 1.1681 | 1.1627 | 1.1654 | 1.1776 | 1.1726 | 1.1751 | -0.41386 | -120.5606 | 119.3167 | -0.61298 | -120.7577 | 119.1303
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8171e-10 | 7.6126e-10 | 1.7737e-09 | -5.8987e-10 | -8.1998e-10 | -1.5068e-09 | -4.1479e-10 | 1.009e-09 | -4.4423e-11 | 2.2571e-10 | -7.352e-10 | -4.2326e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1776 | 1.1726 | 1.1751 | 1.1776 | 1.1726 | 1.1751 | -0.61298 | -120.7577 | 119.1303 | -0.61298 | -120.7577 | 119.1303
Line13_13_14 | 0.10538 | 0.11151 | 0.10788 | 0.10538 | 0.11151 | 0.10788 | 0.024337 | 0.025752 | 0.024913 | 0.024337 | 0.025752 | 0.024913 | -0.0013577 | -0.0022225 | -0.0032 | 0.0014674 | 0.0023439 | 0.0033205 | -0.028627 | -0.030115 | -0.029101 | 0.028853 | 0.03036 | 0.029333 | 92.1024 | -26.5369 | -144.5946 | -87.8976 | 153.4631 | 35.4054 |  | 1.1776 | 1.1726 | 1.1751 | 1.1871 | 1.1824 | 1.1849 | -0.61298 | -120.7577 | 119.1303 | -0.80891 | -120.9516 | 118.947
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5447e-10 | 5.0751e-10 | 1.1825e-09 | -4.6263e-10 | -5.6623e-10 | -9.1558e-10 | -2.7653e-10 | 6.7266e-10 | -2.9615e-11 | 8.745e-11 | -3.9887e-10 | -5.7134e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1776 | 1.1726 | 1.1751 | 1.1776 | 1.1726 | 1.1751 | -0.61298 | -120.7577 | 119.1303 | -0.61298 | -120.7577 | 119.1303
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2724e-10 | 2.5375e-10 | 5.9123e-10 | -3.354e-10 | -3.1247e-10 | -3.2435e-10 | -1.3826e-10 | 3.3633e-10 | -1.4808e-11 | -5.0814e-11 | -6.2545e-11 | -7.1942e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1776 | 1.1726 | 1.1751 | 1.1776 | 1.1726 | 1.1751 | -0.61298 | -120.7577 | 119.1303 | -0.61298 | -120.7577 | 119.1303
Line16_4_18 | 0 | 0.037256 | 0.037325 | 0 | 0.037256 | 0.037325 | 0 | 0.008604 | 0.0086199 | 0 | 0.008604 | 0.0086199 | -3.0362e-11 | 0.0069489 | 0.0069826 | -2.1708e-10 | -0.0069402 | -0.0069658 | -3.1445e-10 | 0.0069676 | 0.0069894 | 5.7437e-12 | -0.0069402 | -0.0069658 | 0 | -165.2147 | 74.7388 | 0 | 14.7853 | -105.2612 |  | 1.152 | 1.1437 | 1.1462 | 1.1514 | 1.1407 | 1.1428 | 0.080121 | -120.1376 | 119.7665 | 0.070862 | -120.2147 | 119.7388
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.7028e-11 | 3.7881e-11 | 4.7431e-10 | -1.6622e-10 | -1.3836e-10 | -1.5059e-10 | -2.6286e-10 | 3.1098e-10 | -6.321e-11 | 1.6314e-11 | 4.1059e-12 | -8.377e-12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1398 | 1.1333 | 1.1361 | 1.1398 | 1.1333 | 1.1361 | 0.20333 | -119.9485 | 119.8953 | 0.20333 | -119.9485 | 119.8953
Line1_1_3 | 0.10538 | 0.11151 | 0.10788 | 0.10538 | 0.11151 | 0.10788 | 0.024337 | 0.025752 | 0.024913 | 0.024337 | 0.025752 | 0.024913 | -0.00091922 | -0.0017368 | -0.0027179 | 0.0010288 | 0.0018582 | 0.0028384 | -0.027723 | -0.029133 | -0.028174 | 0.027949 | 0.029379 | 0.028405 | 92.1024 | -26.5369 | -144.5946 | -87.8976 | 153.4631 | 35.4054 |  | 1.1398 | 1.1333 | 1.1361 | 1.1492 | 1.1431 | 1.1459 | 0.20333 | -119.9485 | 119.8953 | -0.005785 | -120.156 | 119.6991
Line2_1_4 | 0.13192 | 0.11086 | 0.10712 | 0.13192 | 0.11086 | 0.10712 | 0.030465 | 0.025603 | 0.024738 | 0.030465 | 0.025603 | 0.024738 | -0.0095507 | -0.0036726 | -0.0049502 | 0.0097256 | 0.0038021 | 0.0050566 | -0.033384 | -0.028782 | -0.027666 | 0.033721 | 0.029034 | 0.027899 | 106.1685 | -22.677 | -139.9604 | -73.8315 | 157.323 | 40.0396 |  | 1.1398 | 1.1333 | 1.1361 | 1.152 | 1.1437 | 1.1462 | 0.20333 | -119.9485 | 119.8953 | 0.080121 | -120.1376 | 119.7665
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1406e-10 | 7.5762e-11 | 9.4863e-10 | -1.0919e-10 | -1.7624e-10 | -6.249e-10 | -5.2572e-10 | 6.2195e-10 | -1.2642e-10 | 2.7917e-10 | -3.0687e-10 | 5.4833e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1398 | 1.1333 | 1.1361 | 1.1398 | 1.1333 | 1.1361 | 0.20333 | -119.9485 | 119.8953 | 0.20333 | -119.9485 | 119.8953
Line4_2_6 | 0.11766 | 0.12452 | 0.12068 | 0.11766 | 0.12452 | 0.12068 | 0.027173 | 0.028756 | 0.02787 | 0.027173 | 0.028756 | 0.02787 | -0.001292 | -0.0021414 | -0.003264 | 0.0014289 | 0.0022927 | 0.0034147 | -0.031231 | -0.032835 | -0.031801 | 0.031513 | 0.033141 | 0.032091 | 92.3408 | -26.4476 | -144.4622 | -87.6592 | 153.5524 | 35.5378 |  | 1.1503 | 1.1443 | 1.147 | 1.1609 | 1.1552 | 1.1579 | -0.028157 | -120.179 | 119.6776 | -0.25543 | -120.405 | 119.4639
Line5_6_7 | 0.11766 | 0.12452 | 0.12068 | 0.11766 | 0.12452 | 0.12068 | 0.027173 | 0.028756 | 0.02787 | 0.027173 | 0.028756 | 0.02787 | -0.0014289 | -0.0022927 | -0.0034147 | 0.0015658 | 0.002444 | 0.0035654 | -0.031513 | -0.033141 | -0.032091 | 0.031794 | 0.033447 | 0.03238 | 92.3408 | -26.4476 | -144.4622 | -87.6592 | 153.5524 | 35.5378 |  | 1.1609 | 1.1552 | 1.1579 | 1.1715 | 1.1662 | 1.1689 | -0.25543 | -120.405 | 119.4639 | -0.47859 | -120.6268 | 119.2543
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8266e-10 | 6.5698e-10 | 1.7192e-09 | -4.9574e-10 | -7.2144e-10 | -1.4417e-09 | -4.7752e-10 | 1.0026e-09 | -7.487e-11 | 2.7888e-10 | -7.1985e-10 | -1.1441e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1715 | 1.1662 | 1.1689 | 1.1715 | 1.1662 | 1.1689 | -0.47859 | -120.6268 | 119.2543 | -0.47859 | -120.6268 | 119.2543
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4221e-11 | 2.1899e-10 | 5.7308e-10 | -3.073e-10 | -2.8346e-10 | -2.9554e-10 | -1.5917e-10 | 3.342e-10 | -2.4957e-11 | -3.9468e-11 | -5.1457e-11 | -6.1355e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1715 | 1.1662 | 1.1689 | 1.1715 | 1.1662 | 1.1689 | -0.47859 | -120.6268 | 119.2543 | -0.47859 | -120.6268 | 119.2543
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4221e-11 | 2.1899e-10 | 5.7308e-10 | -3.073e-10 | -2.8346e-10 | -2.9554e-10 | -1.5917e-10 | 3.342e-10 | -2.4957e-11 | -3.9468e-11 | -5.1457e-11 | -6.1355e-11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1715 | 1.1662 | 1.1689 | 1.1715 | 1.1662 | 1.1689 | -0.47859 | -120.6268 | 119.2543 | -0.47859 | -120.6268 | 119.2543
Line9_3_11 | 0.10538 | 0.11151 | 0.10788 | 0.10538 | 0.11151 | 0.10788 | 0.024337 | 0.025752 | 0.024913 | 0.024337 | 0.025752 | 0.024913 | -0.0010288 | -0.0018582 | -0.0028384 | 0.0011385 | 0.0019796 | 0.0029589 | -0.027949 | -0.029379 | -0.028405 | 0.028175 | 0.029624 | 0.028637 | 92.1024 | -26.5369 | -144.5946 | -87.8976 | 153.4631 | 35.4054 |  | 1.1492 | 1.1431 | 1.1459 | 1.1587 | 1.1529 | 1.1556 | -0.005785 | -120.156 | 119.6991 | -0.21149 | -120.36 | 119.5063

## LLG_min_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.013514 | 0.011625 | 0.015965 | 0.013514 | 0.011625 | 0.015965 | 0.0031208 | 0.0026846 | 0.0036869 | 0.0031209 | 0.0026846 | 0.0036869 | -0.00018124 | 0.0013714 | -0.0022388 | 0.00018311 | -0.0013707 | 0.0022421 | 0.0044039 | -0.00083512 | 5.6457e-05 | -0.0044022 | 0.00083681 | -5.3843e-05 | -92.0741 | -70.9463 | -99.4127 | 87.9259 | 109.0535 | 80.5874 |  | 1.4123 | 0.59809 | 0.60744 | 1.4118 | 0.59819 | 0.6083 | 0.28255 | -102.2866 | 79.1428 | 0.30772 | -102.3507 | 79.2118
Line10_11_12 | 0.01348 | 0.011597 | 0.015922 | 0.013481 | 0.011597 | 0.015922 | 0.0031132 | 0.0026782 | 0.0036771 | 0.0031132 | 0.0026782 | 0.0036771 | -0.00017315 | 0.0013649 | -0.0022392 | 0.000175 | -0.0013643 | 0.0022425 | 0.0043901 | -0.00083942 | 5.6235e-05 | -0.0043884 | 0.0008411 | -5.3635e-05 | -91.926 | -70.8231 | -99.2808 | 88.0741 | 109.1767 | 80.7193 |  | 1.4113 | 0.5983 | 0.60916 | 1.4107 | 0.59842 | 0.61003 | 0.33266 | -102.4144 | 79.2806 | 0.35775 | -102.4783 | 79.3492
Line11_12_13 | 0.013481 | 0.011597 | 0.015922 | 0.013481 | 0.011597 | 0.015923 | 0.0031132 | 0.0026782 | 0.0036771 | 0.0031133 | 0.0026783 | 0.0036772 | -0.00017501 | 0.0013643 | -0.0022425 | 0.00017686 | -0.0013636 | 0.0022458 | 0.0043884 | -0.0008411 | 5.3633e-05 | -0.0043867 | 0.00084278 | -5.1033e-05 | -91.926 | -70.8234 | -99.2808 | 88.0741 | 109.1764 | 80.7194 |  | 1.4107 | 0.59842 | 0.61003 | 1.4102 | 0.59853 | 0.61089 | 0.35775 | -102.4783 | 79.3492 | 0.38285 | -102.5421 | 79.4176
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2043e-09 | -6.9897e-08 | 6.9062e-08 | -5.8491e-09 | 4.7273e-08 | -4.5793e-08 | -1.6461e-07 | 1.4542e-08 | -1.0226e-08 | 1.0977e-07 | -9.0689e-09 | 5.4327e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4102 | 0.59853 | 0.61089 | 1.4102 | 0.59853 | 0.61089 | 0.38285 | -102.5421 | 79.4176 | 0.38285 | -102.5421 | 79.4176
Line13_13_14 | 0.013481 | 0.011598 | 0.015923 | 0.013482 | 0.011598 | 0.015923 | 0.0031134 | 0.0026784 | 0.0036773 | 0.0031134 | 0.0026784 | 0.0036773 | -0.00017687 | 0.0013637 | -0.0022458 | 0.00017872 | -0.001363 | 0.0022491 | 0.0043869 | -0.0008428 | 5.1042e-05 | -0.0043852 | 0.00084448 | -4.8441e-05 | -91.9259 | -70.8245 | -99.2805 | 88.0741 | 109.1752 | 80.7196 |  | 1.4102 | 0.59853 | 0.61089 | 1.4097 | 0.59864 | 0.61176 | 0.38285 | -102.5421 | 79.4176 | 0.40798 | -102.6059 | 79.4858
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4695e-09 | -4.6598e-08 | 4.6041e-08 | -4.1144e-09 | 2.3974e-08 | -2.2773e-08 | -1.0974e-07 | 9.6944e-09 | -6.817e-09 | 5.4903e-08 | -4.2217e-09 | 2.0242e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4102 | 0.59853 | 0.61089 | 1.4102 | 0.59853 | 0.61089 | 0.38285 | -102.5421 | 79.4176 | 0.38285 | -102.5421 | 79.4176
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7348e-09 | -2.3299e-08 | 2.3021e-08 | -2.3796e-09 | 6.7531e-10 | 2.4775e-10 | -5.487e-08 | 4.8472e-09 | -3.4085e-09 | 3.2823e-11 | 6.2547e-10 | -1.3843e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4102 | 0.59853 | 0.61089 | 1.4102 | 0.59853 | 0.61089 | 0.38285 | -102.5421 | 79.4176 | 0.38285 | -102.5421 | 79.4176
Line16_4_18 | 0 | 2.4832 | 2.5461 | 0 | 2.4832 | 2.5461 | 0 | 0.57348 | 0.58801 | 0 | 0.57348 | 0.588 | 2.2066e-09 | 0.11801 | 0.12481 | -2.3672e-09 | -1.7126e-14 | 7.7738e-16 | -5.5396e-08 | 0.12466 | 0.12827 | 3.801e-11 | -4.2156e-14 | 3.6162e-14 | 0 | -148.9551 | 33.4013 | 0 | 31.0449 | -146.5987 |  | 1.4101 | 0.29934 | 0.30437 | 1.4084 | 0 | 0 | 0.37637 | -102.3851 | 79.1859 | 0.44393 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9115e-09 | -2.3443e-08 | 2.3005e-08 | -2.3942e-09 | 6.7297e-10 | 2.4742e-10 | -5.5221e-08 | 4.6524e-09 | -3.4062e-09 | 2.4261e-11 | 6.3387e-10 | -1.3842e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4123 | 0.59809 | 0.60744 | 1.4123 | 0.59809 | 0.60744 | 0.28255 | -102.2866 | 79.1428 | 0.28255 | -102.2866 | 79.1428
Line1_1_3 | 0.01348 | 0.011597 | 0.015922 | 0.01348 | 0.011597 | 0.015922 | 0.0031131 | 0.0026781 | 0.003677 | 0.0031131 | 0.0026782 | 0.003677 | -0.00016943 | 0.0013662 | -0.0022327 | 0.00017129 | -0.0013656 | 0.002236 | 0.0043935 | -0.00083606 | 6.1438e-05 | -0.0043918 | 0.00083774 | -5.8838e-05 | -91.926 | -70.8225 | -99.281 | 88.0741 | 109.1773 | 80.7191 |  | 1.4123 | 0.59809 | 0.60744 | 1.4118 | 0.5982 | 0.6083 | 0.28255 | -102.2866 | 79.1428 | 0.3076 | -102.3505 | 79.2118
Line2_1_4 | 0.0132 | 2.4818 | 2.5316 | 0.013201 | 2.4818 | 2.5316 | 0.0030485 | 0.57314 | 0.58465 | 0.0030485 | 0.57314 | 0.58465 | -0.00044218 | 0.23666 | 0.2469 | 0.00044849 | -0.11866 | -0.12362 | 0.0042827 | 0.24798 | 0.25527 | -0.0042754 | -0.12391 | -0.128 | -95.6123 | -148.6239 | 33.1883 | 84.3878 | 31.3761 | -146.8117 |  | 1.4123 | 0.59809 | 0.60744 | 1.4101 | 0.29934 | 0.30437 | 0.28255 | -102.2866 | 79.1428 | 0.37637 | -102.3851 | 79.1859
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.823e-09 | -4.6886e-08 | 4.601e-08 | -4.3058e-09 | 2.4116e-08 | -2.2758e-08 | -1.1044e-07 | 9.3048e-09 | -6.8124e-09 | 5.5246e-08 | -4.0185e-09 | 2.022e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4123 | 0.59809 | 0.60744 | 1.4123 | 0.59809 | 0.60744 | 0.28255 | -102.2866 | 79.1428 | 0.28255 | -102.2866 | 79.1428
Line4_2_6 | 0.013514 | 0.011625 | 0.015965 | 0.013514 | 0.011625 | 0.015965 | 0.0031209 | 0.0026846 | 0.0036869 | 0.0031209 | 0.0026847 | 0.003687 | -0.00018311 | 0.0013707 | -0.0022421 | 0.00018497 | -0.00137 | 0.0022454 | 0.0044022 | -0.00083681 | 5.3841e-05 | -0.0044005 | 0.0008385 | -5.1226e-05 | -92.0741 | -70.9465 | -99.4126 | 87.9259 | 109.0532 | 80.5875 |  | 1.4118 | 0.59819 | 0.6083 | 1.4113 | 0.5983 | 0.60917 | 0.30772 | -102.3507 | 79.2118 | 0.33291 | -102.4148 | 79.2806
Line5_6_7 | 0.013514 | 0.011625 | 0.015965 | 0.013514 | 0.011625 | 0.015965 | 0.0031209 | 0.0026847 | 0.003687 | 0.0031209 | 0.0026847 | 0.003687 | -0.00018498 | 0.00137 | -0.0022454 | 0.00018684 | -0.0013694 | 0.0022487 | 0.0044005 | -0.0008385 | 5.1225e-05 | -0.0043988 | 0.00084019 | -4.861e-05 | -92.0741 | -70.9468 | -99.4125 | 87.9259 | 109.0529 | 80.5876 |  | 1.4113 | 0.5983 | 0.60917 | 1.4107 | 0.59841 | 0.61004 | 0.33291 | -102.4148 | 79.2806 | 0.35812 | -102.4788 | 79.3492
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.335e-09 | -7.0004e-08 | 6.9052e-08 | -5.9399e-09 | 4.7344e-08 | -4.5787e-08 | -1.6487e-07 | 1.4398e-08 | -1.0225e-08 | 1.0995e-07 | -8.9709e-09 | 5.432e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4107 | 0.59841 | 0.61004 | 1.4107 | 0.59841 | 0.61004 | 0.35812 | -102.4788 | 79.3492 | 0.35812 | -102.4788 | 79.3492
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7783e-09 | -2.3335e-08 | 2.3017e-08 | -2.3833e-09 | 6.7474e-10 | 2.4766e-10 | -5.4957e-08 | 4.7992e-09 | -3.4082e-09 | 3.0714e-11 | 6.2755e-10 | -1.3843e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4107 | 0.59841 | 0.61004 | 1.4107 | 0.59841 | 0.61004 | 0.35812 | -102.4788 | 79.3492 | 0.35812 | -102.4788 | 79.3492
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7783e-09 | -2.3335e-08 | 2.3017e-08 | -2.3833e-09 | 6.7474e-10 | 2.4766e-10 | -5.4957e-08 | 4.7992e-09 | -3.4082e-09 | 3.0714e-11 | 6.2755e-10 | -1.3843e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.4107 | 0.59841 | 0.61004 | 1.4107 | 0.59841 | 0.61004 | 0.35812 | -102.4788 | 79.3492 | 0.35812 | -102.4788 | 79.3492
Line9_3_11 | 0.01348 | 0.011597 | 0.015922 | 0.01348 | 0.011597 | 0.015922 | 0.0031131 | 0.0026782 | 0.003677 | 0.0031132 | 0.0026782 | 0.0036771 | -0.00017129 | 0.0013656 | -0.002236 | 0.00017315 | -0.0013649 | 0.0022392 | 0.0043918 | -0.00083774 | 5.8837e-05 | -0.0043901 | 0.00083942 | -5.6236e-05 | -91.926 | -70.8228 | -99.2809 | 88.0741 | 109.177 | 80.7192 |  | 1.4118 | 0.5982 | 0.6083 | 1.4113 | 0.5983 | 0.60916 | 0.3076 | -102.3505 | 79.2118 | 0.33266 | -102.4144 | 79.2806

## LLG_min_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.012802 | 0.011013 | 0.015124 | 0.012802 | 0.011013 | 0.015125 | 0.0029566 | 0.0025433 | 0.0034929 | 0.0029566 | 0.0025434 | 0.0034929 | -0.00016267 | 0.0012308 | -0.0020094 | 0.00016434 | -0.0012302 | 0.0020123 | 0.0039525 | -0.00074953 | 5.0671e-05 | -0.003951 | 0.00075104 | -4.8324e-05 | -92.0741 | -70.9463 | -99.4127 | 87.9259 | 109.0535 | 80.5874 |  | 1.338 | 0.56661 | 0.57547 | 1.3375 | 0.56671 | 0.57629 | 0.28255 | -102.2866 | 79.1428 | 0.30772 | -102.3507 | 79.2118
Line10_11_12 | 0.012771 | 0.010987 | 0.015084 | 0.012771 | 0.010987 | 0.015084 | 0.0029493 | 0.0025372 | 0.0034836 | 0.0029494 | 0.0025373 | 0.0034836 | -0.0001554 | 0.001225 | -0.0020097 | 0.00015707 | -0.0012244 | 0.0020127 | 0.0039401 | -0.00075338 | 5.0471e-05 | -0.0039386 | 0.00075489 | -4.8137e-05 | -91.926 | -70.8231 | -99.2808 | 88.0741 | 109.1767 | 80.7193 |  | 1.337 | 0.56681 | 0.5771 | 1.3365 | 0.56692 | 0.57792 | 0.33266 | -102.4144 | 79.2806 | 0.35775 | -102.4783 | 79.3492
Line11_12_13 | 0.012771 | 0.010987 | 0.015084 | 0.012771 | 0.010987 | 0.015085 | 0.0029494 | 0.0025373 | 0.0034836 | 0.0029494 | 0.0025373 | 0.0034836 | -0.00015707 | 0.0012244 | -0.0020127 | 0.00015873 | -0.0012238 | 0.0020156 | 0.0039386 | -0.00075489 | 4.8136e-05 | -0.0039371 | 0.0007564 | -4.5802e-05 | -91.926 | -70.8234 | -99.2808 | 88.0741 | 109.1764 | 80.7194 |  | 1.3365 | 0.56692 | 0.57792 | 1.336 | 0.56702 | 0.57874 | 0.35775 | -102.4783 | 79.3492 | 0.38285 | -102.5421 | 79.4176
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6709e-09 | -6.2733e-08 | 6.1983e-08 | -5.2496e-09 | 4.2428e-08 | -4.11e-08 | -1.4774e-07 | 1.3051e-08 | -9.1775e-09 | 9.8521e-08 | -8.1394e-09 | 4.8759e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.336 | 0.56702 | 0.57874 | 1.336 | 0.56702 | 0.57874 | 0.38285 | -102.5421 | 79.4176 | 0.38285 | -102.5421 | 79.4176
Line13_13_14 | 0.012772 | 0.010987 | 0.015085 | 0.012772 | 0.010988 | 0.015085 | 0.0029495 | 0.0025374 | 0.0034837 | 0.0029496 | 0.0025375 | 0.0034838 | -0.00015874 | 0.0012239 | -0.0020156 | 0.00016041 | -0.0012233 | 0.0020186 | 0.0039373 | -0.00075641 | 4.581e-05 | -0.0039357 | 0.00075792 | -4.3476e-05 | -91.9259 | -70.8245 | -99.2805 | 88.0741 | 109.1752 | 80.7196 |  | 1.336 | 0.56702 | 0.57874 | 1.3355 | 0.56713 | 0.57956 | 0.38285 | -102.5421 | 79.4176 | 0.40798 | -102.6059 | 79.4858
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1139e-09 | -4.1822e-08 | 4.1322e-08 | -3.6927e-09 | 2.1517e-08 | -2.0439e-08 | -9.8492e-08 | 8.7008e-09 | -6.1183e-09 | 4.9275e-08 | -3.789e-09 | 1.8167e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.336 | 0.56702 | 0.57874 | 1.336 | 0.56702 | 0.57874 | 0.38285 | -102.5421 | 79.4176 | 0.38285 | -102.5421 | 79.4176
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.557e-09 | -2.0911e-08 | 2.0661e-08 | -2.1357e-09 | 6.0609e-10 | 2.2236e-10 | -4.9246e-08 | 4.3504e-09 | -3.0592e-09 | 2.9459e-11 | 5.6136e-10 | -1.2424e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.336 | 0.56702 | 0.57874 | 1.336 | 0.56702 | 0.57874 | 0.38285 | -102.5421 | 79.4176 | 0.38285 | -102.5421 | 79.4176
Line16_4_18 | 0 | 2.3525 | 2.4121 | 0 | 2.3525 | 2.4121 | 0 | 0.5433 | 0.55706 | 0 | 0.5433 | 0.55706 | 1.9804e-09 | 0.10592 | 0.11202 | -2.1245e-09 | -1.4339e-14 | -7.0243e-16 | -4.9718e-08 | 0.11189 | 0.11513 | 3.4115e-11 | -3.4173e-14 | 2.8762e-14 | 0 | -148.9551 | 33.4013 | 0 | 31.0449 | -146.5987 |  | 1.3359 | 0.28358 | 0.28835 | 1.3342 | 0 | 0 | 0.37637 | -102.3851 | 79.1859 | 0.44393 | 0 | 0
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7156e-09 | -2.104e-08 | 2.0647e-08 | -2.1488e-09 | 6.04e-10 | 2.2206e-10 | -4.9561e-08 | 4.1756e-09 | -3.0571e-09 | 2.1774e-11 | 5.689e-10 | -1.2423e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.338 | 0.56661 | 0.57547 | 1.338 | 0.56661 | 0.57547 | 0.28255 | -102.2866 | 79.1428 | 0.28255 | -102.2866 | 79.1428
Line1_1_3 | 0.012771 | 0.010986 | 0.015084 | 0.012771 | 0.010986 | 0.015084 | 0.0029493 | 0.0025372 | 0.0034835 | 0.0029493 | 0.0025372 | 0.0034835 | -0.00015207 | 0.0012262 | -0.0020039 | 0.00015373 | -0.0012256 | 0.0020068 | 0.0039432 | -0.00075037 | 5.5141e-05 | -0.0039417 | 0.00075188 | -5.2808e-05 | -91.926 | -70.8225 | -99.281 | 88.0741 | 109.1773 | 80.7191 |  | 1.338 | 0.56661 | 0.57547 | 1.3375 | 0.56671 | 0.57628 | 0.28255 | -102.2866 | 79.1428 | 0.3076 | -102.3505 | 79.2118
Line2_1_4 | 0.012506 | 2.3511 | 2.3984 | 0.012506 | 2.3511 | 2.3984 | 0.002888 | 0.54297 | 0.55388 | 0.0028881 | 0.54297 | 0.55388 | -0.00039686 | 0.21241 | 0.2216 | 0.00040253 | -0.1065 | -0.11095 | 0.0038438 | 0.22256 | 0.22911 | -0.0038372 | -0.11121 | -0.11488 | -95.6123 | -148.6239 | 33.1883 | 84.3878 | 31.3761 | -146.8117 |  | 1.338 | 0.56661 | 0.57547 | 1.3359 | 0.28358 | 0.28835 | 0.28255 | -102.2866 | 79.1428 | 0.37637 | -102.3851 | 79.1859
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4312e-09 | -4.208e-08 | 4.1295e-08 | -3.8644e-09 | 2.1644e-08 | -2.0425e-08 | -9.9123e-08 | 8.3511e-09 | -6.1141e-09 | 4.9583e-08 | -3.6067e-09 | 1.8148e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.338 | 0.56661 | 0.57547 | 1.338 | 0.56661 | 0.57547 | 0.28255 | -102.2866 | 79.1428 | 0.28255 | -102.2866 | 79.1428
Line4_2_6 | 0.012802 | 0.011013 | 0.015125 | 0.012803 | 0.011013 | 0.015125 | 0.0029566 | 0.0025434 | 0.0034929 | 0.0029566 | 0.0025434 | 0.0034929 | -0.00016434 | 0.0012302 | -0.0020123 | 0.00016602 | -0.0012296 | 0.0020153 | 0.003951 | -0.00075104 | 4.8323e-05 | -0.0039495 | 0.00075256 | -4.5976e-05 | -92.0741 | -70.9465 | -99.4126 | 87.9259 | 109.0532 | 80.5875 |  | 1.3375 | 0.56671 | 0.57629 | 1.337 | 0.56681 | 0.57711 | 0.30772 | -102.3507 | 79.2118 | 0.33291 | -102.4148 | 79.2806
Line5_6_7 | 0.012803 | 0.011013 | 0.015125 | 0.012803 | 0.011013 | 0.015125 | 0.0029566 | 0.0025434 | 0.0034929 | 0.0029567 | 0.0025434 | 0.003493 | -0.00016602 | 0.0012296 | -0.0020153 | 0.00016769 | -0.001229 | 0.0020182 | 0.0039495 | -0.00075256 | 4.5975e-05 | -0.003948 | 0.00075408 | -4.3628e-05 | -92.0741 | -70.9468 | -99.4125 | 87.9259 | 109.0529 | 80.5876 |  | 1.337 | 0.56681 | 0.57711 | 1.3365 | 0.56692 | 0.57793 | 0.33291 | -102.4148 | 79.2806 | 0.35812 | -102.4788 | 79.3492
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7882e-09 | -6.2829e-08 | 6.1974e-08 | -5.3311e-09 | 4.2492e-08 | -4.1094e-08 | -1.4797e-07 | 1.2922e-08 | -9.1766e-09 | 9.8677e-08 | -8.0514e-09 | 4.8753e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3365 | 0.56692 | 0.57793 | 1.3365 | 0.56692 | 0.57793 | 0.35812 | -102.4788 | 79.3492 | 0.35812 | -102.4788 | 79.3492
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5961e-09 | -2.0943e-08 | 2.0658e-08 | -2.139e-09 | 6.0558e-10 | 2.2228e-10 | -4.9325e-08 | 4.3073e-09 | -3.0589e-09 | 2.7566e-11 | 5.6323e-10 | -1.2424e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3365 | 0.56692 | 0.57793 | 1.3365 | 0.56692 | 0.57793 | 0.35812 | -102.4788 | 79.3492 | 0.35812 | -102.4788 | 79.3492
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5961e-09 | -2.0943e-08 | 2.0658e-08 | -2.139e-09 | 6.0558e-10 | 2.2228e-10 | -4.9325e-08 | 4.3073e-09 | -3.0589e-09 | 2.7566e-11 | 5.6323e-10 | -1.2424e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.3365 | 0.56692 | 0.57793 | 1.3365 | 0.56692 | 0.57793 | 0.35812 | -102.4788 | 79.3492 | 0.35812 | -102.4788 | 79.3492
Line9_3_11 | 0.012771 | 0.010986 | 0.015084 | 0.012771 | 0.010987 | 0.015084 | 0.0029493 | 0.0025372 | 0.0034835 | 0.0029493 | 0.0025372 | 0.0034836 | -0.00015374 | 0.0012256 | -0.0020068 | 0.0001554 | -0.001225 | 0.0020097 | 0.0039417 | -0.00075188 | 5.2806e-05 | -0.0039401 | 0.00075339 | -5.0473e-05 | -91.926 | -70.8228 | -99.2809 | 88.0741 | 109.177 | 80.7192 |  | 1.3375 | 0.56671 | 0.57628 | 1.337 | 0.56681 | 0.5771 | 0.3076 | -102.3505 | 79.2118 | 0.33266 | -102.4144 | 79.2806

## LLG_min_fault_6
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0028568 | 0.002869 | 0.0028909 | 0.0028569 | 0.002869 | 0.0028909 | 0.00065975 | 0.00066256 | 0.00066762 | 0.00065976 | 0.00066257 | 0.00066763 | 0.00037129 | 0.00024119 | -0.0006298 | -0.00037121 | -0.00024111 | 0.00062989 | 0.00057025 | -0.00051481 | 0.00013074 | -0.00057018 | 0.0005149 | -0.00013066 | -53.6724 | -52.5805 | -54.2427 | 126.3276 | 127.4195 | 125.7573 |  | 1.0314 | 0.85805 | 0.96346 | 1.0312 | 0.85811 | 0.96355 | 3.2597 | -117.4776 | 114.0302 | 3.2615 | -117.4882 | 114.0389
Line10_11_12 | 0.0028497 | 0.0028618 | 0.0028836 | 0.0028498 | 0.0028619 | 0.0028837 | 0.00065811 | 0.00066091 | 0.00066595 | 0.00065812 | 0.00066092 | 0.00066596 | 0.00037156 | 0.00023922 | -0.00062807 | -0.00037149 | -0.00023914 | 0.00062816 | 0.00056779 | -0.00051427 | 0.00013174 | -0.00056771 | 0.00051435 | -0.00013166 | -53.5357 | -52.4451 | -54.1064 | 126.4643 | 127.5549 | 125.8936 |  | 1.0311 | 0.85818 | 0.96365 | 1.0309 | 0.85824 | 0.96374 | 3.2633 | -117.4988 | 114.0476 | 3.265 | -117.5094 | 114.0564
Line11_12_13 | 0.0028498 | 0.0028619 | 0.0028837 | 0.0028498 | 0.0028619 | 0.0028837 | 0.00065812 | 0.00066092 | 0.00066596 | 0.00065813 | 0.00066093 | 0.00066597 | 0.00037149 | 0.00023915 | -0.00062816 | -0.00037142 | -0.00023907 | 0.00062825 | 0.00056771 | -0.00051435 | 0.00013166 | -0.00056764 | 0.00051444 | -0.00013157 | -53.5357 | -52.4451 | -54.1065 | 126.4643 | 127.5549 | 125.8936 |  | 1.0309 | 0.85824 | 0.96374 | 1.0307 | 0.85831 | 0.96384 | 3.265 | -117.5094 | 114.0564 | 3.2668 | -117.52 | 114.0651
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3201e-08 | -1.0225e-08 | 2.3702e-08 | 8.4895e-09 | 7.1025e-09 | -1.5868e-08 | -2.213e-08 | 1.8893e-08 | -4.1695e-09 | 1.4958e-08 | -1.2466e-08 | 2.4325e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0307 | 0.85831 | 0.96384 | 1.0307 | 0.85831 | 0.96384 | 3.2668 | -117.52 | 114.0651 | 3.2668 | -117.52 | 114.0651
Line13_13_14 | 0.0028499 | 0.002862 | 0.0028838 | 0.0028499 | 0.002862 | 0.0028839 | 0.00065816 | 0.00066095 | 0.00066599 | 0.00065816 | 0.00066096 | 0.000666 | 0.00037143 | 0.00023908 | -0.00062828 | -0.00037136 | -0.00023901 | 0.00062836 | 0.00056766 | -0.00051446 | 0.00013158 | -0.00056759 | 0.00051455 | -0.0001315 | -53.5359 | -52.4453 | -54.1065 | 126.4641 | 127.5547 | 125.8935 |  | 1.0307 | 0.85831 | 0.96384 | 1.0306 | 0.85837 | 0.96393 | 3.2668 | -117.52 | 114.0651 | 3.2686 | -117.5306 | 114.0738
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.8004e-09 | -6.8167e-09 | 1.5801e-08 | 4.0893e-09 | 3.6941e-09 | -7.9675e-09 | -1.4753e-08 | 1.2595e-08 | -2.7797e-09 | 7.5812e-09 | -6.1683e-09 | 1.0427e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0307 | 0.85831 | 0.96384 | 1.0307 | 0.85831 | 0.96384 | 3.2668 | -117.52 | 114.0651 | 3.2668 | -117.52 | 114.0651
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4002e-09 | -3.4084e-09 | 7.9006e-09 | -3.1094e-10 | 2.8576e-10 | -6.6896e-11 | -7.3766e-09 | 6.2977e-09 | -1.3898e-09 | 2.046e-10 | 1.2937e-10 | -3.4715e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0307 | 0.85831 | 0.96384 | 1.0307 | 0.85831 | 0.96384 | 3.2668 | -117.52 | 114.0651 | 3.2668 | -117.52 | 114.0651
Line16_4_18 | 0 | 0.02782 | 0.031243 | 0 | 0.02782 | 0.031242 | 0 | 0.0064247 | 0.0072151 | 0 | 0.0064247 | 0.0072151 | -4.3817e-09 | 0.0038815 | 0.0049001 | -3.0885e-10 | -0.0038697 | -0.0048805 | -7.4866e-09 | 0.0038865 | 0.0048963 | 2.0484e-10 | -0.0038697 | -0.0048805 | 0 | -162.5626 | 69.0822 | 0 | 17.4375 | -110.9178 |  | 1.0307 | 0.85496 | 0.96008 | 1.0302 | 0.8518 | 0.9566 | 3.2669 | -117.5253 | 114.0604 | 3.2722 | -117.5625 | 114.0822
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3907e-09 | -3.4592e-09 | 7.9429e-09 | -3.1364e-10 | 2.8639e-10 | -6.575e-11 | -7.4388e-09 | 6.3084e-09 | -1.3632e-09 | 2.0429e-10 | 1.3154e-10 | -3.4904e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0314 | 0.85805 | 0.96346 | 1.0314 | 0.85805 | 0.96346 | 3.2597 | -117.4776 | 114.0302 | 3.2597 | -117.4776 | 114.0302
Line1_1_3 | 0.0028496 | 0.0028618 | 0.0028836 | 0.0028497 | 0.0028618 | 0.0028836 | 0.0006581 | 0.0006609 | 0.00066593 | 0.00065811 | 0.0006609 | 0.00066594 | 0.00037171 | 0.00023937 | -0.00062789 | -0.00037164 | -0.00023929 | 0.00062798 | 0.00056793 | -0.00051409 | 0.0001319 | -0.00056786 | 0.00051418 | -0.00013182 | -53.5356 | -52.445 | -54.1064 | 126.4644 | 127.555 | 125.8936 |  | 1.0314 | 0.85805 | 0.96346 | 1.0312 | 0.85812 | 0.96355 | 3.2597 | -117.4776 | 114.0302 | 3.2615 | -117.4882 | 114.0389
Line2_1_4 | 0.0028549 | 0.026937 | 0.029692 | 0.002855 | 0.026937 | 0.029692 | 0.00065932 | 0.0062209 | 0.0068571 | 0.00065933 | 0.0062209 | 0.0068571 | 0.00036827 | 0.004133 | 0.0042854 | -0.00036796 | -0.0041209 | -0.0042677 | 0.00057167 | 0.003378 | 0.0050281 | -0.00057135 | -0.0033624 | -0.0050127 | -53.9507 | -156.7379 | 64.471 | 126.0493 | 23.2622 | -115.5291 |  | 1.0314 | 0.85805 | 0.96346 | 1.0307 | 0.85496 | 0.96008 | 3.2597 | -117.4776 | 114.0302 | 3.2669 | -117.5253 | 114.0604
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.7813e-09 | -6.9184e-09 | 1.5886e-08 | 4.077e-09 | 3.7456e-09 | -8.0086e-09 | -1.4878e-08 | 1.2617e-08 | -2.7265e-09 | 7.643e-09 | -6.1769e-09 | 1.0142e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0314 | 0.85805 | 0.96346 | 1.0314 | 0.85805 | 0.96346 | 3.2597 | -117.4776 | 114.0302 | 3.2597 | -117.4776 | 114.0302
Line4_2_6 | 0.0028569 | 0.002869 | 0.0028909 | 0.0028569 | 0.0028691 | 0.002891 | 0.00065976 | 0.00066257 | 0.00066763 | 0.00065977 | 0.00066258 | 0.00066764 | 0.00037121 | 0.00024111 | -0.00062989 | -0.00037114 | -0.00024104 | 0.00062998 | 0.00057018 | -0.0005149 | 0.00013065 | -0.0005701 | 0.00051499 | -0.00013057 | -53.6725 | -52.5805 | -54.2427 | 126.3275 | 127.4195 | 125.7573 |  | 1.0312 | 0.85811 | 0.96355 | 1.0311 | 0.85818 | 0.96365 | 3.2615 | -117.4882 | 114.0389 | 3.2633 | -117.4989 | 114.0477
Line5_6_7 | 0.0028569 | 0.0028691 | 0.002891 | 0.0028569 | 0.0028691 | 0.002891 | 0.00065977 | 0.00066258 | 0.00066764 | 0.00065978 | 0.00066259 | 0.00066765 | 0.00037114 | 0.00024104 | -0.00062998 | -0.00037106 | -0.00024097 | 0.00063007 | 0.0005701 | -0.00051499 | 0.00013057 | -0.00057003 | 0.00051508 | -0.00013049 | -53.6725 | -52.5806 | -54.2427 | 126.3275 | 127.4194 | 125.7573 |  | 1.0311 | 0.85818 | 0.96365 | 1.0309 | 0.85824 | 0.96374 | 3.2633 | -117.4989 | 114.0477 | 3.2651 | -117.5095 | 114.0564
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3194e-08 | -1.0263e-08 | 2.3734e-08 | 8.4842e-09 | 7.1278e-09 | -1.5889e-08 | -2.2176e-08 | 1.8901e-08 | -4.15e-09 | 1.4989e-08 | -1.2471e-08 | 2.419e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0309 | 0.85824 | 0.96374 | 1.0309 | 0.85824 | 0.96374 | 3.2651 | -117.5095 | 114.0564 | 3.2651 | -117.5095 | 114.0564
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3979e-09 | -3.4209e-09 | 7.9112e-09 | -3.1161e-10 | 2.8592e-10 | -6.6615e-11 | -7.392e-09 | 6.3004e-09 | -1.3833e-09 | 2.0453e-10 | 1.2991e-10 | -3.4762e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0309 | 0.85824 | 0.96374 | 1.0309 | 0.85824 | 0.96374 | 3.2651 | -117.5095 | 114.0564 | 3.2651 | -117.5095 | 114.0564
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3979e-09 | -3.4209e-09 | 7.9112e-09 | -3.1161e-10 | 2.8592e-10 | -6.6615e-11 | -7.392e-09 | 6.3004e-09 | -1.3833e-09 | 2.0453e-10 | 1.2991e-10 | -3.4762e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.0309 | 0.85824 | 0.96374 | 1.0309 | 0.85824 | 0.96374 | 3.2651 | -117.5095 | 114.0564 | 3.2651 | -117.5095 | 114.0564
Line9_3_11 | 0.0028497 | 0.0028618 | 0.0028836 | 0.0028497 | 0.0028618 | 0.0028836 | 0.00065811 | 0.0006609 | 0.00066594 | 0.00065811 | 0.00066091 | 0.00066595 | 0.00037164 | 0.00023929 | -0.00062798 | -0.00037156 | -0.00023922 | 0.00062807 | 0.00056786 | -0.00051418 | 0.00013182 | -0.00056779 | 0.00051427 | -0.00013174 | -53.5357 | -52.445 | -54.1064 | 126.4643 | 127.555 | 125.8936 |  | 1.0312 | 0.85812 | 0.96355 | 1.0311 | 0.85818 | 0.96365 | 3.2615 | -117.4882 | 114.0389 | 3.2633 | -117.4988 | 114.0476

## LLG_min_fault_10
name | pf_ikss_a_from_ka | pf_ikss_b_from_ka | pf_ikss_c_from_ka | pf_ikss_a_to_ka | pf_ikss_b_to_ka | pf_ikss_c_to_ka | pf_skss_a_from_mw | pf_skss_b_from_mw | pf_skss_c_from_mw | pf_skss_a_to_mw | pf_skss_b_to_mw | pf_skss_c_to_mw | pf_p_a_from_mw | pf_p_b_from_mw | pf_p_c_from_mw | pf_p_a_to_mw | pf_p_b_to_mw | pf_p_c_to_mw | pf_q_a_from_mvar | pf_q_b_from_mvar | pf_q_c_from_mvar | pf_q_a_to_mvar | pf_q_b_to_mvar | pf_q_c_to_mvar | pf_ikss_a_from_degree | pf_ikss_b_from_degree | pf_ikss_c_from_degree | pf_ikss_a_to_degree | pf_ikss_b_to_degree | pf_ikss_c_to_degree | 3xI0 | pf_vm_a_from_pu | pf_vm_b_from_pu | pf_vm_c_from_pu | pf_vm_a_to_pu | pf_vm_b_to_pu | pf_vm_c_to_pu | pf_va_a_from_degree | pf_va_b_from_degree | pf_va_c_from_degree | pf_va_a_to_degree | pf_va_b_to_degree | pf_va_c_to_degree
Line0_1_2 | 0.0027065 | 0.002718 | 0.0027387 | 0.0027065 | 0.002718 | 0.0027388 | 0.00062503 | 0.00062769 | 0.00063249 | 0.00062504 | 0.0006277 | 0.00063249 | 0.00033323 | 0.00021647 | -0.00056525 | -0.00033317 | -0.0002164 | 0.00056533 | 0.0005118 | -0.00046205 | 0.00011734 | -0.00051174 | 0.00046213 | -0.00011726 | -53.6724 | -52.5805 | -54.2427 | 126.3276 | 127.4195 | 125.7573 |  | 0.97711 | 0.81289 | 0.91275 | 0.97696 | 0.81295 | 0.91284 | 3.2597 | -117.4776 | 114.0302 | 3.2615 | -117.4882 | 114.0389
Line10_11_12 | 0.0026997 | 0.0027112 | 0.0027319 | 0.0026998 | 0.0027112 | 0.0027319 | 0.00062348 | 0.00062613 | 0.0006309 | 0.00062348 | 0.00062614 | 0.00063091 | 0.00033348 | 0.0002147 | -0.0005637 | -0.00033341 | -0.00021463 | 0.00056378 | 0.00050959 | -0.00046156 | 0.00011823 | -0.00050953 | 0.00046164 | -0.00011816 | -53.5357 | -52.4451 | -54.1064 | 126.4643 | 127.5549 | 125.8936 |  | 0.9768 | 0.81301 | 0.91293 | 0.97664 | 0.81307 | 0.91302 | 3.2633 | -117.4988 | 114.0476 | 3.265 | -117.5094 | 114.0564
Line11_12_13 | 0.0026998 | 0.0027112 | 0.0027319 | 0.0026998 | 0.0027113 | 0.0027319 | 0.00062348 | 0.00062614 | 0.00063091 | 0.00062349 | 0.00062614 | 0.00063091 | 0.00033341 | 0.00021463 | -0.00056378 | -0.00033335 | -0.00021457 | 0.00056386 | 0.00050953 | -0.00046164 | 0.00011816 | -0.00050946 | 0.00046172 | -0.00011809 | -53.5357 | -52.4451 | -54.1065 | 126.4643 | 127.5549 | 125.8936 |  | 0.97664 | 0.81307 | 0.91302 | 0.97648 | 0.81314 | 0.91311 | 3.265 | -117.5094 | 114.0564 | 3.2668 | -117.52 | 114.0651
Line12_13_15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1848e-08 | -9.1771e-09 | 2.1273e-08 | 7.6194e-09 | 6.3745e-09 | -1.4242e-08 | -1.9862e-08 | 1.6957e-08 | -3.7422e-09 | 1.3425e-08 | -1.1188e-08 | 2.1832e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97648 | 0.81314 | 0.91311 | 0.97648 | 0.81314 | 0.91311 | 3.2668 | -117.52 | 114.0651 | 3.2668 | -117.52 | 114.0651
Line13_13_14 | 0.0026999 | 0.0027114 | 0.002732 | 0.0026999 | 0.0027114 | 0.0027321 | 0.00062352 | 0.00062617 | 0.00063094 | 0.00062352 | 0.00062617 | 0.00063095 | 0.00033336 | 0.00021458 | -0.00056388 | -0.0003333 | -0.00021451 | 0.00056396 | 0.00050948 | -0.00046173 | 0.00011809 | -0.00050941 | 0.00046181 | -0.00011802 | -53.5359 | -52.4453 | -54.1065 | 126.4641 | 127.5547 | 125.8935 |  | 0.97648 | 0.81314 | 0.91311 | 0.97632 | 0.8132 | 0.9132 | 3.2668 | -117.52 | 114.0651 | 3.2686 | -117.5306 | 114.0738
Line14_15_16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.8984e-09 | -6.1181e-09 | 1.4182e-08 | 3.6701e-09 | 3.3155e-09 | -7.1509e-09 | -1.3241e-08 | 1.1304e-08 | -2.4948e-09 | 6.8041e-09 | -5.5361e-09 | 9.3582e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97648 | 0.81314 | 0.91311 | 0.97648 | 0.81314 | 0.91311 | 3.2668 | -117.52 | 114.0651 | 3.2668 | -117.52 | 114.0651
Line15_16_17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9492e-09 | -3.059e-09 | 7.0909e-09 | -2.7907e-10 | 2.5647e-10 | -6.0039e-11 | -6.6205e-09 | 5.6522e-09 | -1.2474e-09 | 1.8363e-10 | 1.1611e-10 | -3.1157e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97648 | 0.81314 | 0.91311 | 0.97648 | 0.81314 | 0.91311 | 3.2668 | -117.52 | 114.0651 | 3.2668 | -117.52 | 114.0651
Line16_4_18 | 0 | 0.026355 | 0.029598 | 0 | 0.026355 | 0.029598 | 0 | 0.0060865 | 0.0068354 | 0 | 0.0060865 | 0.0068354 | -3.9326e-09 | 0.0034837 | 0.0043979 | -2.772e-10 | -0.003473 | -0.0043803 | -6.7192e-09 | 0.0034882 | 0.0043945 | 1.8384e-10 | -0.003473 | -0.0043803 | 0 | -162.5626 | 69.0822 | 0 | 17.4375 | -110.9178 |  | 0.97647 | 0.80996 | 0.90955 | 0.97599 | 0.80697 | 0.90625 | 3.2669 | -117.5253 | 114.0604 | 3.2722 | -117.5625 | 114.0822
Line17_5_19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9406e-09 | -3.1047e-09 | 7.1288e-09 | -2.815e-10 | 2.5704e-10 | -5.9011e-11 | -6.6763e-09 | 5.6618e-09 | -1.2235e-09 | 1.8335e-10 | 1.1806e-10 | -3.1327e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97711 | 0.81289 | 0.91275 | 0.97711 | 0.81289 | 0.91275 | 3.2597 | -117.4776 | 114.0302 | 3.2597 | -117.4776 | 114.0302
Line1_1_3 | 0.0026997 | 0.0027111 | 0.0027318 | 0.0026997 | 0.0027112 | 0.0027318 | 0.00062346 | 0.00062611 | 0.00063088 | 0.00062347 | 0.00062612 | 0.00063089 | 0.00033361 | 0.00021483 | -0.00056354 | -0.00033355 | -0.00021477 | 0.00056362 | 0.00050972 | -0.0004614 | 0.00011838 | -0.00050966 | 0.00046148 | -0.00011831 | -53.5356 | -52.445 | -54.1064 | 126.4644 | 127.555 | 125.8936 |  | 0.97711 | 0.81289 | 0.91275 | 0.97696 | 0.81295 | 0.91284 | 3.2597 | -117.4776 | 114.0302 | 3.2615 | -117.4882 | 114.0389
Line2_1_4 | 0.0027047 | 0.025519 | 0.028129 | 0.0027047 | 0.025519 | 0.028129 | 0.00062462 | 0.0058934 | 0.0064962 | 0.00062462 | 0.0058934 | 0.0064962 | 0.00033052 | 0.0037094 | 0.0038462 | -0.00033025 | -0.0036985 | -0.0038303 | 0.00051308 | 0.0030318 | 0.0045127 | -0.00051279 | -0.0030178 | -0.0044989 | -53.9507 | -156.7379 | 64.471 | 126.0493 | 23.2622 | -115.5291 |  | 0.97711 | 0.81289 | 0.91275 | 0.97647 | 0.80996 | 0.90955 | 3.2597 | -117.4776 | 114.0302 | 3.2669 | -117.5253 | 114.0604
Line3_1_5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.8813e-09 | -6.2093e-09 | 1.4258e-08 | 3.6591e-09 | 3.3617e-09 | -7.1878e-09 | -1.3353e-08 | 1.1324e-08 | -2.447e-09 | 6.8597e-09 | -5.5438e-09 | 9.1026e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97711 | 0.81289 | 0.91275 | 0.97711 | 0.81289 | 0.91275 | 3.2597 | -117.4776 | 114.0302 | 3.2597 | -117.4776 | 114.0302
Line4_2_6 | 0.0027065 | 0.002718 | 0.0027388 | 0.0027065 | 0.0027181 | 0.0027388 | 0.00062504 | 0.0006277 | 0.00063249 | 0.00062505 | 0.00062771 | 0.0006325 | 0.00033317 | 0.0002164 | -0.00056533 | -0.0003331 | -0.00021634 | 0.00056541 | 0.00051174 | -0.00046213 | 0.00011726 | -0.00051167 | 0.00046221 | -0.00011719 | -53.6725 | -52.5805 | -54.2427 | 126.3275 | 127.4195 | 125.7573 |  | 0.97696 | 0.81295 | 0.91284 | 0.9768 | 0.81301 | 0.91293 | 3.2615 | -117.4882 | 114.0389 | 3.2633 | -117.4989 | 114.0477
Line5_6_7 | 0.0027065 | 0.0027181 | 0.0027388 | 0.0027066 | 0.0027181 | 0.0027388 | 0.00062505 | 0.00062771 | 0.0006325 | 0.00062505 | 0.00062771 | 0.00063251 | 0.0003331 | 0.00021634 | -0.00056541 | -0.00033303 | -0.00021627 | 0.00056549 | 0.00051167 | -0.00046221 | 0.00011719 | -0.00051161 | 0.00046229 | -0.00011712 | -53.6725 | -52.5806 | -54.2427 | 126.3275 | 127.4194 | 125.7573 |  | 0.9768 | 0.81301 | 0.91293 | 0.97664 | 0.81307 | 0.91302 | 3.2633 | -117.4989 | 114.0477 | 3.2651 | -117.5095 | 114.0564
Line6_7_8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1842e-08 | -9.211e-09 | 2.1301e-08 | 7.6147e-09 | 6.3973e-09 | -1.426e-08 | -1.9903e-08 | 1.6964e-08 | -3.7246e-09 | 1.3452e-08 | -1.1193e-08 | 2.1711e-09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97664 | 0.81307 | 0.91302 | 0.97664 | 0.81307 | 0.91302 | 3.2651 | -117.5095 | 114.0564 | 3.2651 | -117.5095 | 114.0564
Line7_8_9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9472e-09 | -3.0703e-09 | 7.1003e-09 | -2.7967e-10 | 2.5662e-10 | -5.9788e-11 | -6.6344e-09 | 5.6547e-09 | -1.2415e-09 | 1.8356e-10 | 1.1659e-10 | -3.1199e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97664 | 0.81307 | 0.91302 | 0.97664 | 0.81307 | 0.91302 | 3.2651 | -117.5095 | 114.0564 | 3.2651 | -117.5095 | 114.0564
Line8_8_10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.9472e-09 | -3.0703e-09 | 7.1003e-09 | -2.7967e-10 | 2.5662e-10 | -5.9787e-11 | -6.6344e-09 | 5.6547e-09 | -1.2415e-09 | 1.8356e-10 | 1.1659e-10 | -3.1199e-10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.97664 | 0.81307 | 0.91302 | 0.97664 | 0.81307 | 0.91302 | 3.2651 | -117.5095 | 114.0564 | 3.2651 | -117.5095 | 114.0564
Line9_3_11 | 0.0026997 | 0.0027112 | 0.0027318 | 0.0026997 | 0.0027112 | 0.0027319 | 0.00062347 | 0.00062612 | 0.00063089 | 0.00062348 | 0.00062613 | 0.0006309 | 0.00033355 | 0.00021477 | -0.00056362 | -0.00033348 | -0.0002147 | 0.0005637 | 0.00050966 | -0.00046148 | 0.00011831 | -0.00050959 | 0.00046156 | -0.00011824 | -53.5357 | -52.445 | -54.1064 | 126.4643 | 127.555 | 125.8936 |  | 0.97696 | 0.81295 | 0.91284 | 0.9768 | 0.81301 | 0.91293 | 3.2615 | -117.4882 | 114.0389 | 3.2633 | -117.4988 | 114.0476